## SCI Standard Mappingset
OneView IEC 61400-25-2 Edition 2 | Pre-defined IEC 61400-25 TAG | IEC Logical Node | IEC Data Object | Presentation Name (English) | Presentation Name (German) | Presentation Name (Spanish) | Presentation Name (Polish) | Description | OV SI Type | SI Unit | Type | DataType | CollectorType | Usage 1 | Usage 2 | Comment
CONN.ConSt | #N/A | CONN. | ConSt | Provider connection state | Status der Providerverbindung | Estado de conexión del proveedor | Stan połączenia operatora | Provider connection state | Enum | Enum | Live Value | Long | Live Value
SERVER.DmdWSpt | #N/A | SERVER. | DmdWSpt | Overall Active power setpoint | Gesamtwirkleistungssollwert | Punto de ajuste de la potencia activa total | Ogólna nastawa mocy czynnej | Overall Active power setpoint | W | W | Live Value | Double | Live Value | OneView Server
SERVER.HddSpaceAvl | #N/A | SERVER. | HddSpaceAvl | Free disk space on HD drive | Freier Speicherplatz auf dem Festplattenlaufwerk | Espacio en disco disponible en el disco HD | Wolne miejsce na dysku HD | Free disk space on HD drive | Byte | Byte | Live Value | Double | Live Value | OneView Server
SERVER.HddSpaceAvl_10m_Avg | #N/A | SERVER. | HddSpaceAvl_10m_Avg | Free disk space on HD drive (avg) | Freier Speicherplatz auf dem Festplattenlaufwerk (avg) | Espacio en disco disponible en el disco HD (avg) | Wolne miejsce na dysku HD (avg) | Free disk space on HD drive | Byte | Byte | Average | Double | 10 minute tag | OneView Server
SERVER.HddSpaceAvl_10m_Max | #N/A | SERVER. | HddSpaceAvl_10m_Max | Free disk space on HD drive (max) | Freier Speicherplatz auf dem Festplattenlaufwerk (max) | Espacio en disco disponible en el disco HD (max) | Wolne miejsce na dysku HD (max) | Free disk space on HD drive | Byte | Byte | Maximum | Double | 10 minute tag | OneView Server
SERVER.HddSpaceAvl_10m_Min | #N/A | SERVER. | HddSpaceAvl_10m_Min | Free disk space on HD drive (min) | Freier Speicherplatz auf dem Festplattenlaufwerk (min) | Espacio en disco disponible en el disco HD (min) | Wolne miejsce na dysku HD (min) | Free disk space on HD drive | Byte | Byte | Minimum | Double | 10 minute tag | OneView Server
SERVER.HddSpaceAvl_10m_Std | #N/A | SERVER. | HddSpaceAvl_10m_Std | Free disk space on HD drive (std) | Freier Speicherplatz auf dem Festplattenlaufwerk (std) | Espacio en disco disponible en el disco HD (std) | Wolne miejsce na dysku HD (std) | Free disk space on HD drive | Byte | Byte | Standard Deviation | Double | 10 minute tag | OneView Server
SERVER.OVCpuTm | #N/A | SERVER. | OVCpuTm | OneView CPU usage | OneView CPU-Nutzung | Uso de la CPU de OneView | Użycie procesora OneView | OneView CPU usage | percent | percent | Live Value | Double | Live Value | OneView Server
SERVER.OVCpuTm_10m_Avg | #N/A | SERVER. | OVCpuTm_10m_Avg | OneView CPU usage (avg) | OneView CPU-Nutzung (avg) | Uso de la CPU de OneView (avg) | Użycie procesora OneView (avg) | OneView CPU usage | percent | percent | Average | Double | 10 minute tag | OneView Server
SERVER.OVCpuTm_10m_Max | #N/A | SERVER. | OVCpuTm_10m_Max | OneView CPU usage (max) | OneView CPU-Nutzung (max) | Uso de la CPU de OneView (max) | Użycie procesora OneView (max) | OneView CPU usage | percent | percent | Maximum | Double | 10 minute tag | OneView Server
SERVER.OVCpuTm_10m_Min | #N/A | SERVER. | OVCpuTm_10m_Min | OneView CPU usage (min) | OneView CPU-Nutzung (min) | Uso de la CPU de OneView (min) | Użycie procesora OneView (min) | OneView CPU usage | percent | percent | Minimum | Double | 10 minute tag | OneView Server
SERVER.OVCpuTm_10m_Std | #N/A | SERVER. | OVCpuTm_10m_Std | OneView CPU usage (std) | OneView CPU-Nutzung (std) | Uso de la CPU de OneView (std) | Użycie procesora OneView (std) | OneView CPU usage | percent | percent | Standard Deviation | Double | 10 minute tag | OneView Server
SERVER.OVCpuTmMean | #N/A | SERVER. | OVCpuTmMean | OneView CPU usage mean | OneView CPU-Nutzung Mittelwert | Uso medio de la CPU de OneView | Średnia użycia procesora OneView | OneView CPU usage mean | percent | percent | Live Value | Double | Live Value | OneView Server
SERVER.OVCpuTmMean_10m_Avg | #N/A | SERVER. | OVCpuTmMean_10m_Avg | OneView CPU usage mean (avg) | OneView CPU-Nutzung Mittelwert (avg) | Uso medio de la CPU de OneView (avg) | Średnia użycia procesora OneView (avg) | OneView CPU usage mean | percent | percent | Average | Double | 10 minute tag | OneView Server
SERVER.OVCpuTmMean_10m_Max | #N/A | SERVER. | OVCpuTmMean_10m_Max | OneView CPU usage mean (max) | OneView CPU-Nutzung Mittelwert (max) | Uso medio de la CPU de OneView (max) | Średnia użycia procesora OneView (max) | OneView CPU usage mean | percent | percent | Maximum | Double | 10 minute tag | OneView Server
SERVER.OVCpuTmMean_10m_Min | #N/A | SERVER. | OVCpuTmMean_10m_Min | OneView CPU usage mean (min) | OneView CPU-Nutzung Mittelwert (min) | Uso medio de la CPU de OneView (min) | Średnia użycia procesora OneView (min) | OneView CPU usage mean | percent | percent | Minimum | Double | 10 minute tag | OneView Server
SERVER.OVCpuTmMean_10m_Std | #N/A | SERVER. | OVCpuTmMean_10m_Std | OneView CPU usage mean (std) | OneView CPU-Nutzung Mittelwert (std) | Uso medio de la CPU de OneView (std) | Średnia użycia procesora OneView (std) | OneView CPU usage mean | percent | percent | Standard Deviation | Double | 10 minute tag | OneView Server
SERVER.OVMemUsage | #N/A | SERVER. | OVMemUsage | OneView memory usage | OneView-Speichernutzung | Uso de la memoria de OneView | Użycie pamięci OneView | OneView memory usage | Byte | Byte | Live Value | Double | Live Value | OneView Server
SERVER.OVMemUsage_10m_Avg | #N/A | SERVER. | OVMemUsage_10m_Avg | OneView memory usage (avg) | OneView-Speichernutzung (avg) | Uso de la memoria de OneView (avg) | Użycie pamięci OneView (avg) | OneView memory usage | Byte | Byte | Average | Double | 10 minute tag | OneView Server
SERVER.OVMemUsage_10m_Max | #N/A | SERVER. | OVMemUsage_10m_Max | OneView memory usage (max) | OneView-Speichernutzung (max) | Uso de la memoria de OneView (max) | Użycie pamięci OneView (max) | OneView memory usage | Byte | Byte | Maximum | Double | 10 minute tag | OneView Server
SERVER.OVMemUsage_10m_Min | #N/A | SERVER. | OVMemUsage_10m_Min | OneView memory usage (min) | OneView-Speichernutzung (min) | Uso de la memoria de OneView (min) | Użycie pamięci OneView (min) | OneView memory usage | Byte | Byte | Minimum | Double | 10 minute tag | OneView Server
SERVER.OVMemUsage_10m_Std | #N/A | SERVER. | OVMemUsage_10m_Std | OneView memory usage (std) | OneView-Speichernutzung (std) | Uso de la memoria de OneView (std) | Użycie pamięci OneView (std) | OneView memory usage | Byte | Byte | Standard Deviation | Double | 10 minute tag | OneView Server
SERVER.OVNumClients | #N/A | SERVER. | OVNumClients | Number of OneView Active Clients | Anzahl aktiver OneView Kunden | Número de clientes activos de OneView | Liczba aktywnych klientów OneView | Number of OneView Clients | count | count | Live Value | Double | Live Value | OneView Server
SERVER.OVNumClients_10m_Avg | #N/A | SERVER. | OVNumClients_10m_Avg | Number of OneView Active Clients (avg) | Anzahl aktiver OneView Kunden (avg) | Número de clientes activos de OneView (avg) | Liczba aktywnych klientów OneView (avg) | Number of OneView Clients | count | count | Average | Double | 10 minute tag | OneView Server
SERVER.OVNumClients_10m_Max | #N/A | SERVER. | OVNumClients_10m_Max | Number of OneView Active Clients (max) | Anzahl aktiver OneView Kunden (max) | Número de clientes activos de OneView (max) | Liczba aktywnych klientów OneView (max) | Number of OneView Clients | count | count | Maximum | Double | 10 minute tag | OneView Server
SERVER.OVNumClients_10m_Min | #N/A | SERVER. | OVNumClients_10m_Min | Number of OneView Active Clients (min) | Anzahl aktiver OneView Kunden (min) | Número de clientes activos de OneView (min) | Liczba aktywnych klientów OneView (min) | Number of OneView Clients | count | count | Minimum | Double | 10 minute tag | OneView Server
SERVER.OVNumClients_10m_Std | #N/A | SERVER. | OVNumClients_10m_Std | Number of OneView Active Clients (std) | Anzahl aktiver OneView Kunden (std) | Número de clientes activos de OneView (std) | Liczba aktywnych klientów OneView (std) | Number of OneView Clients | count | count | Standard Deviation | Double | 10 minute tag | OneView Server
SERVER.OVNumUsers | #N/A | SERVER. | OVNumUsers | Number of OneView Active Users | Anzahl aktiver OneView Nutzer | Número de usuarios activos de OneView | Liczba aktywnych użytkowników OneView | Number of OneView Users | count | count | Live Value | Double | Live Value | OneView Server
SERVER.OVNumUsers_10m_Avg | #N/A | SERVER. | OVNumUsers_10m_Avg | Number of OneView Active Users (avg) | Anzahl aktiver OneView Nutzer (avg) | Número de usuarios activos de OneView (avg) | Liczba aktywnych użytkowników OneView (avg) | Number of OneView Users | count | count | Average | Double | 10 minute tag | OneView Server
SERVER.OVNumUsers_10m_Max | #N/A | SERVER. | OVNumUsers_10m_Max | Number of OneView Active Users (max) | Anzahl aktiver OneView Nutzer (max) | Número de usuarios activos de OneView (max) | Liczba aktywnych użytkowników OneView (max) | Number of OneView Users | count | count | Maximum | Double | 10 minute tag | OneView Server
SERVER.OVNumUsers_10m_Min | #N/A | SERVER. | OVNumUsers_10m_Min | Number of OneView Active Users (min) | Anzahl aktiver OneView Nutzer (min) | Número de usuarios activos de OneView (min) | Liczba aktywnych użytkowników OneView (min) | Number of OneView Users | count | count | Minimum | Double | 10 minute tag | OneView Server
SERVER.OVNumUsers_10m_Std | #N/A | SERVER. | OVNumUsers_10m_Std | Number of OneView Active Users (std) | Anzahl aktiver OneView Nutzer (std) | Número de usuarios activos de OneView (std) | Liczba aktywnych użytkowników OneView (std) | Number of OneView Users | count | count | Standard Deviation | Double | 10 minute tag | OneView Server
SERVER.SysCpuTm | #N/A | SERVER. | SysCpuTm | System CPU usage | System-CPU-Nutzung | Uso de la CPU del sistema | Użycie CPU | System CPU usage | percent | percent | Live Value | Double | Live Value | OneView Server
SERVER.SysCpuTm_10m_Avg | #N/A | SERVER. | SysCpuTm_10m_Avg | System CPU usage (avg) | System-CPU-Nutzung (avg) | Uso de la CPU del sistema (avg) | Użycie CPU (avg) | System CPU usage | percent | percent | Average | Double | 10 minute tag | OneView Server
SERVER.SysCpuTm_10m_Max | #N/A | SERVER. | SysCpuTm_10m_Max | System CPU usage (max) | System-CPU-Nutzung (max) | Uso de la CPU del sistema (max) | Użycie CPU (max) | System CPU usage | percent | percent | Maximum | Double | 10 minute tag | OneView Server
SERVER.SysCpuTm_10m_Min | #N/A | SERVER. | SysCpuTm_10m_Min | System CPU usage (min) | System-CPU-Nutzung (min) | Uso de la CPU del sistema (min) | Użycie CPU (min) | System CPU usage | percent | percent | Minimum | Double | 10 minute tag | OneView Server
SERVER.SysCpuTm_10m_Std | #N/A | SERVER. | SysCpuTm_10m_Std | System CPU usage (std) | System-CPU-Nutzung (std) | Uso de la CPU del sistema (std) | Użycie CPU (std) | System CPU usage | percent | percent | Standard Deviation | Double | 10 minute tag | OneView Server
SERVER.SysCpuTmMean | #N/A | SERVER. | SysCpuTmMean | System CPU usage mean | System-CPU-Nutzung Mittelwert | Medio uso de la CPU del sistema | Średnie użycie CPU | System CPU usage mean | percent | percent | Live Value | Double | Live Value | OneView Server
SERVER.SysCpuTmMean_10m_Avg | #N/A | SERVER. | SysCpuTmMean_10m_Avg | System CPU usage mean (avg) | System-CPU-Nutzung Mittelwert (avg) | Medio uso de la CPU del sistema (avg) | Średnie użycie CPU (avg) | System CPU usage mean | percent | percent | Average | Double | 10 minute tag | OneView Server
SERVER.SysCpuTmMean_10m_Max | #N/A | SERVER. | SysCpuTmMean_10m_Max | System CPU usage mean (max) | System-CPU-Nutzung Mittelwert (max) | Medio uso de la CPU del sistema (max) | Średnie użycie CPU (max) | System CPU usage mean | percent | percent | Maximum | Double | 10 minute tag | OneView Server
SERVER.SysCpuTmMean_10m_Min | #N/A | SERVER. | SysCpuTmMean_10m_Min | System CPU usage mean (min) | System-CPU-Nutzung Mittelwert (min) | Medio uso de la CPU del sistema (min) | Średnie użycie CPU (min) | System CPU usage mean | percent | percent | Minimum | Double | 10 minute tag | OneView Server
SERVER.SysCpuTmMean_10m_Std | #N/A | SERVER. | SysCpuTmMean_10m_Std | System CPU usage mean (std) | System-CPU-Nutzung Mittelwert (std) | Medio uso de la CPU del sistema (std) | Średnie użycie CPU (std) | System CPU usage mean | percent | percent | Standard Deviation | Double | 10 minute tag | OneView Server
SERVER.SysMemUsage | #N/A | SERVER. | SysMemUsage | System memory usage | System-Speichernutzung | Uso de la memoria del sistema | Użycie pamięci systemowej | System memory usage | Byte | Byte | Live Value | Double | Live Value | OneView Server
SERVER.SysMemUsage_10m_Avg | #N/A | SERVER. | SysMemUsage_10m_Avg | System memory usage (avg) | System-Speichernutzung (avg) | Uso de la memoria del sistema (avg) | Użycie pamięci systemowej (avg) | System memory usage | Byte | Byte | Average | Double | 10 minute tag | OneView Server
SERVER.SysMemUsage_10m_Max | #N/A | SERVER. | SysMemUsage_10m_Max | System memory usage (max) | System-Speichernutzung (max) | Uso de la memoria del sistema (max) | Użycie pamięci systemowej (max) | System memory usage | Byte | Byte | Maximum | Double | 10 minute tag | OneView Server
SERVER.SysMemUsage_10m_Min | #N/A | SERVER. | SysMemUsage_10m_Min | System memory usage (min) | System-Speichernutzung (min) | Uso de la memoria del sistema (min) | Użycie pamięci systemowej (min) | System memory usage | Byte | Byte | Minimum | Double | 10 minute tag | OneView Server
SERVER.SysMemUsage_10m_Std | #N/A | SERVER. | SysMemUsage_10m_Std | System memory usage (std) | System-Speichernutzung (std) | Uso de la memoria del sistema (std) | Użycie pamięci systemowej (std) | System memory usage | Byte | Byte | Standard Deviation | Double | 10 minute tag | OneView Server
SERVER.TurSt | #N/A | SERVER. | TurSt | Overall Turbine Status | Gesamter Turbinenstatus | Estado de la turbina general | Ogólny stan turbiny | Overall Turbine Status | Enum | Enum | Live Value | Long | Live Value
WALM.ActAlmCnt | #N/A | WALM. | ActAlmCnt | Number Of Active Alarms | Anzahl aktiver Alarme | Número de alarmas activas | Liczba aktywnych alarmów | Number of active alarms | count | Count | Live Value | Long | Live Value
WALM.ActAlmCnt_10m_Sum | #N/A | WALM. | ActAlmCnt_10m_Sum | Number Of Active Alarms (sum) | Anzahl aktiver Alarme (sum) | Número de alarmas activas (sum) | Liczba aktywnych alarmów (sum) | Active alarm count during 10 min period | count | Count | Summation | Long | 10 minute tag
WALM.ActAlmSt | #N/A | WALM. | ActAlmSt | First Active alarm code | Erster aktiver Alarmcode | Código de la primera alarma activa | Pierwszy aktywny kod alarmowy | First active alarm code (ONLY NWT) | Enum | Enum | Live Value | Long | Live Value
WALM.ActWarCnt | #N/A | WALM. | ActWarCnt | Number Of Active Warnings | Anzahl aktiver Warnungen | Número de avisos activos | Liczba aktywnych ostrzeżeń | Number of active warnings | count | Enum | Live Value | Long | Live Value
WALM.ActWarSt | #N/A | WALM. | ActWarSt | First Active warning code | Erster aktiver Warncode | Código del primer aviso activo | Pierwszy aktywny kod ostrzeżenia | First active warning code (ONLY NWT) | Enum | Enum | Live Value | Long | Live Value
WALM.AlmLvl | #N/A | WALM. | AlmLvl | Active alarm level | Aktive Alarmstufe | Nivel de alarma activa | Aktywny poziom alarmu | Active alarm level (Alarm, warning, operation) | Enum | Enum | Live Value | Long | Live Value
WALM.AlmSt | WALM.AlmSt | WALM. | AlmSt | Active alarm code | Aktiver Alarmcode | Código de alarma activa | Aktywny kod alarmowy | Active alarm code | Enum | Enum | Live Value | Long | Live Value
WALM.AlmSt_10m_End | #N/A | WALM. | AlmSt_10m_End | First active alarm code (end) | Erster aktiver Alarmcode (end) | Código de la primera alarma activa (end) | Pierwszy aktywny kod alarmowy (end) | First active alarm code in the 10 minute period | Enum | Enum | Endvalue | Long | 10 minute tag
WALM.AlmTms | #N/A | WALM. | AlmTms | Time with an alarm | Zeit mit einem Alarm | Tiempo con una alarma | Czas z alarmem | Time with an alarm | s | seconds | Live Value | Long | Live Value
WALM.AlmTms_10m_Sum | #N/A | WALM. | AlmTms_10m_Sum | Time with an alarm (sum) | Zeit mit einem Alarm (sum) | Tiempo con una alarma (sum) | Czas z alarmem (sum) | Time with an alarm in the each 10 minute periode, i.e. 0-600 seconds | s | seconds | Summation | Long | 10 minute tag
WALM.AlmVal1 | #N/A | WALM. | AlmVal1 | First parameter of the active alarm | Erster Parameter des aktiven Alarms | Primer parámetro de la alarma activa | Pierwszy parametr aktywnego alarmu | First parameter of the active alarm | Enum | Enum | Live Value | Double | Live Value
WALM.AlmVal1_10m_End | #N/A | WALM. | AlmVal1_10m_End | First parameter of the active alarm (end) | Erster Parameter des aktiven Alarms (end) | Primer parámetro de la alarma activa (end) | Pierwszy parametr aktywnego alarmu (end) | First parameter of the active alarm in the 10 minute period | Enum | Enum | Endvalue | Double | 10 minute tag
WALM.AlmVal2 | #N/A | WALM. | AlmVal2 | Second parameter active alarm | Zweiter Parameter aktiver Alarme | Segundo parámetro de la alarma activa | Alarm aktywny drugiego parametru | Second parameter of the active alarm | Enum | Enum | Live Value | Double | Live Value
WALM.AlmVal2_10m_End | #N/A | WALM. | AlmVal2_10m_End | Second parameter active alarm (end) | Zweiter Parameter aktiver Alarme (end) | Segundo parámetro de la alarma activa (end) | Alarm aktywny drugiego parametru (end) | Second parameter of the active alarm in the 10 minute period | Enum | Enum | Endvalue | Double | 10 minute tag
WALM.WarSt | #N/A | WALM. | WarSt | Active warning code | Aktiver Warncode | Código del aviso activo | Aktywny kod ostrzeżenia | Active warning code | Enum | Enum | Live Value | Long | Live Value
WALM.WarSt_10m_End | #N/A | WALM. | WarSt_10m_End | First active warning code (end) | Erster aktiver Warncode (end) | Código del primer aviso activo (end) | Pierwszy aktywny kod ostrzeżenia (end) | First active warning code in the 10 minute period | Enum | Enum | Endvalue | Long | 10 minute tag
WAPC.BatStopCnt | #N/A | WAPC. | BatStopCnt | Number of Stopped by bat/bird control | Anzahl der Stopps durch Fledermaus-/Vogelregelung | Cantidad de paradas por control de murciélago/pájaro | Liczba zatrzymanych przez nietoperze/ptaki | Number of Stopped by bat/bird control | count | Count | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.CtlSt | #N/A | WAPC. | CtlSt | Active power control state | Status der Wirkleistungsregelung | Estado del control de potencia activa | Stan sterowania mocą czynną | Active power control state 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.CtlStStr | #N/A | WAPC. | CtlStStr | Active power control state Text | Statustext der Wirkleistungsregelung | Texto del estado del control de potencia activa | Stan sterowania mocą czynną Tekst | Active power control state text | Enum | Enum | Live Value | String | Live Value | Universal Park Controller (UPC)
WAPC.CutHiTurNum | WAPC.CutHiTurNum | WAPC. | CutHiTurNum | Number of turbines not running due to high wind speed | Anzahl der Turbinen, die aufgrund hoher Windgeschwindigkeit nicht laufen | Cantidad de turbinas no funcionando debido a la alta velocidad del viento | Liczba turbin zatrzymanych z powodu dużej prędkości wiatru | Number of turbines not running due to high wind speed | count | Count | Total Counter | Long | Live Value
WAPC.CutLoTurNum | WAPC.CutLoTurNum | WAPC. | CutLoTurNum | Number of turbines not running due to low wind speed | Anzahl der Turbinen, die aufgrund niedriger Windgeschwindigkeit nicht laufen | Cantidad de turbinas no funcionando debido a la baja velocidad del viento | Liczba turbin zatrzymanych z powodu niskiej prędkości wiatru | Number of turbines not running due to low wind speed | count | Count | Total Counter | Long | Live Value
WAPC.DelAct | WAPC.DelAct | WAPC. | DelAct | Activate delta control function | Aktivieren der Deltaregelungsfunktion | Activar función de control de delta | Włączanie funkcji sterowania delta | Activate delta control function | Enum | Enum | Live Value | Long | Live Value
WAPC.DelEna | WAPC.DelEna | WAPC. | DelEna | Delta function enabled | Deltafunktion aktiviert | Función delta habilitada | Funkcja Delta włączona | Delta function enabled | Enum | Enum | Live Value | Long | Live Value
WAPC.DelSpt | WAPC.DelSpt | WAPC. | DelSpt | Active Power Delta Setpoint | Deltawirkleistungssollwert | Punto de ajuste de delta de potencia activa | Nastawa Delta mocy czynnej | Set reference value for the delta function, wind power plant active power reserve | W | W | Setpoint | Double | Live Value
WAPC.DrtOpTms_10m_Sum | #N/A | WAPC. | DrtOpTms_10m_Sum | No of seconds derated internal or remote (sum) | Anzahl der reduzierten Sekunden intern oder remote (sum) | No. de segundos disminuido interno o remoto (sum) | Liczba sekund opóźnienia wewnętrznie lub zdalnie (sum) | No of seconds derated internal or remote | s | seconds | Summation | Double | 10 minute tag
WAPC.EmgWSptSt | #N/A | WAPC. | EmgWSptSt | Emergency active power setpoint state | Status des Not-Wirkleistungssollwerts | Estado del punto de ajuste de potencia activa de emergencia | Stan awaryjnej nastawy mocy czynnej | Emergency active power setpoint state 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.ExDrtOpTms_10m_Sum | #N/A | WAPC. | ExDrtOpTms_10m_Sum | No of seconds derated remote (sum) | Anzahl der reduzierten Sekunden remote (sum) | No. de segundos disminuido remoto (sum) | Liczba sekund opóźnienia zdalnie (sum) | No of seconds derated remote | s | seconds | Summation | Double | 10 minute tag
WAPC.Gra | WAPC.Gra | WAPC. | Gra | Wind power plant gradient | Windkraftanlagen Gradient | Gradiente de la planta eólica | Gradient elektrowni wiatrowej | Wind power plant gradient | W_s | W/s | Live Value | Double | Live Value
WAPC.GraAct | WAPC.GraAct | WAPC. | GraAct | Activate gradient control function | Aktivieren der Gradientenregelungsfunktion | Activar función de control de gradiente | Aktywowanie funkcji sterowania gradientem | Activate gradient control function | Enum | Enum | Live Value | Long | Live Value
WAPC.GraEna | WAPC.GraEna | WAPC. | GraEna | Gradient function enabled | Gradientenfunktion aktiviert | Función de gradiente habilitada | Funkcja gradientu włączona | Gradient function enabled | Enum | Enum | Live Value | Long | Live Value
WAPC.GrdLossW | #N/A | WAPC. | GrdLossW | UPC Estimated grid loss | UPC Geschätzter Netzverlust | Pérdidas estimadas de red UPC | UPC Szacowana strata sieci | Estimated grid loss | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.GrdOpSt | #N/A | WAPC. | GrdOpSt | Site Utlity Command Status | Status des netzseitigen Befehls | Estado de comando de utilidad de sitio | Stan polecenia operatora | Site Utlity Command Status | Enum | Enum | Live Value | Long | Live Value
WAPC.Hz | #N/A | WAPC. | Hz | Frequency in PCC | Frequenz am NVP | Frecuencia en PCC | Częstotliwość w PCC | Frequency | Hz | Hz | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.Hz_10m_Avg | #N/A | WAPC. | Hz_10m_Avg | Frequency in PCC (avg) | Frequenz am NVP (avg) | Frecuencia en PCC (avg) | Częstotliwość w PCC (avg) | Frequency in PCC Averge | Hz | Hz | Average | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.Hz_10m_Max | #N/A | WAPC. | Hz_10m_Max | Frequency in PCC (max) | Frequenz am NVP (max) | Frecuencia en PCC (max) | Częstotliwość w PCC (max) | Frequency in PCC Maximum | Hz | Hz | Maximum | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.Hz_10m_Min | #N/A | WAPC. | Hz_10m_Min | Frequency in PCC (min) | Frequenz am NVP (min) | Frecuencia en PCC (min) | Częstotliwość w PCC (min) | Frequency in PCC Minimum | Hz | Hz | Minimum | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.Hz_10m_Std | #N/A | WAPC. | Hz_10m_Std | Frequency in PCC (std) | Frequenz am NVP (std) | Frecuencia en PCC (std) | Częstotliwość w PCC (std) | Measured Frequency for power control system | Hz | Hz | Standard Deviation | Double | 10 minute tag
WAPC.Hz_1s_End | #N/A | WAPC. | Hz_1s_End | Frequency in PCC (end) | Frequenz am NVP (end) | Frecuencia en PCC (end) | Częstotliwość w PCC (end) | Frequency in PCC | Hz | Hz | Endvalue | Double | 1 second tag | Universal Park Controller (UPC)
WAPC.HzCmpSt | #N/A | WAPC. | HzCmpSt | Frequency compensation state | Status der Frequenzkompensation | Estado de compensación de la frecuencia | Stan kompensacji częstotliwości | Frequency compensation state 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.HzCmpStStr | #N/A | WAPC. | HzCmpStStr | Frequency compensation state text | Statustext der Frequenzkompensation | Texto del estado de compensación de la frecuencia | Tekst stanu kompensacji częstotliwości | Frequency compensation state text | String | String | Live Value | String | Live Value | Universal Park Controller (UPC)
WAPC.IceStopCnt | #N/A | WAPC. | IceStopCnt | Number of Stopped by ice control | Anzahl der Stpps durch Eiskontrolle | Número de paradas por control de hielo | Liczba zatrzymanych przez kontrolę lodu | Number of Stopped by ice control | count | Count | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.ICntrbW | #N/A | WAPC. | ICntrbW | UPC I Contribution | UPC I Beitrag | Contribución UPC I | UPC Udział I | I Contribution | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.IntnDrtCnt_10m_Sum | #N/A | WAPC. | IntnDrtCnt_10m_Sum | Internal derate state changes (sum) | Interne Änderungen des Derate-Status (sum) | Cambios en el estado de disminución interno (sum) | Zmiany stanu redukcji wewn. (sum) | Internal derate state changes | count | Count | Summation | Double | 10 minute tag
WAPC.IntnDrtSt_10m_End | #N/A | WAPC. | IntnDrtSt_10m_End | Internal derate state (end) | Interner Derate-Status (end) | Estado de disminución interno (end) | Wewnętrzny stan redukcji (end) | Internal derate state | Enum | Enum | Endvalue | Double | 10 minute tag
WAPC.IntnDrtTms_10m_Sum | #N/A | WAPC. | IntnDrtTms_10m_Sum | Internal derate state time (sum) | Interne Zeit des Derate-Status (sum) | Hora de estado de disminución interno (sum) | Czas wewn. Stanu redukcji (sum) | Internal derate state time | s | seconds | Summation | Double | 10 minute tag
WAPC.IntnWSpt | #N/A | WAPC. | IntnWSpt | UPC Internal active power setpoint | UPC interner Wirkleistungssollwert | Punto de ajuste de potencia activa interna de UPC | UPC Wewnętrzna nastawa mocy czynnej | Internal active power setpoint | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.IntnWSpt_10m_Avg | #N/A | WAPC. | IntnWSpt_10m_Avg | UPC Internal active power setpoint (avg) | UPC interner Wirkleistungssollwert (avg) | Punto de ajuste de potencia activa interna de UPC (avg) | UPC Wewnętrzna nastawa mocy czynnej (avg) | Internal Setpoint Average | W | W | Average | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.IntnWSpt_10m_Max | #N/A | WAPC. | IntnWSpt_10m_Max | UPC Internal active power setpoint (max) | UPC interner Wirkleistungssollwert (max) | Punto de ajuste de potencia activa interna de UPC (max) | UPC Wewnętrzna nastawa mocy czynnej (max) | Internal Setpoint Maximum | W | W | Maximum | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.IntnWSpt_10m_Min | #N/A | WAPC. | IntnWSpt_10m_Min | UPC Internal active power setpoint (min) | UPC interner Wirkleistungssollwert (min) | Punto de ajuste de potencia activa interna de UPC (min) | UPC Wewnętrzna nastawa mocy czynnej (min) | Internal Setpoint Minimum | W | W | Minimum | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.IntnWSpt_1s_End | #N/A | WAPC. | IntnWSpt_1s_End | UPC Internal active power setpoint (end) | UPC interner Wirkleistungssollwert (end) | Punto de ajuste de potencia activa interna de UPC (end) | UPC Wewnętrzna nastawa mocy czynnej (end) | Internal Setpoint (setpoint calculated after considering grid losses, turbine consumption etc.) | W | W | Endvalue | Double | Live Value | Universal Park Controller (UPC)
WAPC.LaPMActSector | #N/A | WAPC. | LaPMActSector | Load and Power Mode Active wind sector | LaPM Aktiver Windsektor | Sector eólico activo de LaPM | LaPM Aktywny sektor wiatrowy | Load and Power Mode Active wind sector | Enum | Enum | Live Value | Long | Live Value
WAPC.LaPMActSector_10m_End | #N/A | WAPC. | LaPMActSector_10m_End | Load and Power Mode Active wind sector (end) | LaPM Aktiver Windsektor (end) | Sector eólico activo de LaPM (end) | LaPM Aktywny sektor wiatrowy (end) | Active wind sector in 10 min period | Enum | Enum | Endvalue | Long | 10 minute tag | Vestas Load and Power Mode
WAPC.LaPMActSectorTms_10m_Sum | #N/A | WAPC. | LaPMActSectorTms_10m_Sum | Load and Power Mode Active sector time (sum) | LaPM Aktiver Sektor Zeit (sum) | Hora del sector activo LaPM (sum) | LaPM Czas sektorowy Aktywny (sum) | Active sector time in 10 min period | s | seconds | Summation | Long | 10 minute tag | Vestas Load and Power Mode
WAPC.LaPMEndSectorAng | #N/A | WAPC. | LaPMEndSectorAng | Load and Power Mode Sector Angle | LaPM Sektor-Winkel | Ángulo del sector LaPM | Kąt sektora LaPM | Load and Power Mode Sector Angle | deg | Degrees | Live Value | Double | Live Value
WAPC.LaPMEndSectorAng_10m_Avg | #N/A | WAPC. | LaPMEndSectorAng_10m_Avg | Load and Power Mode Sector Angle (avg) | LaPM Sektor-Winkel (avg) | Ángulo del sector LaPM (avg) | Kąt sektora LaPM (avg) | Sector angle end in 10 min period | deg | Degrees | Average | Double | 10 minute tag | Vestas Load and Power Mode
WAPC.LaPMFullLodHiWdMod | #N/A | WAPC. | LaPMFullLodHiWdMod | Load and Power Mode Mode for full load high wind | LaPM-Modus für Volllast bei starkem Wind | Modo de LaPM para viento de carga alta completa | Tryb LaPM dla pełnego obciążenia silnym wiatrem | Load and Power Mode Mode for full load high wind | Enum | Enum | Live Value | Long | Live Value
WAPC.LaPMFullLodHiWdMod_10m_End | #N/A | WAPC. | LaPMFullLodHiWdMod_10m_End | Load and Power Mode Mode for full load high wind (end) | LaPM-Modus für Volllast bei starkem Wind (end) | Modo de LaPM para viento de carga alta completa (end) | Tryb LaPM dla pełnego obciążenia silnym wiatrem (end) | Mode for full load high wind in 10 min period | Enum | Enum | Endvalue | Long | 10 minute tag | Vestas Load and Power Mode
WAPC.LaPMFullLodLoWdMod | #N/A | WAPC. | LaPMFullLodLoWdMod | Load and Power Mode Mode for full load low wind | LaPM-Modus für Volllast bei wenig Wind | Modo de LaPM para viento de carga baja completa | Tryb LaPM dla pełnego obciążenia przy słabym wietrze | Load and Power Mode Mode for full load low wind | Enum | Enum | Live Value | Long | Live Value
WAPC.LaPMFullLodLoWdMod_10m_End | #N/A | WAPC. | LaPMFullLodLoWdMod_10m_End | Load and Power Mode Mode for full load low wind (end) | LaPM-Modus für Volllast bei wenig Wind (end) | Modo de LaPM para viento de carga baja completa (end) | Tryb LaPM dla pełnego obciążenia przy słabym wietrze (end) | Mode for full load low wind in 10 min period | Enum | Enum | Endvalue | Long | 10 minute tag | Vestas Load and Power Mode
WAPC.LaPMFullLodTreshold | #N/A | WAPC. | LaPMFullLodTreshold | Load and Power Mode Treshold for switching full load | LaPM Schwellenwert für das Schalten von Volllast | Límite de LaPM para cambiar la carga completa | LaPM Próg dla przełączania pełnego obciążenia | Load and Power Mode Treshold for switching full load | m_s | m/s | Live Value | Double | Live Value
WAPC.LaPMFullLodTreshold_10m_End | #N/A | WAPC. | LaPMFullLodTreshold_10m_End | Load and Power Mode Treshold for switching full load (end) | LaPM Schwellenwert für das Schalten von Volllast (end) | Límite de LaPM para cambiar la carga completa (end) | LaPM Próg dla przełączania pełnego obciążenia (end) | Treshold for switching full load in 10 min period | m_s | m/s | Endvalue | Double | 10 minute tag | Vestas Load and Power Mode
WAPC.LaPMHorWdDir | #N/A | WAPC. | LaPMHorWdDir | Load and Power Mode Absolute Wind Direction | LaPM Absolute Windrichtung | Dirección del viento absoluta de LaPM | Bezwzględny kierunek wiatru LaPM | Load and Power Mode Absolute Wind Direction | deg | Degrees | Live Value | Double | Live Value
WAPC.LaPMHorWdDir_10m_Avg | #N/A | WAPC. | LaPMHorWdDir_10m_Avg | Load and Power Mode Absolute Wind Direction (avg) | LaPM Absolute Windrichtung (avg) | Dirección del viento absoluta de LaPM (avg) | Bezwzględny kierunek wiatru LaPM (avg) | Absolute wind direction in 10 min period | deg | Degrees | Average | Double | 10 minute tag | Vestas Load and Power Mode
WAPC.LaPMPaLodMod | #N/A | WAPC. | LaPMPaLodMod | Load and Power Mode Mode for partial load | LaPM-Modus für Teillast | Modo de LaPM para carga parcial | Tryb LaPM dla częściowego obciążenia | Load and Power Mode Mode for partial load | Enum | Enum | Live Value | Long | Live Value
WAPC.LaPMPaLodMod_10m_End | #N/A | WAPC. | LaPMPaLodMod_10m_End | Load and Power Mode Mode for partial load (end) | LaPM-Modus für Teillast (end) | Modo de LaPM para carga parcial (end) | Tryb LaPM dla częściowego obciążenia (end) | Mode for partial load in 10 min period | Enum | Enum | Endvalue | Long | 10 minute tag | Vestas Load and Power Mode
WAPC.LaPMStrSectorAng | #N/A | WAPC. | LaPMStrSectorAng | Load and Power Mode Sector Angle | LaPM Sektor Winkel | Ángulo del sector de LaPM | Kąt sektora LaPM | Load and Power Mode Sector Angle | deg | Degrees | Live Value | Double | Live Value
WAPC.LaPMStrSectorAng_10m_Avg | #N/A | WAPC. | LaPMStrSectorAng_10m_Avg | Load and Power Mode Sector Angle (avg) | LaPM Sektor Winkel (avg) | Ángulo del sector de LaPM (avg) | Kąt sektora LaPM (avg) | Sector angle begin in 10 min period | deg | Degrees | Average | Double | 10 minute tag | Vestas Load and Power Mode
WAPC.ManWDelGraSpt | #N/A | WAPC. | ManWDelGraSpt | Delta manual active power setpoint ramp rate | Manueller Deltawirkleistungssollwert Rampenrate | Delta de velocidad de aumento del punto de ajuste de la potencia activa manual | Ręczna nastawa Delta szybk. zmiany mocy czynnej | Delta manual active power setpoint ramp rate | W_s | W/s | Setpoint | Double | Live Value | Universal Park Controller (UPC)
WAPC.ManWDelSpt | #N/A | WAPC. | ManWDelSpt | UPC Delta manual active power setpoint | UPC manueller Deltawirkleistungssollwert | Punto de ajuste de la potencia activa manual de delta de UPC | UPC Delta ręczna nastawa mocy czynnej | Delta manual active power setpoint | W | W | Setpoint | Double | Live Value | Universal Park Controller (UPC)
WAPC.ManWDelSptSt | #N/A | WAPC. | ManWDelSptSt | UPC Delta manual active power setpoint state | Status des UPC manueller Deltawirkleistungssollwert | Estado del punto de ajuste de la potencia activa manual de delta de UPC | UPC Delta ręczny stan aktywnej wartości zadanej mocy | Delta manual active power setpoint state 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.ManWGraSpt | #N/A | WAPC. | ManWGraSpt | Absolute manual active power setpoint ramp rate | Absolute manuelle Wirkleistungssollwert-Rampenrate | Velocidad de aumento del punto de ajuste de la potencia activa manual absoluta | Bezwzględna ręczna nastawa szybkości zmiany mocy czynnej | Absolute manual active power setpoint ramp rate | W_s | W/s | Setpoint | Double | Live Value | Universal Park Controller (UPC)
WAPC.ManWSpt | #N/A | WAPC. | ManWSpt | UPC Absolute manual active power setpoint | UPC Absoluter manueller Wirkleistungssollwert | Punto de ajuste de la potencia activa manual absoluta de UPC | UPC Bezwzględna ręczna nastawa mocy czynnej | Absolute manual active power setpoint | W | W | Setpoint | Double | Live Value | Universal Park Controller (UPC)
WAPC.ManWSptNoSt | #N/A | WAPC. | ManWSptNoSt | UPC No manual active power setpoint state | Status des UPC Kein manueller Wirkleistungssollwert | Estado del punto de ajuste de la potencia activa no manual de UPC | UPC Brak ręcznego stanu nastawy mocy czynnej | No manual active power setpoint state 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.ManWSptSt | #N/A | WAPC. | ManWSptSt | UPC Absolute manual active power setpoint state | Status des UPC Absoluter manueller Wirkleistungssollwert | Estado del punto de ajuste de la potencia activa manual absoluta de UPC | UPC Bezwzględna ręcznie nastawa mocy czynnej stan | Absolute manual active power setpoint state 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.NoCommW | #N/A | WAPC. | NoCommW | UPC Power of turbines with no comm | UPC Leistung der Turbinen, die nicht kommunizieren | Potencia de las turbinas sin comunicación de UPC | UPC Moc turbin bez komun. | Power of turbines with no comm | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.NoCtlCnt | #N/A | WAPC. | NoCtlCnt | Number of not controllable units | Anzahl der nicht regelbaren Anlagen | Cantidad de unidades no controlables | Liczba jednostek niekontrolowanych | Number of No control | count | Count | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.OpCnt | #N/A | WAPC. | OpCnt | Number of operational units | Anzahl der betriebsfähigen Anlagen | Cantidad de unidades operativas | Liczba jednostek operacyjnych | Number of Operational | count | Count | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.OperSt | #N/A | WAPC. | OperSt | UPC State | Staus des UPC | Estado de UPC | Stan UPC | Park Controller State | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.OpTms_10m_Sum | #N/A | WAPC. | OpTms_10m_Sum | Time system has been online (sum) | Zeit, in der das System online war (sum) | Tiempo que el sistema ha estado online (sum) | Czas system jest online (sum) | Second counter that the system has been online | s | seconds | Summation | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.OpTurNum | WAPC.OpTurNum | WAPC. | OpTurNum | Actual number of wind turbines in operation | Tatsächliche Anzahl der Windturbinen in Betrieb | Cantidad real de turbinas eólicas en funcionamiento | Rzeczywista liczba turbin wiatrowych pracuj. | Actual number of wind turbines in operation | count | Count | Total Counter | Long | Live Value
WAPC.PCntrbW | #N/A | WAPC. | PCntrbW | UPC P Contribution | UPC P Beitrag | Contribución P de UPC | UPC Udział P | P Contribution | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.PsblW | #N/A | WAPC. | PsblW | UPC Possible Active Power | UPC mögliche Wirkleistung | Potencia activa posible de UPC | UPC Możliwa Moc czynna | Possible Power | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.PsblW_10m_Avg | #N/A | WAPC. | PsblW_10m_Avg | UPC Possible Active Power (avg) | UPC mögliche Wirkleistung (avg) | Potencia activa posible de UPC (avg) | UPC Możliwa Moc czynna (avg) | Possible Power Average | W | W | Average | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.PsblW_10m_Max | #N/A | WAPC. | PsblW_10m_Max | UPC Possible Active Power (max) | UPC mögliche Wirkleistung (max) | Potencia activa posible de UPC (max) | UPC Możliwa Moc czynna (max) | Possible Power Maximum | W | W | Maximum | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.PsblW_10m_Min | #N/A | WAPC. | PsblW_10m_Min | UPC Possible Active Power (min) | UPC mögliche Wirkleistung (min) | Potencia activa posible de UPC (min) | UPC Możliwa Moc czynna (min) | Possible Power Minimum | W | W | Minimum | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.PslbW_1s_End | #N/A | WAPC. | PslbW_1s_End | UPC Possible Active Power (end) | UPC mögliche Wirkleistung (end) | Potencia activa posible de UPC (end) | UPC Możliwa Moc czynna (end) | Possible Active Power | W | W | Endvalue | Double | Live Value | Universal Park Controller (UPC)
WAPC.ResWSpt | #N/A | WAPC. | ResWSpt | UPC Resulting active power setpoint | UPC resultierender Wirkleistungssollwert | Punto de ajuste de potencia activa resultante de UPC | UPC Wynikowa nastawa mocy czynnej | Resulting active power setpoint | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.ResWSpt_10m_Avg | #N/A | WAPC. | ResWSpt_10m_Avg | UPC Resulting active power setpoint (avg) | UPC resultierender Wirkleistungssollwert (avg) | Punto de ajuste de potencia activa resultante de UPC (avg) | UPC Wynikowa nastawa mocy czynnej (avg) | Resulting Setpoint (controller setpoint) Average | W | W | Average | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.ResWSpt_10m_Max | #N/A | WAPC. | ResWSpt_10m_Max | UPC Resulting active power setpoint (max) | UPC resultierender Wirkleistungssollwert (max) | Punto de ajuste de potencia activa resultante de UPC (max) | UPC Wynikowa nastawa mocy czynnej (max) | Resulting Setpoint (controller setpoint) Maximum | W | W | Maximum | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.ResWSpt_10m_Min | #N/A | WAPC. | ResWSpt_10m_Min | UPC Resulting active power setpoint (min) | UPC resultierender Wirkleistungssollwert (min) | Punto de ajuste de potencia activa resultante de UPC (min) | UPC Wynikowa nastawa mocy czynnej (min) | Resulting Setpoint (controller setpoint) Minimum | W | W | Minimum | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.ResWSpt_1s_End | #N/A | WAPC. | ResWSpt_1s_End | UPC Resulting active power setpoint (end) | UPC resultierender Wirkleistungssollwert (end) | Punto de ajuste de potencia activa resultante de UPC (end) | UPC Wynikowa nastawa mocy czynnej (end) | Resulting Setpoint (controller setpoint) | W | W | Endvalue | Double | Live Value | Universal Park Controller (UPC)
WAPC.SectorStopCnt | #N/A | WAPC. | SectorStopCnt | Number of units Stopped by sector management | Anzahl der Einheiten gestoppt durch Sektorverwaltung | Cantidad de unidades paradas por la gestión del sector | Liczba jednostek zatrzymanych przez zarządzanie sektorem | Number Stops by sector management | count | Count | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.ShadowStopCnt | #N/A | WAPC. | ShadowStopCnt | Number of units Stopped by shadow control | Anzahl der Einheiten gestoppt durch Schattenwurfmodul | Cantidad de unidades paradas por control de sombra | Liczba jednostek zatrzymanych przez kontrolę cienia | Number Stops by shadow control | count | Count | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.StManu | #N/A | WAPC. | StManu | UPC state OEM code | UPC-Status OEM-Code | Código del fabricante del equipo original de estado de UPC | Kod OEM stanu UPC | Park Controller state OEM code | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.StManuStr | #N/A | WAPC. | StManuStr | OEM state text | OEM-Statustext | Texto de estado del fabricante del equipo original | Tekst stanu OEM | OEM state string | String | String | Live Value | String | Live Value | Universal Park Controller (UPC)
WAPC.StopCnt | #N/A | WAPC. | StopCnt | Number of units Stopped | Anzahl der gestoppten Einheiten | Cantidad de unidades paradas | Liczba jednostek zatrzymanych | Number of Stops | count | Count | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.TraWDelSpt | #N/A | WAPC. | TraWDelSpt | UPC Delta trading active power setpoint | UPC Delta Trading-Wirkleistungssollwert | Delta de UPC de punto de ajuste de la potencia activa de comercio | UPC Delta trading nastawa mocy czynnej | Delta trading active power setpoint | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.TraWDelSptSt | #N/A | WAPC. | TraWDelSptSt | UPC Delta trading active power setpoint state | Stauts des UPC Delta Trading-Wirkleistungssollwert | Delta de UPC de estado del punto de ajuste de la potencia activa de comercio | UPC Delta trading nastawa mocy czynnej stan | Delta trading active power setpoint state 0: No comm 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.TraWSpt | #N/A | WAPC. | TraWSpt | UPC Absolute trading active power setpoint | UPC Absoluter Trading-Wirkleistungssollwert | Punto de ajuste de la potencia activa de comercio absoluto de UPC | UPC Trading absolutna nastawa mocy czynnej | Absolute trading active power setpoint | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.TraWSptSt | #N/A | WAPC. | TraWSptSt | UPC Absolute trading active power setpoint state | Status des UPC Absoluter Trading-Wirkleistungssollwert | Estado del punto de ajuste de la potencia activa de comercio absoluto de UPC | UPC Trading absolutna nastawa mocy czynnej stan | Absolute trading active power setpoint state 0: No comm 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.TurBasW | #N/A | WAPC. | TurBasW | UPC Turbine Basis Power | UPC Turbine Basisleistung | Potencia básica de la turbina de UPC | UPC Turbine Basis Power | Turbine # Basis Power | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.TurCsmpW | #N/A | WAPC. | TurCsmpW | UPC Turbine consumption | UPC Turbinenverbrauch | Consumo de la turbina de UPC | UPC pobór turbiny | Turbine consumption | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.TurDisW | #N/A | WAPC. | TurDisW | UPC Power of control disabled turbines | UPC Leistung der regelungsunfähigen Turbinen | Turbinas con el control de la potencia desactivado de UPC | UPC Moc turbin wyłączonych z kontroli | Power of control disabled turbines | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.TurLoLimW | #N/A | WAPC. | TurLoLimW | UPC Turbine Lower tolerance limit | UPC Turbine Untere Toleranzgrenze | Límite de tolerancia inferior de la turbina de UPC | Turbina UPC Dolna granica tolerancji | Turbine # Lower tolerance limit | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.TurMinW | #N/A | WAPC. | TurMinW | UPC Turbine Minimum setpoint | UPC Turbine Minimaler Sollwert | Punto de ajuste mínimo de la turbina de UPC | UPC Turbina Minimalna wartość nastawy | Turbine # Minimum setpoint | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.TurNomW | #N/A | WAPC. | TurNomW | UPC Turbine Nominal power | UPC Turbine Nennleistung | Potencia nominal de la turbina de UPC | Moc nominalna turbiny UPC | Turbine # Nominal power | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.TurPsblW | #N/A | WAPC. | TurPsblW | UPC Turbine Available power | UPC Turbine Verfügbare Leistung | Potencia disponible de la turbina de UPC | UPC Turbina Dostępna moc | Turbine # Available power | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.TurSpltPtW | #N/A | WAPC. | TurSpltPtW | UPC Turbine Split point | UPC Turbine Split point | Punto de separación de la turbina de UPC | UPC Turbina Punkt podziału | Turbine # Split point | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.TurSt | #N/A | WAPC. | TurSt | UPC Status of turbine for UPC Park Controller | UPC Status der Turbine für UPC Parkregler | Estado de la turbina de UPC para el controlador del parque de UPC | UPC Status turbiny dla sterownika UPC Park Controller | Status of turbine for SCI UPC Park Controller. 1=Turbine in operation 2=Turbine stopped by UPC 3=Turbine unavailable for control | Enum | Enum | Live Value | Long | Live Value
WAPC.TurStOk_1s_End | #N/A | WAPC. | TurStOk_1s_End | Number of turbines available for control (end) | Anzahl der für die Steuerung verfügbaren Turbinen (end) | Cantidad de turbinas disponibles para el control (end) | Liczba turbin dostępnych do sterowania (end) | Number of turbines available for control | count | count | Endvalue | Long | 1 second tag | Universal Park Controller (UPC)
WAPC.TurUpLimW | #N/A | WAPC. | TurUpLimW | UPC Turbine Upper tolerance limit | UPC Turbine Obere Toleranzgrenze | Límite de tolerancia superior de la turbina de UPC | UPC Turbina Górna granica tolerancji | Turbine # Upper tolerance limit | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.TurW | #N/A | WAPC. | TurW | UPC Turbine Active power | UPC Turbine Wirkleistung | Potencia activa de la turbina de UPC | UPC Turbina moc czynna | Turbine # Active power | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.TurWSpt | #N/A | WAPC. | TurWSpt | UPC Turbine Active power setpoint | UPC Turbine Wirkleistungssollwert | Punto de ajuste de la potencia activa de la turbina de UPC | UPC Turbina nastawa mocy czynnej | Turbine Active power setpoint | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.UtlWDelSpt | #N/A | WAPC. | UtlWDelSpt | UPC Delta utility active power setpoint | UPC Deltawirkleistungssollwert des Netzbetreibers | Delta de UPC de punto de ajuste de la potencia activa de utilidad | UPC Delta nastawa mocy czynnej operatora | Delta utility active power setpoint | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.UtlWDelSptSt | #N/A | WAPC. | UtlWDelSptSt | UPC Delta utility active power setpoint state | UPC Status des Deltawirkleistungssollwerts des Netzbetreibers | Delta de UPC de estado del punto de ajuste de la potencia activa de utilidad | UPC Delta nastawa mocy czynnej operatora stan | Delta utility active power setpoint state 0: No comm 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.UtlWSpt | #N/A | WAPC. | UtlWSpt | UPC Absolute utility active power setpoint | UPC Absoluter Wirkleistungssollwert des Netzbetreibers | Punto de ajuste de la potencia activa de utilidad absoluta de UPC | UPC Absolutna nastawa operatora mocy czynnej stan | Absolute utility active power setpoint | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.UtlWSptSt | #N/A | WAPC. | UtlWSptSt | UPC Absolute utility active power setpoint state | UPC Status des Absoluten Wirkleistungssollwertes des Netzbetreibers | Estado del punto de ajuste de la potencia activa de utilidad absoluta de UPC | UPC Absolutna nastawa operatora mocy czynnej | Absolute utility active power setpoint state 0: No comm 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WAPC.VA | WAPC.VA | WAPC. | VA | Wind power plant apparent power | Scheinleistung der Windkraftanlage | Potencia aparente de la central eólica | Elektrownia wiatrowa moc pozorna | Wind power plant apparent power | VAr | VAr | Live Value | Double | Live Value
WAPC.VAAct | WAPC.VAAct | WAPC. | VAAct | Activate apparent power control function | Aktivieren der Scheinleistungsregelungsfunktion | Activar función de control de potencia aparente | Włączanie funkcji sterowania mocą pozorną | Activate apparent power control function | Enum | Enum | Live Value | Long | Live Value
WAPC.VAEna | WAPC.VAEna | WAPC. | VAEna | Active power control mode enabled controlling apparent power | Wirkleistungsregelungsmodus ermöglicht Scheinleistungsregelung | Módulo de control de potencia activa habilitado que controla la potencia aparente | Aktywny tryb sterowania mocą czynną pozwala na sterowanie mocą pozorną | Active power control mode enabled controlling apparent power | Enum | Enum | Live Value | Long | Live Value
WAPC.VASpt | WAPC.VASpt | WAPC. | VASpt | Apparent power setpoint | Scheinleistungssollwert | Punto de ajuste de la potencia aparente | Nastawa mocy pozornej | Set reference value for the wind power plant apparent power output | W | W | Setpoint | Double | Live Value
WAPC.W | WAPC.W | WAPC. | W | Wind power plant active generation | Windkraftanlage Wirkleistung | Generación activa de la central eólica | Produkcja energii elektr. wiatrowej | Wind power plant active generation | W | W | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.W_10m_Avg | #N/A | WAPC. | W_10m_Avg | Active Power (avg) | Wirkleistung (avg) | Potencia activa (avg) | Moc czynna (avg) | Active power Average | W | W | Average | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.W_10m_Max | #N/A | WAPC. | W_10m_Max | Active Power (max) | Wirkleistung (max) | Potencia activa (max) | Moc czynna (max) | Active power Maximum | W | W | Maximum | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.W_10m_Min | #N/A | WAPC. | W_10m_Min | Active Power (min) | Wirkleistung (min) | Potencia activa (min) | Moc czynna (min) | Active power Minimum | W | W | Minimum | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.W_1s_End | #N/A | WAPC. | W_1s_End | Active Power (end) | Wirkleistung (end) | Potencia activa (end) | Moc czynna (end) | Active Power | W | W | Endvalue | Double | Live Value | Universal Park Controller (UPC)
WAPC.WAct | WAPC.WAct | WAPC. | WAct | Activate active power control function | Aktivieren der Wirkleistungsregelungsfunktion | Activar función de control de potencia activa | Włączanie funkcji sterowania mocą czynną | Activate active power control function | Enum | Enum | Live Value | Long | Live Value
WAPC.WCap | WAPC.WCap | WAPC. | WCap | Wind power plant active power capability | Wirkleistungsfähigkeit der Windkraftanlage | Capacidad de potencia activa de la central eólica | Zdolność prod. mocy czynnej elektr. wiatrowej | Wind power plant active power output capability | W | W | Live Value | Double | Live Value
WAPC.WDel | WAPC.WDel | WAPC. | WDel | Wind power plant active power reserve | Wirkleistungsreserve der Windkraftanlagen | Reserva de potencia activa de la central eólica | Rezerwa mocy czynnej elektr. wiatrowej | Wind power plant active power reserve utilizing the delta function – the difference between active power generation capability and active | W | W | Live Value | Double | Live Value
WAPC.WDnGraSpt | WAPC.WDnGraSpt | WAPC. | WDnGraSpt | Setpoint gradient ramp down | Sollwert-Gradient-Rampe abwärts | Disminución de velocidad del gradiente del punto de ajuste | Nastawa gradientu spadku | Set reference value for gradient ramping down the wind power plant active power output | W_s | W/s | Setpoint | Double | Live Value
WAPC.WdSpd | #N/A | WAPC. | WdSpd | Wind speed | Windgeschwindigkeit | Velocidad del viento | Prędkość wiatru | Wind speed | m_s | m/s | Live Value | Double | Live Value | Universal Park Controller (UPC)
WAPC.WdSpd_10m_Avg | #N/A | WAPC. | WdSpd_10m_Avg | Wind speed (avg) | Windgeschwindigkeit (avg) | Velocidad del viento (avg) | Prędkość wiatru (avg) | Park Average Wind Speed Average | m_s | m/s | Average | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.WdSpd_10m_Max | #N/A | WAPC. | WdSpd_10m_Max | Wind speed (max) | Windgeschwindigkeit (max) | Velocidad del viento (max) | Prędkość wiatru (max) | Park Average Wind Speed Maximum | m_s | m/s | Maximum | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.WdSpd_10m_Min | #N/A | WAPC. | WdSpd_10m_Min | Wind speed (min) | Windgeschwindigkeit (min) | Velocidad del viento (min) | Prędkość wiatru (min) | Park Average Wind Speed Minimum | m_s | m/s | Minimum | Double | 10 minute tag | Universal Park Controller (UPC)
WAPC.WdSpd_1s_End | #N/A | WAPC. | WdSpd_1s_End | Wind speed (end) | Windgeschwindigkeit (end) | Velocidad del viento (end) | Prędkość wiatru (end) | Park Average Wind Speed | m_s | m/s | Endvalue | Double | 1 second tag | Universal Park Controller (UPC)
WAPC.WLim | #N/A | WAPC. | WLim | Active power limit | Wirkleistungsbegrenzung | Límite de potencia activa | Limit mocy czynnej | Active power limit | W | W | Live Value | Double | Live Value
WAPC.WLimEna | WAPC.WLimEna | WAPC. | WLimEna | Active power limitation mode enabled | Modus der Wirkleistungsbegrenzung aktiviert | Modo de limitación de la potencia activa habilitado | Włączony tryb ograniczenia mocy czynnej | Active power limitation mode enabled | Enum | Enum | Live Value | Long | Live Value
WAPC.WMinCap | WAPC.WMinCap | WAPC. | WMinCap | Wind power plant minimum capability active power | Mindestwirkleistungsfähigkeit der Windkraftanlage | Capacidad mínima de la potencia activa de la central eólica | Elektrownia wiatrowa minimalna moc czynna | Wind power plant minimum capability active power | W | W | Live Value | Double | Live Value
WAPC.WSpt | WAPC.WSpt | WAPC. | WSpt | Wind power plant Active power Setpoint | Windkraftanlage Wirkleistungssollwert | Punto de ajuste de potencia activa de la central eólica | Elektrownia wiatrowa moc czynna Nastawa | Set reference value for the wind power plant active power output | W | W | Setpoint | Double | Live Value | Universal Park Controller (UPC)
WAPC.WSpt_10m_Avg | #N/A | WAPC. | WSpt_10m_Avg | Wind power plant Active power Setpoint (avg) | Windkraftanlage Wirkleistungssollwert (avg) | Punto de ajuste de potencia activa de la central eólica (avg) | Elektrownia wiatrowa moc czynna Nastawa (avg) | Set reference value for the wind power plant active power output | W | W | Average | Double | 10 minute tag
WAPC.WSpt_10m_Max | #N/A | WAPC. | WSpt_10m_Max | Wind power plant Active power Setpoint (max) | Windkraftanlage Wirkleistungssollwert (max) | Punto de ajuste de potencia activa de la central eólica (max) | Elektrownia wiatrowa moc czynna Nastawa (max) | Set reference value for the wind power plant active power output | W | W | Maximum | Double | 10 minute tag
WAPC.WSpt_10m_Min | #N/A | WAPC. | WSpt_10m_Min | Wind power plant Active power Setpoint (min) | Windkraftanlage Wirkleistungssollwert (min) | Punto de ajuste de potencia activa de la central eólica (min) | Elektrownia wiatrowa moc czynna Nastawa (min) | Set reference value for the wind power plant active power output | W | W | Minimum | Double | 10 minute tag
WAPC.WSptSrc_10m_Avg | #N/A | WAPC. | WSptSrc_10m_Avg | Turbine active power generation setpoint source (avg) | Turbinen-Wirkleistungserzeugung Sollwertquelle (avg) | Fuente del punto de ajuste de generación de potencia activa de la turbina (avg) | Źródło zadanej mocy czynnej turbiny (avg) | Turbine active power generation setpoint source | Enum | Enum | Average | Long | 10 minute tag
WAPC.WUpGraSpt | WAPC.WUpGraSpt | WAPC. | WUpGraSpt | Setpoint gradient ramp up | Anstieg des Sollwertgradienten | Aumento de velocidad del gradiente del punto de ajuste | Nastawa gradientu wzrostu | Set reference value for gradient ramping up the wind power plant active power output | W_s | W/s | Setpoint | Double | Live Value
WAVL.AvlTms | #N/A | WAVL. | AvlTms | Turbine availability time | Zeit der Turbinenverfügbarkeit | Tiempo de disponibilidad de la turbina | Czas dostępności turbiny | Turbine availability time in seconds (implementation specific) | s | seconds | Total Counter | Long | Live Value
WAVL.AvlTms_Mly_Sum | #N/A | WAVL. | AvlTms_Mly_Sum | Turbine availability time (sum) | Zeit der Turbinenverfügbarkeit (sum) | Tiempo de disponibilidad de la turbina (sum) | Czas dostępności turbiny (sum) | Turbine availability time in seconds (implementation specific) | s | seconds | Summation | Long | Monthly tag
WAVL.CnttAvl | #N/A | WAVL. | CnttAvl | Contractual availability | Vertragliche Verfügbarkeit | Disponibilidad contractual | Dostępność umowna | Contractual availability during turbine lifetime | percent | percent | Live Value | Double | Live Value
WAVL.CnttAvl_10m_End | #N/A | WAVL. | CnttAvl_10m_End | Contractual availability (end) | Vertragliche Verfügbarkeit (end) | Disponibilidad contractual (end) | Dostępność umowna (end) | Contractual availability during turbine lifetime, 10 minute end | percent | percent | Endvalue | Double | 10 minute tag
WAVL.CnttAvl_Dly_Sum | #N/A | WAVL. | CnttAvl_Dly_Sum | Contractual availability (sum) | Vertragliche Verfügbarkeit (sum) | Disponibilidad contractual (sum) | Dostępność umowna (sum) | Contractual availability in each Daily period | percent | percent | Summation | Double | Daily tag
WAVL.CnttAvl_Mly_Sum | #N/A | WAVL. | CnttAvl_Mly_Sum | Contractual availability (sum) | Vertragliche Verfügbarkeit (sum) | Disponibilidad contractual (sum) | Dostępność umowna (sum) | Contractual availability in each Monthly period | percent | percent | Summation | Double | Monthly tag
WAVL.CnttAvl_Wly_Sum | #N/A | WAVL. | CnttAvl_Wly_Sum | Contractual availability (sum) | Vertragliche Verfügbarkeit (sum) | Disponibilidad contractual (sum) | Dostępność umowna (sum) | Contractual availability in each Weekly period | percent | percent | Summation | Double | Weekly tag
WAVL.CnttAvl_Yly_Sum | #N/A | WAVL. | CnttAvl_Yly_Sum | Contractual availability (sum) | Vertragliche Verfügbarkeit (sum) | Disponibilidad contractual (sum) | Dostępność umowna (sum) | Contractual availability in each Yearly period | percent | percent | Summation | Double | Yearly tag
WAVL.Ia | WAVL.Ia | WAVL. | Ia | Information available | Information verfügbar | Información disponible | Dostępne informacje | Information available | Enum | Enum | Live Value | Long | Live Value
WAVL.Iafm | WAVL.Iafm | WAVL. | Iafm | Information available force majeure | Verfügbare Information höhere Gewalt | Información disponible sobre fuerza mayor | Informacje dostępne siła wyższa | Information available force majeure | Enum | Enum | Live Value | Long | Live Value
WAVL.Iano | WAVL.Iano | WAVL. | Iano | Information available nonoperative | Verfügbare Information nicht-operativ | Información disponible sobre no operativo | Dostępne informacje nieoperacyjne | Information available nonoperative | Enum | Enum | Live Value | Long | Live Value
WAVL.Ianofo | WAVL.Ianofo | WAVL. | Ianofo | Information available nonoperative forced outage | Verfügbare Information nicht operativ erzwungener Ausfall | Información disponible sobre no operativo por fuerza mayor | Dostępne informacje nieoperacyjne wymuszone odstawienie | Information available nonoperative forced outage | Enum | Enum | Live Value | Long | Live Value
WAVL.Ianopca | WAVL.Ianopca | WAVL. | Ianopca | Information available nonoperative planned corrective actions | Verfügbare Information nicht operativ geplante Korrekturmaßnahmen | Información disponible sobre acciones correctivas planificadas no operativas | Dostępne informacje nieoperacyjne planowe działania naprawcze | Information available nonoperative planned corrective actions | Enum | Enum | Live Value | Long | Live Value
WAVL.Ianos | WAVL.Ianos | WAVL. | Ianos | Information available nonoperative suspended | Verfügbare Information nicht operativ ausgesetzt | Información disponible sobre no operativo suspendido | Dostępne informacje nieoperacyjne zatrzymanie | Information available nonoperative suspended | Enum | Enum | Live Value | Long | Live Value
WAVL.Ianosm | WAVL.Ianosm | WAVL. | Ianosm | Information available nonoperative scheduled maintenance | Information verfügbar nichtoperativ geplante Wartung | Información disponible sobre mantenimiento programado no operativo | Dostępne informacje nieoperacyjne planowa konserwacja | Information available nonoperative scheduled maintenance | Enum | Enum | Live Value | Long | Live Value
WAVL.Iao | WAVL.Iao | WAVL. | Iao | Information available operative | Verfügbare Information operativ | Información disponible sobre operativo | Dostępne informacje operacyjne | Information available operative | Enum | Enum | Live Value | Long | Live Value
WAVL.Iaog | WAVL.Iaog | WAVL. | Iaog | Information available operative generating | Verfügbare Information operativ erzeugend | Información disponible sobre operativo generador | Informacje dostępne operacyjne generacja | Information available operative generating | Enum | Enum | Live Value | Long | Live Value
WAVL.Iaogfp | WAVL.Iaogfp | WAVL. | Iaogfp | Information available operative generating with full performance | Verfügbare Information operativ generierend mit voller Leistung | Información disponible sobre operativo generador con pleno rendimiento | Dostępne informacje operacyjne generacja z pełną wydajnością | Information available operative generating with full performance | Enum | Enum | Live Value | Long | Live Value
WAVL.Iaogpp | WAVL.Iaogpp | WAVL. | Iaogpp | Information available operative generating with partial performance | Verfügbare Information operativ generierend mit Teilleistung | Información disponible sobre operativo generador con rendimiento parcial | Dostępne informacje operacyjne generacja z częściową wydajnością | Information available operative generating with partial performance | Enum | Enum | Live Value | Long | Live Value
WAVL.Iaong | WAVL.Iaong | WAVL. | Iaong | Information available operative nongenerating | Verfügbare Information operativ nicht erzeugend | Información disponible sobre operativo no generador | Dostępne informacje operacyjne niegenerujące | Information available operative nongenerating | Enum | Enum | Live Value | Long | Live Value
WAVL.Iaongel | WAVL.Iaongel | WAVL. | Iaongel | Information available operative nongenerating out of electrical specification | Verfügbare Information operativ nicht-erzeugend außerhalb der elektrischen Spezifikation | Información disponible sobre operativo no generador al margen de las especificaciones eléctricas | Dostępne informacje operacyjne niegenerujące przekr. specyfikacji elektrycznej | Information available operative nongenerating out of electrical specification | Enum | Enum | Live Value | Long | Live Value
WAVL.Iaongen | WAVL.Iaongen | WAVL. | Iaongen | Information available operative nongenerating out of environmental specification | Verfügbare Information operativ nicht-erzeugend außerhalb der Umweltspezifikation | Información disponible sobre operativo no generador al margen de las especificaciones ambientales | Dostępne informacje operacyjne niegenerujące przekr. specyfikacji środowiskowej | Information available operative nongenerating out of environmental specification | Enum | Enum | Live Value | Long | Live Value
WAVL.Iaongrs | WAVL.Iaongrs | WAVL. | Iaongrs | Information available operative nongenerating requested shutdown | Verfügbare Information operativ nicht erzeugend angeforderte Abschaltung | Información disponible sobre operativo no generador apagado requerido | Dostępne informacje operacyjne niegenerujące wymuszone zatrzymanie | Information available operative nongenerating requested shutdown | Enum | Enum | Live Value | Long | Live Value
WAVL.Iaongts | WAVL.Iaongts | WAVL. | Iaongts | Information available operative nongenerating technical standby | Verfügbare Information operativ nicht erzeugend technischer Bereitschaftsdienst | Información disponible sobre operativo no generador espera técnica | Dostępne informacje operacyjne niegenerujące gotowość techniczna | Information available operative nongenerating technical standby | Enum | Enum | Live Value | Long | Live Value
WAVL.Iu | WAVL.Iu | WAVL. | Iu | Information unavailable | Information nicht verfügbar | Información indisponible | Informacje niedostępne | Information unavailable | Enum | Enum | Live Value | Long | Live Value
WAVL.OpTmsRs | WAVL.OpTmsRs | WAVL. | OpTmsRs | Operation time | Betriebszeit | Tiempo de funcionamiento | Czas pracy | Operation time in seconds (implementation specific) | s | seconds | Total Counter | Long | Live Value
WAVL.PwrAvl | #N/A | WAVL. | PwrAvl | Powerbased availability | Leistungsabhängige Verfügbarkeit | Disponibilidad en base a la potencia | Dostępność energetyczna | Powerbased availability | percent | percent | Live Value | Double | Live Value
WAVL.PwrAvl_Dly_Sum | #N/A | WAVL. | PwrAvl_Dly_Sum | Powerbased availability (sum) | Leistungsabhängige Verfügbarkeit (sum) | Disponibilidad en base a la potencia (sum) | Dostępność energetyczna (sum) | Powerbased availability in each Daily period | percent | percent | Summation | Double | Daily tag
WAVL.PwrAvl_Mly_Sum | #N/A | WAVL. | PwrAvl_Mly_Sum | Powerbased availability (sum) | Leistungsabhängige Verfügbarkeit (sum) | Disponibilidad en base a la potencia (sum) | Dostępność energetyczna (sum) | Powerbased availability in each Monthly period | percent | percent | Summation | Double | Monthly tag
WAVL.PwrAvl_Wly_Sum | #N/A | WAVL. | PwrAvl_Wly_Sum | Powerbased availability (sum) | Leistungsabhängige Verfügbarkeit (sum) | Disponibilidad en base a la potencia (sum) | Dostępność energetyczna (sum) | Powerbased availability in each Weekly period | percent | percent | Summation | Double | Weekly tag
WAVL.PwrAvl_Yly_Sum | #N/A | WAVL. | PwrAvl_Yly_Sum | Powerbased availability (sum) | Leistungsabhängige Verfügbarkeit (sum) | Disponibilidad en base a la potencia (sum) | Dostępność energetyczna (sum) | Powerbased availability in each Yearly period | percent | percent | Summation | Double | Yearly tag
WAVL.SysAvl | WAVL.SysAvl | WAVL. | SysAvl | System availability | Verfügbarkeit der Anlage | Disponibilidad del sistema | Dostępność systemu | System availability (implementation specific) | percent | percent | Live Value | Double | Live Value
WAVL.TurAvl | WAVL.TurAvl | WAVL. | TurAvl | Turbine availability | Verfügbarkeit der Turbine | Disponibilidad de la turbina | Dostępność turbin | Turbine availability (implementation specific) | percent | percent | Live Value | Double | Live Value
WAVL.TurAvl_10m_End | #N/A | WAVL. | TurAvl_10m_End | Turbine availability (end) | Verfügbarkeit der Turbine (end) | Disponibilidad de la turbina (end) | Dostępność turbin (end) | Turbine availability (implementation specific), 10 minute end | percent | percent | Endvalue | Double | 10 minute tag
WAVL.TurAvl_Dly_Sum | #N/A | WAVL. | TurAvl_Dly_Sum | Turbine availability Daily (sum) | Verfügbarkeit der Turbine Täglich (sum) | Disponibilidad de la turbina diaria (sum) | Dostępność turbin Dzienna (sum) | Turbine availability (implementation specific) in each Daily period | percent | percent | Summation | Double | Daily tag
WAVL.TurAvl_Mly_Sum | #N/A | WAVL. | TurAvl_Mly_Sum | Turbine availability Monthly (sum) | Verfügbarkeit der Turbine Monatlich (sum) | Disponibilidad de la turbina mensual (sum) | Dostępność turbin Miesięczna (sum) | Turbine availability (implementation specific) in each Monthly period | percent | percent | Summation | Double | Monthly tag
WAVL.TurAvl_Wly_Sum | #N/A | WAVL. | TurAvl_Wly_Sum | Turbine availability Weekly (sum) | Verfügbarkeit der Turbine Wöchentlich (sum) | Disponibilidad de la turbina semanal (sum) | Dostępność turbin Tygodniowa (sum) | Turbine availability (implementation specific) in each Weekly period | percent | percent | Summation | Double | Weekly tag
WAVL.TurAvl_Yly_Sum | #N/A | WAVL. | TurAvl_Yly_Sum | Turbine availability Yearly (sum) | Verfügbarkeit der Turbine Jährlich (sum) | Disponibilidad de la turbina anual (sum) | Dostępność turbin Roczna (sum) | Turbine availability (implementation specific) in each Yearly period | percent | percent | Summation | Double | Yearly tag
WCNV.AirTmp | #N/A | WCNV. | AirTmp | Converter Air Temp | Konverter Lufttemperatur | Temperatura del aire del convertidor | Konwerter Temp powiet. | Converter Air temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.AirTmp_10m_Avg | #N/A | WCNV. | AirTmp_10m_Avg | Converter Air Temp (avg) | Konverter Lufttemperatur (avg) | Temperatura del aire del convertidor (avg) | Konwerter Temp powiet. (avg) | Converter Air temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.AirTmp_10m_Max | #N/A | WCNV. | AirTmp_10m_Max | Converter Air Temp (max) | Konverter Lufttemperatur (max) | Temperatura del aire del convertidor (max) | Konwerter Temp powiet. (max) | Converter Air temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.AirTmp_10m_Min | #N/A | WCNV. | AirTmp_10m_Min | Converter Air Temp (min) | Konverter Lufttemperatur (min) | Temperatura del aire del convertidor (min) | Konwerter Temp powiet. (min) | Converter Air temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.AirTmp_10m_Std | #N/A | WCNV. | AirTmp_10m_Std | Converter Air Temp (std) | Konverter Lufttemperatur (std) | Temperatura del aire del convertidor (std) | Konwerter Temp powiet. (std) | Converter Air temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.ASpt | #N/A | WCNV. | ASpt | Converter current set point | Stromwandler-Sollwert | Punto de ajuste de la corriente del convertidor | Konwerter bież. nastawa | Converter current set point | A | A | Setpoint | Double | Live Value | Used in some specialised presentations
WCNV.ASpt_10m_Avg | #N/A | WCNV. | ASpt_10m_Avg | Converter current set point | Stromwandler-Sollwert | Punto de ajuste de la corriente del convertidor | Konwerter bież. nastawa | Converter current set point | A | A | Setpoint | Double | 10 minute tag | Common tags for analysis
WCNV.ASpt_10m_Max | #N/A | WCNV. | ASpt_10m_Max | Converter current set point | Stromwandler-Sollwert | Punto de ajuste de la corriente del convertidor | Konwerter bież. nastawa | Converter current set point | A | A | Setpoint | Double | 10 minute tag | Common tags for analysis
WCNV.ASpt_10m_Min | #N/A | WCNV. | ASpt_10m_Min | Converter current set point | Stromwandler-Sollwert | Punto de ajuste de la corriente del convertidor | Konwerter bież. nastawa | Converter current set point | A | A | Setpoint | Double | 10 minute tag | Common tags for analysis
WCNV.ASpt_10m_Std | #N/A | WCNV. | ASpt_10m_Std | Converter current set point | Stromwandler-Sollwert | Punto de ajuste de la corriente del convertidor | Konwerter bież. nastawa | Converter current set point | A | A | Setpoint | Double | 10 minute tag | Common tags for analysis
WCNV.AuxTrfTmp | #N/A | WCNV. | AuxTrfTmp | Auxiliary Transformer Temp | Hilfstransformator Temperatur | Temperatura del transformador auxiliar | Transformator pomocniczy Temp | Auxiliary transformer temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.AuxTrfTmp_10m_Avg | #N/A | WCNV. | AuxTrfTmp_10m_Avg | Auxiliary Transformer Temp (avg) | Hilfstransformator Temperatur (avg) | Temperatura del transformador auxiliar (avg) | Transformator pomocniczy Temp (avg) | Auxiliary transformer temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.AuxTrfTmp_10m_Max | #N/A | WCNV. | AuxTrfTmp_10m_Max | Auxiliary Transformer Temp (max) | Hilfstransformator Temperatur (max) | Temperatura del transformador auxiliar (max) | Transformator pomocniczy Temp (max) | Auxiliary transformer temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.AuxTrfTmp_10m_Min | #N/A | WCNV. | AuxTrfTmp_10m_Min | Auxiliary Transformer Temp (min) | Hilfstransformator Temperatur (min) | Temperatura del transformador auxiliar (min) | Transformator pomocniczy Temp (min) | Auxiliary transformer temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.AuxTrfTmp_10m_Std | #N/A | WCNV. | AuxTrfTmp_10m_Std | Auxiliary Transformer Temp (std) | Hilfstransformator Temperatur (std) | Temperatura del transformador auxiliar (std) | Transformator pomocniczy Temp (std) | Auxiliary transformer temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.BusBarTmp | #N/A | WCNV. | BusBarTmp | Converter Busbar Temp | Konverter Sammelschienen-Temperatur | Temperatura del embarrado del convertidor | Konwerter Magistrala Temp | Converter BusBar Temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.BusBarTmp_10m_Avg | #N/A | WCNV. | BusBarTmp_10m_Avg | Converter Busbar Temp (avg) | Konverter Sammelschienen-Temperatur (avg) | Temperatura del embarrado del convertidor (avg) | Konwerter Magistrala Temp (avg) | Converter BusBar Temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.BusBarTmp_10m_Max | #N/A | WCNV. | BusBarTmp_10m_Max | Converter Busbar Temp (max) | Konverter Sammelschienen-Temperatur (max) | Temperatura del embarrado del convertidor (max) | Konwerter Magistrala Temp (max) | Converter BusBar Temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.BusBarTmp_10m_Min | #N/A | WCNV. | BusBarTmp_10m_Min | Converter Busbar Temp (min) | Konverter Sammelschienen-Temperatur (min) | Temperatura del embarrado del convertidor (min) | Konwerter Magistrala Temp (min) | Converter BusBar Temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.BusBarTmp_10m_Std | #N/A | WCNV. | BusBarTmp_10m_Std | Converter Busbar Temp (std) | Konverter Sammelschienen-Temperatur (std) | Temperatura del embarrado del convertidor (std) | Konwerter Magistrala Temp (std) | Converter BusBar Temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.BypassCnt | #N/A | WCNV. | BypassCnt | Number of activations of the bypass contactor | Anzahl der Aktivierungen des Bypass-Schützes | Número de activaciones del contactor de bypass | Liczba aktywacji stycznika obejściowego | Number of activations of the bypass contactor | count | Count | Total Counter | Long | Live Value
WCNV.BypassCnt_10m_End | #N/A | WCNV. | BypassCnt_10m_End | Number of activations of the bypass contactor (end) | Anzahl der Aktivierungen des Bypass-Schützes (end) | Número de activaciones del contactor de bypass (end) | Liczba aktywacji stycznika obejściowego (end) | Number of activations of the bypass contactor | count | Count | Endvalue | Long | 10 minute tag
WCNV.BypassTms | #N/A | WCNV. | BypassTms | Time the by-pass contactor has been activated | Zeit, in der das Bypass-Schütz aktiviert wurde | Tiempo que el contactor de bypass ha estado activado | Czas aktywacji stycznika przy przejściach | Time the by-pass contactor has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.BypassTms_10m_End | #N/A | WCNV. | BypassTms_10m_End | Time the by-pass contactor has been activated (end) | Zeit, in der das Bypass-Schütz aktiviert wurde (end) | Tiempo que el contactor de bypass ha estado activado (end) | Czas aktywacji stycznika przy przejściach (end) | Time the by-pass contactor has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.ClAirTmp | #N/A | WCNV. | ClAirTmp | Converter Cooling Air Temp | kühllufttemperatur des Konverters | Temperatura del aire de refrigeración del convertidor | Konwerter Temp pow.chłodz. | Converter cooling Air temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.ClAirTmp_10m_Avg | #N/A | WCNV. | ClAirTmp_10m_Avg | Converter Cooling Air Temp (avg) | kühllufttemperatur des Konverters (avg) | Temperatura del aire de refrigeración del convertidor (avg) | Konwerter Temp pow.chłodz. (avg) | Converter cooling Air temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.ClAirTmp_10m_Max | #N/A | WCNV. | ClAirTmp_10m_Max | Converter Cooling Air Temp (max) | kühllufttemperatur des Konverters (max) | Temperatura del aire de refrigeración del convertidor (max) | Konwerter Temp pow.chłodz. (max) | Converter cooling Air temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.ClAirTmp_10m_Min | #N/A | WCNV. | ClAirTmp_10m_Min | Converter Cooling Air Temp (min) | kühllufttemperatur des Konverters (min) | Temperatura del aire de refrigeración del convertidor (min) | Konwerter Temp pow.chłodz. (min) | Converter cooling Air temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.ClAirTmp_10m_Std | #N/A | WCNV. | ClAirTmp_10m_Std | Converter Cooling Air Temp (std) | kühllufttemperatur des Konverters (std) | Temperatura del aire de refrigeración del convertidor (std) | Konwerter Temp pow.chłodz. (std) | Converter cooling Air temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.ClSt | WCNV.ClSt | WCNV. | ClSt | Converter Cooling System Status | Status des Konverterkühlsystems | Estado del sistema de refrigeración del convertidor | Stan systemu chłodzenia konwertera | Status of converter cooling system | Enum | Enum | Live Value | Long | Live Value
WCNV.ClWtrPress | #N/A | WCNV. | ClWtrPress | Converter Cooling Water Pressure | Kühlwasserdruck des Konverters | Presión del agua de refrigeración del convertidor | Ciśnienie wody chłodzącej konwertera | Converter cooling water Pressure | bar | bar | Live Value | Double | Live Value
WCNV.ClWtrPress_10m_Avg | #N/A | WCNV. | ClWtrPress_10m_Avg | Converter Cooling Water Pressure (avg) | Kühlwasserdruck des Konverters (avg) | Presión del agua de refrigeración del convertidor (avg) | Ciśnienie wody chłodzącej konwertera (avg) | Converter cooling water Pressure | bar | bar | Average | Double | 10 minute tag
WCNV.ClWtrPress_10m_Max | #N/A | WCNV. | ClWtrPress_10m_Max | Converter Cooling Water Pressure (max) | Kühlwasserdruck des Konverters (max) | Presión del agua de refrigeración del convertidor (max) | Ciśnienie wody chłodzącej konwertera (max) | Converter cooling water Pressure | bar | bar | Maximum | Double | 10 minute tag
WCNV.ClWtrPress_10m_Min | #N/A | WCNV. | ClWtrPress_10m_Min | Converter Cooling Water Pressure (min) | Kühlwasserdruck des Konverters (min) | Presión del agua de refrigeración del convertidor (min) | Ciśnienie wody chłodzącej konwertera (min) | Converter cooling water Pressure | bar | bar | Minimum | Double | 10 minute tag
WCNV.ClWtrPress_10m_Std | #N/A | WCNV. | ClWtrPress_10m_Std | Converter Cooling Water Pressure (std) | Kühlwasserdruck des Konverters (std) | Presión del agua de refrigeración del convertidor (std) | Ciśnienie wody chłodzącej konwertera (std) | Converter cooling water Pressure | bar | bar | Standard Deviation | Double | 10 minute tag
WCNV.ClWtrTmp | #N/A | WCNV. | ClWtrTmp | Converter Cooling Water Temp | Kühlwassertemperatur des Konverters | Temperatura del agua de refrigeración del convertidor | Konwerter Temp wody chłodz. | Converter cooling water temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.ClWtrTmp_10m_Avg | #N/A | WCNV. | ClWtrTmp_10m_Avg | Converter Cooling Water Temp (avg) | Kühlwassertemperatur des Konverters (avg) | Temperatura del agua de refrigeración del convertidor (avg) | Konwerter Temp wody chłodz. (avg) | Converter cooling water temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.ClWtrTmp_10m_Max | #N/A | WCNV. | ClWtrTmp_10m_Max | Converter Cooling Water Temp (max) | Kühlwassertemperatur des Konverters (max) | Temperatura del agua de refrigeración del convertidor (max) | Konwerter Temp wody chłodz. (max) | Converter cooling water temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.ClWtrTmp_10m_Min | #N/A | WCNV. | ClWtrTmp_10m_Min | Converter Cooling Water Temp (min) | Kühlwassertemperatur des Konverters (min) | Temperatura del agua de refrigeración del convertidor (min) | Konwerter Temp wody chłodz. (min) | Converter cooling water temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.ClWtrTmp_10m_Std | #N/A | WCNV. | ClWtrTmp_10m_Std | Converter Cooling Water Temp (std) | Kühlwassertemperatur des Konverters (std) | Temperatura del agua de refrigeración del convertidor (std) | Konwerter Temp wody chłodz. (std) | Converter cooling water temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.CnvOpSt | WCNV.CnvOpSt | WCNV. | CnvOpSt | Converter Operation Status | Status des Konverterbetriebs | Estado de funcionamiento del convertidor | Stan operacji konwertera | Converter Operation Status | Enum | Enum | Live Value | Long | Live Value
WCNV.CtlPnlFanCnt | #N/A | WCNV. | CtlPnlFanCnt | Number of activations of the control panel fan | Anzahl der Aktivierungen des Bedienfeldlüfters | Número de activaciones del ventilador del panel de control | Liczba aktywacji wentylatora panelu sterowania | Number of activations of the control panel fan | count | Count | Total Counter | Long | Live Value
WCNV.CtlPnlFanCnt_10m_End | #N/A | WCNV. | CtlPnlFanCnt_10m_End | Number of activations of the control panel fan (end) | Anzahl der Aktivierungen des Bedienfeldlüfters (end) | Número de activaciones del ventilador del panel de control (end) | Liczba aktywacji wentylatora panelu sterowania (end) | Number of activations of the control panel fan | count | Count | Endvalue | Long | 10 minute tag
WCNV.CtlPnlFanTms | #N/A | WCNV. | CtlPnlFanTms | Time control panel fan has been activated | Zeit, in der der Bedienfeldlüfter aktiviert wurde | Tiempo que el ventilador del panel de control ha estado activado | Wentylator panelu sterowania czas aktywacji | Time control panel fan has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.CtlPnlFanTms_10m_End | #N/A | WCNV. | CtlPnlFanTms_10m_End | Time control panel fan has been activated (end) | Zeit, in der der Bedienfeldlüfter aktiviert wurde (end) | Tiempo que el ventilador del panel de control ha estado activado (end) | Wentylator panelu sterowania czas aktywacji (end) | Time control panel fan has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.CtlPnlHtCnt | #N/A | WCNV. | CtlPnlHtCnt | Number of activations of control panel heater | Anzahl der Aktivierungen der Bedienfeldheizung | Número de activaciones del calentador del panel de control | Liczba aktywacji nagrzewnicy panelu sterowania | Number of activations of control panel heater | count | Count | Total Counter | Long | Live Value
WCNV.CtlPnlHtCnt_10m_End | #N/A | WCNV. | CtlPnlHtCnt_10m_End | Number of activations of control panel heater (end) | Anzahl der Aktivierungen der Bedienfeldheizung (end) | Número de activaciones del calentador del panel de control (end) | Liczba aktywacji nagrzewnicy panelu sterowania (end) | Number of activations of control panel heater | count | Count | Endvalue | Long | 10 minute tag
WCNV.CtlPnlHtTms | #N/A | WCNV. | CtlPnlHtTms | Time control panel heat has been activated | Zeit, in der die Bedienfeldheizung aktiviert wurde | Tiempo que el calentador del panel de control ha estado activado | Ogrzewanie panelu sterowania czas aktywacji | Time control panel heat has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.CtlPnlHtTms_10m_End | #N/A | WCNV. | CtlPnlHtTms_10m_End | Time control panel heat has been activated (end) | Zeit, in der die Bedienfeldheizung aktiviert wurde (end) | Tiempo que el calentador del panel de control ha estado activado (end) | Ogrzewanie panelu sterowania czas aktywacji (end) | Time control panel heat has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.CtlPnlTmp | #N/A | WCNV. | CtlPnlTmp | Control Panel Temp | Bedienfeld Temperatur | Temperatura del panel de control | Temp panelu sterowania | Control panel temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.CtlPnlTmp_10m_Avg | #N/A | WCNV. | CtlPnlTmp_10m_Avg | Control Panel Temp (avg) | Bedienfeld Temperatur (avg) | Temperatura del panel de control (avg) | Temp panelu sterowania (avg) | Control panel temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.CtlPnlTmp_10m_Max | #N/A | WCNV. | CtlPnlTmp_10m_Max | Control Panel Temp (max) | Bedienfeld Temperatur (max) | Temperatura del panel de control (max) | Temp panelu sterowania (max) | Control panel temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.CtlPnlTmp_10m_Min | #N/A | WCNV. | CtlPnlTmp_10m_Min | Control Panel Temp (min) | Bedienfeld Temperatur (min) | Temperatura del panel de control (min) | Temp panelu sterowania (min) | Control panel temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.CtlPnlTmp_10m_Std | #N/A | WCNV. | CtlPnlTmp_10m_Std | Control Panel Temp (std) | Bedienfeld Temperatur (std) | Temperatura del panel de control (std) | Temp panelu sterowania (std) | Control panel temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.CtlTmp | #N/A | WCNV. | CtlTmp | Converter Panel Temp | Umrichterfeld Temperatur | Temperatura del panel del convertidor | Temp panelu konwertera | Converter panel temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.CtlTmp_10m_Avg | #N/A | WCNV. | CtlTmp_10m_Avg | Converter Panel Temp (avg) | Umrichterfeld Temperatur (avg) | Temperatura del panel del convertidor (avg) | Temp panelu konwertera (avg) | Converter panel temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.CtlTmp_10m_Max | #N/A | WCNV. | CtlTmp_10m_Max | Converter Panel Temp (max) | Umrichterfeld Temperatur (max) | Temperatura del panel del convertidor (max) | Temp panelu konwertera (max) | Converter panel temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.CtlTmp_10m_Min | #N/A | WCNV. | CtlTmp_10m_Min | Converter Panel Temp (min) | Umrichterfeld Temperatur (min) | Temperatura del panel del convertidor (min) | Temp panelu konwertera (min) | Converter panel temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.CtlTmp_10m_Std | #N/A | WCNV. | CtlTmp_10m_Std | Converter Panel Temp (std) | Umrichterfeld Temperatur (std) | Temperatura del panel del convertidor (std) | Temp panelu konwertera (std) | Converter panel temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.CtlTmp1 | #N/A | WCNV. | CtlTmp1 | Converter Panel 1 Temp | Umrichterfeld 1 Temperatur | Temperatura del panel 1 del convertidor | Panel konwertera 1 Temp | Converter panel 1 temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.CtlTmp1_10m_Avg | #N/A | WCNV. | CtlTmp1_10m_Avg | Converter Panel 1 Temp (avg) | Umrichterfeld 1 Temperatur (avg) | Temperatura del panel 1 del convertidor (avg) | Panel konwertera 1 Temp (avg) | Converter panel 1 temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.CtlTmp2 | #N/A | WCNV. | CtlTmp2 | Converter Panel 2 Temp | Umrichterfeld 2 Temperatur | Temperatura del panel 2 del convertidor | Panel konwertera 2 Temp | Converter panel 2 temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.CtlTmp2_10m_Avg | #N/A | WCNV. | CtlTmp2_10m_Avg | Converter Panel 2 Temp (avg) | Umrichterfeld 2 Temperatur (avg) | Temperatura del panel 2 del convertidor (avg) | Panel konwertera 2 Temp (avg) | Converter panel 2 temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.DclA | WCNV.DclA | WCNV. | DclA | Converter DC-link Current | Konverter DC-Zwischenkreisstrom | Corriente del enlace CC del convertidor | Konwerter DC-link Prąd | DC-link current inside converter | A | A | Live Value | Double | Live Value
WCNV.DclA1 | #N/A | WCNV. | DclA1 | Converter DC-link L1 Current | Konverter Zwischenkreis L1 Strom | Corriente L1 del enlace CC del convertidor | Konwerter DC-link L1 Prąd | DC-link current inside converter, phase L1 | A | A | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WCNV.DclA2 | #N/A | WCNV. | DclA2 | Converter DC-link L2 Current | Konverter Zwischenkreis L2 Strom | Corriente L2 del enlace CC del convertidor | Konwerter DC-link L2 Prąd | DC-link current inside converter, phase L2 | A | A | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WCNV.DclA3 | #N/A | WCNV. | DclA3 | Converter DC-link L3 Current | Konverter Zwischenkreis L3 Strom | Corriente L3 del enlace CC del convertidor | Konwerter DC-link L3 Prąd | DC-link current inside converter, phase L3 | A | A | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WCNV.DclTmp | WCNV.DclTmp | WCNV. | DclTmp | Converter DC-link Temp | Konverter DC-Zwischenkreis Temperatur | Temperatura del enlace CC del convertidor | Konwerter DC-link Temp | Converter DC-link Temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.DclTmp_10m_Avg | #N/A | WCNV. | DclTmp_10m_Avg | Converter DC-link Temp (avg) | Konverter DC-Zwischenkreis Temperatur (avg) | Temperatura del enlace CC del convertidor (avg) | Konwerter DC-link Temp (avg) | Converter DC-link Temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.DclTmp_10m_Max | #N/A | WCNV. | DclTmp_10m_Max | Converter DC-link Temp (max) | Konverter DC-Zwischenkreis Temperatur (max) | Temperatura del enlace CC del convertidor (max) | Konwerter DC-link Temp (max) | Converter DC-link Temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.DclTmp_10m_Min | #N/A | WCNV. | DclTmp_10m_Min | Converter DC-link Temp (min) | Konverter DC-Zwischenkreis Temperatur (min) | Temperatura del enlace CC del convertidor (min) | Konwerter DC-link Temp (min) | Converter DC-link Temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.DclTmp_10m_Std | #N/A | WCNV. | DclTmp_10m_Std | Converter DC-link Temp (std) | Konverter DC-Zwischenkreis Temperatur (std) | Temperatura del enlace CC del convertidor (std) | Konwerter DC-link Temp (std) | Converter DC-link Temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.DclV | WCNV.DclV | WCNV. | DclV | Converter DC-link Voltage | Konverter Zwischenkreisspannung | Tensión del enlace CC del convertidor | Konwerter DC-link Napięcie | DC-link voltage inside converter | V | V | Live Value | Double | Live Value
WCNV.DclV_10m_Avg | #N/A | WCNV. | DclV_10m_Avg | Converter DC-link Voltage (avg) | Konverter Zwischenkreisspannung (avg) | Tensión del enlace CC del convertidor (avg) | Konwerter DC-link Napięcie (avg) | DC-link voltage inside converter | V | V | Average | Double | 10 minute tag
WCNV.DclV_10m_Max | #N/A | WCNV. | DclV_10m_Max | Converter DC-link Voltage (max) | Konverter Zwischenkreisspannung (max) | Tensión del enlace CC del convertidor (max) | Konwerter DC-link Napięcie (max) | DC-link voltage inside converter | V | V | Maximum | Double | 10 minute tag
WCNV.DclV_10m_Min | #N/A | WCNV. | DclV_10m_Min | Converter DC-link Voltage (min) | Konverter Zwischenkreisspannung (min) | Tensión del enlace CC del convertidor (min) | Konwerter DC-link Napięcie (min) | DC-link voltage inside converter | V | V | Minimum | Double | 10 minute tag
WCNV.DclV_10m_Std | #N/A | WCNV. | DclV_10m_Std | Converter DC-link Voltage (std) | Konverter Zwischenkreisspannung (std) | Tensión del enlace CC del convertidor (std) | Konwerter DC-link Napięcie (std) | DC-link voltage inside converter | V | V | Standard Deviation | Double | 10 minute tag
WCNV.DmdTorq | #N/A | WCNV. | DmdTorq | Converter Torque setpoint | Konverter Drehmomentsollwert | Punto de ajuste de torsión del convertidor | Nastawa momentu obrotowego konwertera | Converter Torque setpoint | Enum | Enum | Live Value | Double | Live Value
WCNV.DmdTorq_10m_Avg | #N/A | WCNV. | DmdTorq_10m_Avg | Converter Torque setpoint (avg) | Konverter Drehmomentsollwert (avg) | Punto de ajuste de torsión del convertidor (avg) | Nastawa momentu obrotowego konwertera (avg) | Converter Torque setpoint | Enum | Enum | Average | Double | 10 minute tag
WCNV.DmdTorq_10m_Max | #N/A | WCNV. | DmdTorq_10m_Max | Converter Torque setpoint (max) | Konverter Drehmomentsollwert (max) | Punto de ajuste de torsión del convertidor (max) | Nastawa momentu obrotowego konwertera (max) | Converter Torque setpoint | Enum | Enum | Maximum | Double | 10 minute tag
WCNV.DmdTorq_10m_Min | #N/A | WCNV. | DmdTorq_10m_Min | Converter Torque setpoint (min) | Konverter Drehmomentsollwert (min) | Punto de ajuste de torsión del convertidor (min) | Nastawa momentu obrotowego konwertera (min) | Converter Torque setpoint | Enum | Enum | Minimum | Double | 10 minute tag
WCNV.DmdTorq_10m_Std | #N/A | WCNV. | DmdTorq_10m_Std | Converter Torque setpoint (std) | Konverter Drehmomentsollwert (std) | Punto de ajuste de torsión del convertidor (std) | Nastawa momentu obrotowego konwertera (std) | Converter Torque setpoint | Enum | Enum | Standard Deviation | Double | 10 minute tag
WCNV.G1Cnt | #N/A | WCNV. | G1Cnt | Number of activations of the generator 1 contactor | Anzahl der Aktivierungen des Schützes von Generator 1 | Número de activaciones del contactor 1 del generador | Liczba aktywacji stycznika generatora 1 | Number of activations of the generator 1 contactor | count | Count | Total Counter | Long | Live Value
WCNV.G1Cnt_10m_End | #N/A | WCNV. | G1Cnt_10m_End | Number of activations of the generator 1 contactor (end) | Anzahl der Aktivierungen des Schützes von Generator 1 (end) | Número de activaciones del contactor 1 del generador (end) | Liczba aktywacji stycznika generatora 1 (end) | Number of activations of the generator 1 contactor | count | Count | Endvalue | Long | 10 minute tag
WCNV.G1OpTms | #N/A | WCNV. | G1OpTms | Time the Generator 1 contactor has been activated | Zeit, in der das Schütz von Generator 1 aktiviert wurde | Tiempo que el contactor del generador 1 ha estado activado | Czas aktywacji stycznika Generator 1 | Time the Generator 1 contactor has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.G1OpTms_10m_End | #N/A | WCNV. | G1OpTms_10m_End | Time the Generator 1 contactor has been activated (end) | Zeit, in der das Schütz von Generator 1 aktiviert wurde (end) | Tiempo que el contactor del generador 1 ha estado activado (end) | Czas aktywacji stycznika Generator 1 (end) | Time the Generator 1 contactor has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.G2Cnt | #N/A | WCNV. | G2Cnt | Number of activations of the generator 2 contactor | Anzahl der Aktivierungen des Schützes von Generator 2 | Número de activaciones del contactor 2 del generador | Liczba aktywacji stycznika generatora 2 | Number of activations of the generator 2 contactor | count | Count | Total Counter | Long | Live Value
WCNV.G2Cnt_10m_End | #N/A | WCNV. | G2Cnt_10m_End | Number of activations of the generator 2 contactor (end) | Anzahl der Aktivierungen des Schützes von Generator 2 (end) | Número de activaciones del contactor 2 del generador (end) | Liczba aktywacji stycznika generatora 2 (end) | Number of activations of the generator 2 contactor | count | Count | Endvalue | Long | 10 minute tag
WCNV.G2OpTms | #N/A | WCNV. | G2OpTms | Time the Generator 2 contactor has been activated | Zeit, in der das Schütz von Generator 2 aktiviert wurde | Tiempo que el contactor del generador 2 ha estado activado | Czas aktywacji stycznika Generator 2 | Time the Generator 2 contactor has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.G2OpTms_10m_End | #N/A | WCNV. | G2OpTms_10m_End | Time the Generator 2 contactor has been activated (end) | Zeit, in der das Schütz von Generator 2 aktiviert wurde (end) | Tiempo que el contactor del generador 2 ha estado activado (end) | Czas aktywacji stycznika Generator 2 (end) | Time the Generator 2 contactor has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.GnA | WCNV.GnA | WCNV. | GnA | Converter Generator Side Current | Konverter Generatorseitiger Strom | Corriente del convertidor en el lado del generador | Prąd konwertera strona gen. | Generator side 3 phase current | A | A | Live Value | Double | Live Value
WCNV.GnA1 | #N/A | WCNV. | GnA1 | Converter Generator L1 Side Current | Konverter Generator L1-seitiger Strom | Corriente del convertidor L1 en el lado del generador | Konwerter prąd L1 strona gen. | Current of phase L1 at the generator side | A | A | Live Value | Double | Live Value
WCNV.GnA2 | #N/A | WCNV. | GnA2 | Converter Generator L2 Side Current | Konverter Generator L2-seitiger Strom | Corriente del convertidor L2 en el lado del generador | Konwerter prąd L2 strona gen. | Current of phase L2 at the generator side | A | A | Live Value | Double | Live Value
WCNV.GnA3 | #N/A | WCNV. | GnA3 | Converter Generator L3 Side Current | Konverter Generator L3-seitiger Strom | Corriente del convertidor L3 en el lado del generador | Konwerter prąd L3 strona gen. | Current of phase L3 at the generator side | A | A | Live Value | Double | Live Value
WCNV.GnHz | WCNV.GnHz | WCNV. | GnHz | Generator Frequency | Generator Frequenz | Frecuencia del generador | Częstotliwość generatora | Generator side frequency | Hz | Hz | Live Value | Double | Live Value
WCNV.GnPF | WCNV.GnPF | WCNV. | GnPF | Power factor generator side | Leistungsfaktor Generatorseite | Factor de potencia en el lado del generador | Wsp. Mocy strona gen. | Generator side 3 phase power factor | pf | PF | Live Value | Double
WCNV.GnPNV | WCNV.GnPNV | WCNV. | GnPNV | Converter P-N Voltage Generator side | Konverter P-N Spannung Generatorseite | Tensión P-N del convertidor en el lado del generador | Konwerter nap.P-N strona gen. | Voltage of all three phases between phase and neutral at the converter level (Generator side) | V | V | Live Value | Double | Live Value | Used in some specialised presentations
WCNV.GnPNV_10m_Avg | #N/A | WCNV. | GnPNV_10m_Avg | Converter P-N Voltage Generator side (avg) | Konverter P-N Spannung Generatorseite (avg) | Tensión P-N del convertidor en el lado del generador (avg) | Konwerter nap.P-N strona gen. (avg) | Voltage of all three phases between phase and neutral at the converter level (Generator side) | V | V | Average | Double | 10 minute tag | Common tags for analysis
WCNV.GnPNV_10m_Max | #N/A | WCNV. | GnPNV_10m_Max | Converter P-N Voltage Generator side (max) | Konverter P-N Spannung Generatorseite (max) | Tensión P-N del convertidor en el lado del generador (max) | Konwerter nap.P-N strona gen. (max) | Voltage of all three phases between phase and neutral at the converter level (Generator side) | V | V | Maximum | Double | 10 minute tag | Common tags for analysis
WCNV.GnPNV_10m_Min | #N/A | WCNV. | GnPNV_10m_Min | Converter P-N Voltage Generator side (min) | Konverter P-N Spannung Generatorseite (min) | Tensión P-N del convertidor en el lado del generador (min) | Konwerter nap.P-N strona gen. (min) | Voltage of all three phases between phase and neutral at the converter level (Generator side) | V | V | Minimum | Double | 10 minute tag | Common tags for analysis
WCNV.GnPNV_10m_Std | #N/A | WCNV. | GnPNV_10m_Std | Converter P-N Voltage Generator side (std) | Konverter P-N Spannung Generatorseite (std) | Tensión P-N del convertidor en el lado del generador (std) | Konwerter nap.P-N strona gen. (std) | Voltage of all three phases between phase and neutral at the converter level (Generator side) | V | V | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WCNV.GnPNV1 | #N/A | WCNV. | GnPNV1 | Converter P-N L1 Voltage Generator side | Konverter P-N L1 Spannung Generatorseite | Tensión P-N L1 del convertidor en el lado del generador | Konwerter P-N L1 Napięcie strona gen. | Voltage between phase L1 and neutral at the converter level (Generator side) | V | V | Live Value | Double | Live Value
WCNV.GnPNV1_10m_Avg | #N/A | WCNV. | GnPNV1_10m_Avg | Converter P-N L1 Voltage Generator side (avg) | Konverter P-N L1 Spannung Generatorseite (avg) | Tensión P-N L1 del convertidor en el lado del generador (avg) | Konwerter P-N L1 Napięcie strona gen. (avg) | Voltage between phase L1 and neutral at the converter level (Generator side) | V | V | Average | Double | 10 minute tag
WCNV.GnPNV1_10m_Max | #N/A | WCNV. | GnPNV1_10m_Max | Converter P-N L1 Voltage Generator side (max) | Konverter P-N L1 Spannung Generatorseite (max) | Tensión P-N L1 del convertidor en el lado del generador (max) | Konwerter P-N L1 Napięcie strona gen. (max) | Voltage between phase L1 and neutral at the converter level (Generator side) | V | V | Maximum | Double | 10 minute tag
WCNV.GnPNV1_10m_Min | #N/A | WCNV. | GnPNV1_10m_Min | Converter P-N L1 Voltage Generator side (min) | Konverter P-N L1 Spannung Generatorseite (min) | Tensión P-N L1 del convertidor en el lado del generador (min) | Konwerter P-N L1 Napięcie strona gen. (min) | Voltage between phase L1 and neutral at the converter level (Generator side) | V | V | Minimum | Double | 10 minute tag
WCNV.GnPNV1_10m_Std | #N/A | WCNV. | GnPNV1_10m_Std | Converter P-N L1 Voltage Generator side (std) | Konverter P-N L1 Spannung Generatorseite (std) | Tensión P-N L1 del convertidor en el lado del generador (std) | Konwerter P-N L1 Napięcie strona gen. (std) | Voltage between phase L1 and neutral at the converter level (Generator side) | V | V | Standard Deviation | Double | 10 minute tag
WCNV.GnPNV2 | #N/A | WCNV. | GnPNV2 | Converter P-N L2 Voltage Generator side | Konverter P-N L2 Spannung Generatorseite | Tensión P-N L2 del convertidor en el lado del generador | Konwerter P-N L2 Napięcie strona gen. | Voltage between phase L2 and neutral at the converter level (Generator side) | V | V | Live Value | Double | Live Value
WCNV.GnPNV2_10m_Avg | #N/A | WCNV. | GnPNV2_10m_Avg | Converter P-N L2 Voltage Generator side (avg) | Konverter P-N L2 Spannung Generatorseite (avg) | Tensión P-N L2 del convertidor en el lado del generador (avg) | Konwerter P-N L2 Napięcie strona gen. (avg) | Voltage between phase L2 and neutral at the converter level (Generator side) | V | V | Average | Double | 10 minute tag
WCNV.GnPNV2_10m_Max | #N/A | WCNV. | GnPNV2_10m_Max | Converter P-N L2 Voltage Generator side (max) | Konverter P-N L2 Spannung Generatorseite (max) | Tensión P-N L2 del convertidor en el lado del generador (max) | Konwerter P-N L2 Napięcie strona gen. (max) | Voltage between phase L2 and neutral at the converter level (Generator side) | V | V | Maximum | Double | 10 minute tag
WCNV.GnPNV2_10m_Min | #N/A | WCNV. | GnPNV2_10m_Min | Converter P-N L2 Voltage Generator side (min) | Konverter P-N L2 Spannung Generatorseite (min) | Tensión P-N L2 del convertidor en el lado del generador (min) | Konwerter P-N L2 Napięcie strona gen. (min) | Voltage between phase L2 and neutral at the converter level (Generator side) | V | V | Minimum | Double | 10 minute tag
WCNV.GnPNV2_10m_Std | #N/A | WCNV. | GnPNV2_10m_Std | Converter P-N L2 Voltage Generator side (std) | Konverter P-N L2 Spannung Generatorseite (std) | Tensión P-N L2 del convertidor en el lado del generador (std) | Konwerter P-N L2 Napięcie strona gen. (std) | Voltage between phase L2 and neutral at the converter level (Generator side) | V | V | Standard Deviation | Double | 10 minute tag
WCNV.GnPNV3 | #N/A | WCNV. | GnPNV3 | Converter P-N L3 Voltage Generator side | Konverter P-N L3 Spannung Generatorseite | Tensión P-N L3 del convertidor en el lado del generador | Konwerter P-N L3 Napięcie strona gen. | Voltage between phase L3 and neutral at the converter level (Generator side) | V | V | Live Value | Double | Live Value
WCNV.GnPNV3_10m_Avg | #N/A | WCNV. | GnPNV3_10m_Avg | Converter P-N L3 Voltage Generator side (avg) | Konverter P-N L3 Spannung Generatorseite (avg) | Tensión P-N L3 del convertidor en el lado del generador (avg) | Konwerter P-N L3 Napięcie strona gen. (avg) | Voltage between phase L3 and neutral at the converter level (Generator side) | V | V | Average | Double | 10 minute tag
WCNV.GnPNV3_10m_Max | #N/A | WCNV. | GnPNV3_10m_Max | Converter P-N L3 Voltage Generator side (max) | Konverter P-N L3 Spannung Generatorseite (max) | Tensión P-N L3 del convertidor en el lado del generador (max) | Konwerter P-N L3 Napięcie strona gen. (max) | Voltage between phase L3 and neutral at the converter level (Generator side) | V | V | Maximum | Double | 10 minute tag
WCNV.GnPNV3_10m_Min | #N/A | WCNV. | GnPNV3_10m_Min | Converter P-N L3 Voltage Generator side (min) | Konverter P-N L3 Spannung Generatorseite (min) | Tensión P-N L3 del convertidor en el lado del generador (min) | Konwerter P-N L3 Napięcie strona gen. (min) | Voltage between phase L3 and neutral at the converter level (Generator side) | V | V | Minimum | Double | 10 minute tag
WCNV.GnPNV3_10m_Std | #N/A | WCNV. | GnPNV3_10m_Std | Converter P-N L3 Voltage Generator side (std) | Konverter P-N L3 Spannung Generatorseite (std) | Tensión P-N L3 del convertidor en el lado del generador (std) | Konwerter P-N L3 Napięcie strona gen. (std) | Voltage between phase L3 and neutral at the converter level (Generator side) | V | V | Standard Deviation | Double | 10 minute tag
WCNV.GnPPV | WCNV.GnPPV | WCNV. | GnPPV | Converter P-P Voltage Generator side | Konverter P-P Spannung Generatorseite | Tensión P-P del convertidoren el lado del generador | Strona Konwertera napięcia P-P | Generator side 3 phase phase-to-phase voltage | V | V | Live Value | Double | Live Value
WCNV.GnTmp | WCNV.GnTmp | WCNV. | GnTmp | Converter Generator Side Temp | Konverter Generatorseitige Temperatur | Temperatura del convertidor en el lado del generador | Konwerter Temp. strona gen. | Converter temperature generator side | deg_c | °C | Live Value | Double | Live Value
WCNV.GnTmp_10m_Avg | #N/A | WCNV. | GnTmp_10m_Avg | Converter Generator Side Temp (avg) | Konverter Generatorseitige Temperatur (avg) | Temperatura del convertidor en el lado del generador (avg) | Konwerter Temp. strona gen. (avg) | Converter temperature generator side | deg_c | °C | Average | Double | 10 minute tag
WCNV.GnTmp_10m_Max | #N/A | WCNV. | GnTmp_10m_Max | Converter Generator Side Temp (max) | Konverter Generatorseitige Temperatur (max) | Temperatura del convertidor en el lado del generador (max) | Konwerter Temp. strona gen. (max) | Converter temperature generator side | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.GnTmp_10m_Min | #N/A | WCNV. | GnTmp_10m_Min | Converter Generator Side Temp (min) | Konverter Generatorseitige Temperatur (min) | Temperatura del convertidor en el lado del generador (min) | Konwerter Temp. strona gen. (min) | Converter temperature generator side | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.GnTmp_10m_Std | #N/A | WCNV. | GnTmp_10m_Std | Converter Generator Side Temp (std) | Konverter Generatorseitige Temperatur (std) | Temperatura del convertidor en el lado del generador (std) | Konwerter Temp. strona gen. (std) | Converter temperature generator side | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.GnTmp1 | #N/A | WCNV. | GnTmp1 | Converter Generator L1 Side Temp | Konverter Generator L1-seitige Temperatur | Temperatura del convertidor L1 en el lado del generador | Konwerter L1 Temp. strona gen. | Converter temperature phase L1, generator side | deg_c | °C | Live Value | Double | Live Value
WCNV.GnTmp1_10m_Avg | #N/A | WCNV. | GnTmp1_10m_Avg | Converter Generator L1 Side Temp (avg) | Konverter Generator L1-seitige Temperatur (avg) | Temperatura del convertidor L1 en el lado del generador (avg) | Konwerter L1 Temp. strona gen. (avg) | Converter temperature phase L1, generator side | deg_c | °C | Average | Double | 10 minute tag
WCNV.GnTmp1_10m_Max | #N/A | WCNV. | GnTmp1_10m_Max | Converter Generator L1 Side Temp (max) | Konverter Generator L1-seitige Temperatur (max) | Temperatura del convertidor L1 en el lado del generador (max) | Konwerter L1 Temp. strona gen. (max) | Converter temperature phase L1, generator side | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.GnTmp1_10m_Min | #N/A | WCNV. | GnTmp1_10m_Min | Converter Generator L1 Side Temp (min) | Konverter Generator L1-seitige Temperatur (min) | Temperatura del convertidor L1 en el lado del generador (min) | Konwerter L1 Temp. strona gen. (min) | Converter temperature phase L1, generator side | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.GnTmp1_10m_Std | #N/A | WCNV. | GnTmp1_10m_Std | Converter Generator L1 Side Temp (std) | Konverter Generator L1-seitige Temperatur (std) | Temperatura del convertidor L1 en el lado del generador (std) | Konwerter L1 Temp. strona gen. (std) | Converter temperature phase L1, generator side | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.GnTmp2 | #N/A | WCNV. | GnTmp2 | Converter Generator L2 Side Temp | Konverter Generator L2-seitige Temperatur | Temperatura del convertidor L2 en el lado del generador | Konwerter L2 Temp. strona gen. | Converter temperature phase L2, generator side | deg_c | °C | Live Value | Double | Live Value
WCNV.GnTmp2_10m_Avg | #N/A | WCNV. | GnTmp2_10m_Avg | Converter Generator L2 Side Temp (avg) | Konverter Generator L2-seitige Temperatur (avg) | Temperatura del convertidor L2 en el lado del generador (avg) | Konwerter L2 Temp. strona gen. (avg) | Converter temperature phase L2, generator side | deg_c | °C | Average | Double | 10 minute tag
WCNV.GnTmp2_10m_Max | #N/A | WCNV. | GnTmp2_10m_Max | Converter Generator L2 Side Temp (max) | Konverter Generator L2-seitige Temperatur (max) | Temperatura del convertidor L2 en el lado del generador (max) | Konwerter L2 Temp. strona gen. (max) | Converter temperature phase L2, generator side | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.GnTmp2_10m_Min | #N/A | WCNV. | GnTmp2_10m_Min | Converter Generator L2 Side Temp (min) | Konverter Generator L2-seitige Temperatur (min) | Temperatura del convertidor L2 en el lado del generador (min) | Konwerter L2 Temp. strona gen. (min) | Converter temperature phase L2, generator side | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.GnTmp2_10m_Std | #N/A | WCNV. | GnTmp2_10m_Std | Converter Generator L2 Side Temp (std) | Konverter Generator L2-seitige Temperatur (std) | Temperatura del convertidor L2 en el lado del generador (std) | Konwerter L2 Temp. strona gen. (std) | Converter temperature phase L2, generator side | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.GnTmp3 | #N/A | WCNV. | GnTmp3 | Converter Generator L3 Side Temp | Konverter Generator L3-seitige Temperatur | Temperatura del convertidor L3 en el lado del generador | Konwerter L3 Temp. strona gen. | Converter temperature phase L3, generator side | deg_c | °C | Live Value | Double | Live Value
WCNV.GnTmp3_10m_Avg | #N/A | WCNV. | GnTmp3_10m_Avg | Converter Generator L3 Side Temp (avg) | Konverter Generator L3-seitige Temperatur (avg) | Temperatura del convertidor L3 en el lado del generador (avg) | Konwerter L3 Temp. strona gen. (avg) | Converter temperature phase L3, generator side | deg_c | °C | Average | Double | 10 minute tag
WCNV.GnTmp3_10m_Max | #N/A | WCNV. | GnTmp3_10m_Max | Converter Generator L3 Side Temp (max) | Konverter Generator L3-seitige Temperatur (max) | Temperatura del convertidor L3 en el lado del generador (max) | Konwerter L3 Temp. strona gen. (max) | Converter temperature phase L3, generator side | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.GnTmp3_10m_Min | #N/A | WCNV. | GnTmp3_10m_Min | Converter Generator L3 Side Temp (min) | Konverter Generator L3-seitige Temperatur (min) | Temperatura del convertidor L3 en el lado del generador (min) | Konwerter L3 Temp. strona gen. (min) | Converter temperature phase L3, generator side | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.GnTmp3_10m_Std | #N/A | WCNV. | GnTmp3_10m_Std | Converter Generator L3 Side Temp (std) | Konverter Generator L3-seitige Temperatur (std) | Temperatura del convertidor L3 en el lado del generador (std) | Konwerter L3 Temp. strona gen. (std) | Converter temperature phase L3, generator side | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.GriA | WCNV.GriA | WCNV. | GriA | Converter Grid Side Current | Konverter netzseitiger Strom | Corriente del convertidor en el lado de la red eléctrica | Konwerter Prąd strona sieci | Current of all three phases at the converter level | A | A | Live Value | Double | Live Value | Used in some specialised presentations
WCNV.GriA_10m_Avg | #N/A | WCNV. | GriA_10m_Avg | Converter Grid Side Current (avg) | Konverter netzseitiger Strom (avg) | Corriente del convertidor en el lado de la red eléctrica (avg) | Konwerter Prąd strona sieci (avg) | Current of all three phases at the converter level | A | A | Average | Double | 10 minute tag | Common tags for analysis
WCNV.GriA_10m_Max | #N/A | WCNV. | GriA_10m_Max | Converter Grid Side Current (max) | Konverter netzseitiger Strom (max) | Corriente del convertidor en el lado de la red eléctrica (max) | Konwerter Prąd strona sieci (max) | Current of all three phases at the converter level | A | A | Maximum | Double | 10 minute tag | Common tags for analysis
WCNV.GriA_10m_Min | #N/A | WCNV. | GriA_10m_Min | Converter Grid Side Current (min) | Konverter netzseitiger Strom (min) | Corriente del convertidor en el lado de la red eléctrica (min) | Konwerter Prąd strona sieci (min) | Current of all three phases at the converter level | A | A | Minimum | Double | 10 minute tag | Common tags for analysis
WCNV.GriA_10m_Std | #N/A | WCNV. | GriA_10m_Std | Converter Grid Side Current (std) | Konverter netzseitiger Strom (std) | Corriente del convertidor en el lado de la red eléctrica (std) | Konwerter Prąd strona sieci (std) | Current of all three phases at the converter level | A | A | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WCNV.GriA1 | #N/A | WCNV. | GriA1 | Converter Grid L1 Side Current | Konverter Netz L1-seitiger Strom | Corriente del convertidor L1 en el lado de la red eléctrica | Konwerter L1 Prąd strona sieci | Current of phase L1 at the converter level | A | A | Live Value | Double | Live Value | Used in some specialised presentations
WCNV.GriA1_10m_Avg | #N/A | WCNV. | GriA1_10m_Avg | Converter Grid L1 Side Current (avg) | Konverter Netz L1-seitiger Strom (avg) | Corriente del convertidor L1 en el lado de la red eléctrica (avg) | Konwerter L1 Prąd strona sieci (avg) | Current of phase L1 at the converter level | A | A | Average | Double | 10 minute tag | Common tags for analysis
WCNV.GriA1_10m_Max | #N/A | WCNV. | GriA1_10m_Max | Converter Grid L1 Side Current (max) | Konverter Netz L1-seitiger Strom (max) | Corriente del convertidor L1 en el lado de la red eléctrica (max) | Konwerter L1 Prąd strona sieci (max) | Current of phase L1 at the converter level | A | A | Maximum | Double | 10 minute tag | Common tags for analysis
WCNV.GriA1_10m_Min | #N/A | WCNV. | GriA1_10m_Min | Converter Grid L1 Side Current (min) | Konverter Netz L1-seitiger Strom (min) | Corriente del convertidor L1 en el lado de la red eléctrica (min) | Konwerter L1 Prąd strona sieci (min) | Current of phase L1 at the converter level | A | A | Minimum | Double | 10 minute tag | Common tags for analysis
WCNV.GriA1_10m_Std | #N/A | WCNV. | GriA1_10m_Std | Converter Grid L1 Side Current (std) | Konverter Netz L1-seitiger Strom (std) | Corriente del convertidor L1 en el lado de la red eléctrica (std) | Konwerter L1 Prąd strona sieci (std) | Current of phase L1 at the converter level | A | A | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WCNV.GriA2 | #N/A | WCNV. | GriA2 | Converter Grid L2 Side Current | Konverter Netz L2-seitiger Strom | Corriente del convertidor L2 en el lado de la red eléctrica | Konwerter L2 Prąd strona sieci | Current of phase L2 at the converter level | A | A | Live Value | Double | Live Value | Used in some specialised presentations
WCNV.GriA2_10m_Avg | #N/A | WCNV. | GriA2_10m_Avg | Converter Grid L2 Side Current (avg) | Konverter Netz L2-seitiger Strom (avg) | Corriente del convertidor L2 en el lado de la red eléctrica (avg) | Konwerter L2 Prąd strona sieci (avg) | Current of phase L2 at the converter level | A | A | Average | Double | 10 minute tag | Common tags for analysis
WCNV.GriA2_10m_Max | #N/A | WCNV. | GriA2_10m_Max | Converter Grid L2 Side Current (max) | Konverter Netz L2-seitiger Strom (max) | Corriente del convertidor L2 en el lado de la red eléctrica (max) | Konwerter L2 Prąd strona sieci (max) | Current of phase L2 at the converter level | A | A | Maximum | Double | 10 minute tag | Common tags for analysis
WCNV.GriA2_10m_Min | #N/A | WCNV. | GriA2_10m_Min | Converter Grid L2 Side Current (min) | Konverter Netz L2-seitiger Strom (min) | Corriente del convertidor L2 en el lado de la red eléctrica (min) | Konwerter L2 Prąd strona sieci (min) | Current of phase L2 at the converter level | A | A | Minimum | Double | 10 minute tag | Common tags for analysis
WCNV.GriA2_10m_Std | #N/A | WCNV. | GriA2_10m_Std | Converter Grid L2 Side Current (std) | Konverter Netz L2-seitiger Strom (std) | Corriente del convertidor L2 en el lado de la red eléctrica (std) | Konwerter L2 Prąd strona sieci (std) | Current of phase L2 at the converter level | A | A | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WCNV.GriA3 | #N/A | WCNV. | GriA3 | Converter Grid L3 Side Current | Konverter Netz L3-seitiger Strom | Corriente del convertidor L3 en el lado de la red eléctrica | Konwerter L3 Prąd strona sieci | Current of phase L3 at the converter level | A | A | Live Value | Double | Live Value | Used in some specialised presentations
WCNV.GriA3_10m_Avg | #N/A | WCNV. | GriA3_10m_Avg | Converter Grid L3 Side Current (avg) | Konverter Netz L3-seitiger Strom (avg) | Corriente del convertidor L3 en el lado de la red eléctrica (avg) | Konwerter L3 Prąd strona sieci (avg) | Current of phase L3 at the converter level | A | A | Average | Double | 10 minute tag | Common tags for analysis
WCNV.GriA3_10m_Max | #N/A | WCNV. | GriA3_10m_Max | Converter Grid L3 Side Current (max) | Konverter Netz L3-seitiger Strom (max) | Corriente del convertidor L3 en el lado de la red eléctrica (max) | Konwerter L3 Prąd strona sieci (max) | Current of phase L3 at the converter level | A | A | Maximum | Double | 10 minute tag | Common tags for analysis
WCNV.GriA3_10m_Min | #N/A | WCNV. | GriA3_10m_Min | Converter Grid L3 Side Current (min) | Konverter Netz L3-seitiger Strom (min) | Corriente del convertidor L3 en el lado de la red eléctrica (min) | Konwerter L3 Prąd strona sieci (min) | Current of phase L3 at the converter level | A | A | Minimum | Double | 10 minute tag | Common tags for analysis
WCNV.GriA3_10m_Std | #N/A | WCNV. | GriA3_10m_Std | Converter Grid L3 Side Current (std) | Konverter Netz L3-seitiger Strom (std) | Corriente del convertidor L3 en el lado de la red eléctrica (std) | Konwerter L3 Prąd strona sieci (std) | Current of phase L3 at the converter level | A | A | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WCNV.GriAsymA | #N/A | WCNV. | GriAsymA | Grid current Asymmetry | Netzstrom Asymmetrie | Asimetría de la corriente de la red eléctrica | Asymetria prądu sieci | Converter Grid current Asymmetry | A | A | Live Value | Double | Live Value
WCNV.GriASymA_10m_Avg | #N/A | WCNV. | GriASymA_10m_Avg | Grid current Asymmetry (avg) | Netzstrom Asymmetrie (avg) | Asimetría de la corriente de la red eléctrica (avg) | Asymetria prądu sieci (avg) | Converter Grid current Asymmetry | A | A | Average | Double | 10 minute tag | Common tags for analysis
WCNV.GriASymA_10m_Max | #N/A | WCNV. | GriASymA_10m_Max | Grid current Asymmetry (max) | Netzstrom Asymmetrie (max) | Asimetría de la corriente de la red eléctrica (max) | Asymetria prądu sieci (max) | Converter Grid current Asymmetry | A | A | Maximum | Double | 10 minute tag | Common tags for analysis
WCNV.GriASymA_10m_Min | #N/A | WCNV. | GriASymA_10m_Min | Grid current Asymmetry (min) | Netzstrom Asymmetrie (min) | Asimetría de la corriente de la red eléctrica (min) | Asymetria prądu sieci (min) | Converter Grid current Asymmetry | A | A | Minimum | Double | 10 minute tag | Common tags for analysis
WCNV.GriASymA_10m_Std | #N/A | WCNV. | GriASymA_10m_Std | Grid current Asymmetry (std) | Netzstrom Asymmetrie (std) | Asimetría de la corriente de la red eléctrica (std) | Asymetria prądu sieci (std) | Converter Grid current Asymmetry | A | A | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WCNV.GriFilTmp1 | #N/A | WCNV. | GriFilTmp1 | Converter Grid Filter L1 Temp | Konverter Netzfilter L1 Temperatur | Temperatura del filtro del convertidor L1 de la red eléctrica | Konwereter Filtr sieci L1 Temp | Converter grid filter temperature phase L1 | deg_c | °C | Live Value | Double | Live Value
WCNV.GriFilTmp1_10m_Avg | #N/A | WCNV. | GriFilTmp1_10m_Avg | Converter Grid Filter L1 Temp (avg) | Konverter Netzfilter L1 Temperatur (avg) | Temperatura del filtro del convertidor L1 de la red eléctrica (avg) | Konwereter Filtr sieci L1 Temp (avg) | Converter grid filter temperature phase L1 | deg_c | °C | Average | Double | 10 minute tag
WCNV.GriFilTmp1_10m_Max | #N/A | WCNV. | GriFilTmp1_10m_Max | Converter Grid Filter L1 Temp (max) | Konverter Netzfilter L1 Temperatur (max) | Temperatura del filtro del convertidor L1 de la red eléctrica (max) | Konwereter Filtr sieci L1 Temp (max) | Converter grid filter temperature phase L1 | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.GriFilTmp1_10m_Min | #N/A | WCNV. | GriFilTmp1_10m_Min | Converter Grid Filter L1 Temp (min) | Konverter Netzfilter L1 Temperatur (min) | Temperatura del filtro del convertidor L1 de la red eléctrica (min) | Konwereter Filtr sieci L1 Temp (min) | Converter grid filter temperature phase L1 | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.GriFilTmp1_10m_Std | #N/A | WCNV. | GriFilTmp1_10m_Std | Converter Grid Filter L1 Temp (std) | Konverter Netzfilter L1 Temperatur (std) | Temperatura del filtro del convertidor L1 de la red eléctrica (std) | Konwereter Filtr sieci L1 Temp (std) | Converter grid filter temperature phase L1 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.GriFilTmp2 | #N/A | WCNV. | GriFilTmp2 | Converter Grid Filter L2 Temp | Konverter Netzfilter L2 Temperatur | Temperatura del filtro del convertidor L2 de la red eléctrica | Konwereter Filtr sieci L2 Temp | Converter grid filter temperature phase L2 | deg_c | °C | Live Value | Double | Live Value
WCNV.GriFilTmp2_10m_Avg | #N/A | WCNV. | GriFilTmp2_10m_Avg | Converter Grid Filter L2 Temp (avg) | Konverter Netzfilter L2 Temperatur (avg) | Temperatura del filtro del convertidor L2 de la red eléctrica (avg) | Konwereter Filtr sieci L2 Temp (avg) | Converter grid filter temperature phase L2 | deg_c | °C | Average | Double | 10 minute tag
WCNV.GriFilTmp2_10m_Max | #N/A | WCNV. | GriFilTmp2_10m_Max | Converter Grid Filter L2 Temp (max) | Konverter Netzfilter L2 Temperatur (max) | Temperatura del filtro del convertidor L2 de la red eléctrica (max) | Konwereter Filtr sieci L2 Temp (max) | Converter grid filter temperature phase L2 | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.GriFilTmp2_10m_Min | #N/A | WCNV. | GriFilTmp2_10m_Min | Converter Grid Filter L2 Temp (min) | Konverter Netzfilter L2 Temperatur (min) | Temperatura del filtro del convertidor L2 de la red eléctrica (min) | Konwereter Filtr sieci L2 Temp (min) | Converter grid filter temperature phase L2 | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.GriFilTmp2_10m_Std | #N/A | WCNV. | GriFilTmp2_10m_Std | Converter Grid Filter L2 Temp (std) | Konverter Netzfilter L2 Temperatur (std) | Temperatura del filtro del convertidor L2 de la red eléctrica (std) | Konwereter Filtr sieci L2 Temp (std) | Converter grid filter temperature phase L2 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.GriFilTmp3 | #N/A | WCNV. | GriFilTmp3 | Converter Grid Filter L3 Temp | Konverter Netzfilter L3 Temperatur | Temperatura del filtro del convertidor L3 de la red eléctrica | Konwereter Filtr sieci L3 Temp | Converter grid filter temperature phase L3 | deg_c | °C | Live Value | Double | Live Value
WCNV.GriFilTmp3_10m_Avg | #N/A | WCNV. | GriFilTmp3_10m_Avg | Converter Grid Filter L3 Temp (avg) | Konverter Netzfilter L3 Temperatur (avg) | Temperatura del filtro del convertidor L3 de la red eléctrica (avg) | Konwereter Filtr sieci L3 Temp (avg) | Converter grid filter temperature phase L3 | deg_c | °C | Average | Double | 10 minute tag
WCNV.GriFilTmp3_10m_Max | #N/A | WCNV. | GriFilTmp3_10m_Max | Converter Grid Filter L3 Temp (max) | Konverter Netzfilter L3 Temperatur (max) | Temperatura del filtro del convertidor L3 de la red eléctrica (max) | Konwereter Filtr sieci L3 Temp (max) | Converter grid filter temperature phase L3 | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.GriFilTmp3_10m_Min | #N/A | WCNV. | GriFilTmp3_10m_Min | Converter Grid Filter L3 Temp (min) | Konverter Netzfilter L3 Temperatur (min) | Temperatura del filtro del convertidor L3 de la red eléctrica (min) | Konwereter Filtr sieci L3 Temp (min) | Converter grid filter temperature phase L3 | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.GriFilTmp3_10m_Std | #N/A | WCNV. | GriFilTmp3_10m_Std | Converter Grid Filter L3 Temp (std) | Konverter Netzfilter L3 Temperatur (std) | Temperatura del filtro del convertidor L3 de la red eléctrica (std) | Konwereter Filtr sieci L3 Temp (std) | Converter grid filter temperature phase L3 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.GriHz | WCNV.GriHz | WCNV. | GriHz | Frequency | Frequenz | Frecuencia | Częstotliwość | Frequency at all three phases at the converter level | Hz | Hz | Live Value | Double | Live Value | Used in some specialised presentations
WCNV.GriHz_10m_Avg | #N/A | WCNV. | GriHz_10m_Avg | Frequency (avg) | Frequenz (avg) | Frecuencia (avg) | Częstotliwość (avg) | Frequency at all three phases at the converter level | Hz | Hz | Average | Double | 10 minute tag | Common tags for analysis
WCNV.GriHz_10m_Max | #N/A | WCNV. | GriHz_10m_Max | Frequency (max) | Frequenz (max) | Frecuencia (max) | Częstotliwość (max) | Frequency at all three phases at the converter level | Hz | Hz | Maximum | Double | 10 minute tag | Common tags for analysis
WCNV.GriHz_10m_Min | #N/A | WCNV. | GriHz_10m_Min | Frequency (min) | Frequenz (min) | Frecuencia (min) | Częstotliwość (min) | Frequency at all three phases at the converter level | Hz | Hz | Minimum | Double | 10 minute tag | Common tags for analysis
WCNV.GriHz_10m_Std | #N/A | WCNV. | GriHz_10m_Std | Frequency (std) | Frequenz (std) | Frecuencia (std) | Częstotliwość (std) | Frequency at all three phases at the converter level | Hz | Hz | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WCNV.GriPF | WCNV.GriPF | WCNV. | GriPF | Power factor grid side | Leistungsfaktor Netzseite | Factor de potencia en el lado de la red eléctrica | Wsp.mocy strona sieci | Power factor average of all three phases | pf | PF | Live Value | Double | Live Value | Used in some specialised presentations
WCNV.GriPF_10m_Avg | #N/A | WCNV. | GriPF_10m_Avg | Power factor grid side (avg) | Leistungsfaktor Netzseite (avg) | Factor de potencia en el lado de la red eléctrica (avg) | Wsp.mocy strona sieci (avg) | Power factor average of all three phases | pf | PF | Average | Double | 10 minute tag | Common tags for analysis
WCNV.GriPF_10m_Max | #N/A | WCNV. | GriPF_10m_Max | Power factor grid side (max) | Leistungsfaktor Netzseite (max) | Factor de potencia en el lado de la red eléctrica (max) | Wsp.mocy strona sieci (max) | Power factor average of all three phases | pf | PF | Maximum | Double | 10 minute tag | Common tags for analysis
WCNV.GriPF_10m_Min | #N/A | WCNV. | GriPF_10m_Min | Power factor grid side (min) | Leistungsfaktor Netzseite (min) | Factor de potencia en el lado de la red eléctrica (min) | Wsp.mocy strona sieci (min) | Power factor average of all three phases | pf | PF | Minimum | Double | 10 minute tag | Common tags for analysis
WCNV.GriPF_10m_Std | #N/A | WCNV. | GriPF_10m_Std | Power factor grid side (std) | Leistungsfaktor Netzseite (std) | Factor de potencia en el lado de la red eléctrica (std) | Wsp.mocy strona sieci (std) | Power factor average of all three phases | pf | PF | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WCNV.GriPF1 | #N/A | WCNV. | GriPF1 | Power factor L1 grid side | Leistungsfaktor L1 Netzseite | Factor de potencia L1 en el lado de la red eléctrica | Wsp.mocy strona sieci L1 | Power factor phase L1 grid side | pf | PF | Live Value | Double | Live Value
WCNV.GriPF1_10m_Avg | #N/A | WCNV. | GriPF1_10m_Avg | Power factor L1 grid side (avg) | Leistungsfaktor L1 Netzseite (avg) | Factor de potencia L1 en el lado de la red eléctrica (avg) | Wsp.mocy strona sieci L1 (avg) | Power factor phase L1 grid side | pf | PF | Average | Double | 10 minute tag
WCNV.GriPF1_10m_Max | #N/A | WCNV. | GriPF1_10m_Max | Power factor L1 grid side (max) | Leistungsfaktor L1 Netzseite (max) | Factor de potencia L1 en el lado de la red eléctrica (max) | Wsp.mocy strona sieci L1 (max) | Power factor phase L1 grid side | pf | PF | Maximum | Double | 10 minute tag
WCNV.GriPF1_10m_Min | #N/A | WCNV. | GriPF1_10m_Min | Power factor L1 grid side (min) | Leistungsfaktor L1 Netzseite (min) | Factor de potencia L1 en el lado de la red eléctrica (min) | Wsp.mocy strona sieci L1 (min) | Power factor phase L1 grid side | pf | PF | Minimum | Double | 10 minute tag
WCNV.GriPF1_10m_Std | #N/A | WCNV. | GriPF1_10m_Std | Power factor L1 grid side (std) | Leistungsfaktor L1 Netzseite (std) | Factor de potencia L1 en el lado de la red eléctrica (std) | Wsp.mocy strona sieci L1 (std) | Power factor phase L1 grid side | pf | PF | Standard Deviation | Double | 10 minute tag
WCNV.GriPF2 | #N/A | WCNV. | GriPF2 | Power factor L2 grid side | Leistungsfaktor L2 Netzseite | Factor de potencia L2 en el lado de la red eléctrica | Wsp.mocy strona sieci L2 | Power factor phase L2 grid side | pf | PF | Live Value | Double | Live Value
WCNV.GriPF2_10m_Avg | #N/A | WCNV. | GriPF2_10m_Avg | Power factor L2 grid side (avg) | Leistungsfaktor L2 Netzseite (avg) | Factor de potencia L2 en el lado de la red eléctrica (avg) | Wsp.mocy strona sieci L2 (avg) | Power factor phase L2 grid side | pf | PF | Average | Double | 10 minute tag
WCNV.GriPF2_10m_Max | #N/A | WCNV. | GriPF2_10m_Max | Power factor L2 grid side (max) | Leistungsfaktor L2 Netzseite (max) | Factor de potencia L2 en el lado de la red eléctrica (max) | Wsp.mocy strona sieci L2 (max) | Power factor phase L2 grid side | pf | PF | Maximum | Double | 10 minute tag
WCNV.GriPF2_10m_Min | #N/A | WCNV. | GriPF2_10m_Min | Power factor L2 grid side (min) | Leistungsfaktor L2 Netzseite (min) | Factor de potencia L2 en el lado de la red eléctrica (min) | Wsp.mocy strona sieci L2 (min) | Power factor phase L2 grid side | pf | PF | Minimum | Double | 10 minute tag
WCNV.GriPF2_10m_Std | #N/A | WCNV. | GriPF2_10m_Std | Power factor L2 grid side (std) | Leistungsfaktor L2 Netzseite (std) | Factor de potencia L2 en el lado de la red eléctrica (std) | Wsp.mocy strona sieci L2 (std) | Power factor phase L2 grid side | pf | PF | Standard Deviation | Double | 10 minute tag
WCNV.GriPF3 | #N/A | WCNV. | GriPF3 | Power factor L3 grid side | Leistungsfaktor L3 Netzseite | Factor de potencia L3 en el lado de la red eléctrica | Wsp.mocy strona sieci L3 | Power factor phase L3 grid side | pf | PF | Live Value | Double | Live Value
WCNV.GriPF3_10m_Avg | #N/A | WCNV. | GriPF3_10m_Avg | Power factor L3 grid side (avg) | Leistungsfaktor L3 Netzseite (avg) | Factor de potencia L3 en el lado de la red eléctrica (avg) | Wsp.mocy strona sieci L3 (avg) | Power factor phase L3 grid side | pf | PF | Average | Double | 10 minute tag
WCNV.GriPF3_10m_Max | #N/A | WCNV. | GriPF3_10m_Max | Power factor L3 grid side (max) | Leistungsfaktor L3 Netzseite (max) | Factor de potencia L3 en el lado de la red eléctrica (max) | Wsp.mocy strona sieci L3 (max) | Power factor phase L3 grid side | pf | PF | Maximum | Double | 10 minute tag
WCNV.GriPF3_10m_Min | #N/A | WCNV. | GriPF3_10m_Min | Power factor L3 grid side (min) | Leistungsfaktor L3 Netzseite (min) | Factor de potencia L3 en el lado de la red eléctrica (min) | Wsp.mocy strona sieci L3 (min) | Power factor phase L3 grid side | pf | PF | Minimum | Double | 10 minute tag
WCNV.GriPF3_10m_Std | #N/A | WCNV. | GriPF3_10m_Std | Power factor L3 grid side (std) | Leistungsfaktor L3 Netzseite (std) | Factor de potencia L3 en el lado de la red eléctrica (std) | Wsp.mocy strona sieci L3 (std) | Power factor phase L3 grid side | pf | PF | Standard Deviation | Double | 10 minute tag
WCNV.GriPNV | WCNV.GriPNV | WCNV. | GriPNV | Converter P-N Voltage Grid side | Konverter P-N Spannung Netzseite | Tensión P-N del convertidor en el lado de la red eléctrica | Konwerter PN Nap. strona sieci | Voltage between phasesand neutral at the converter level (Grid side) | V | V | Live Value | Double | Live Value | Used in some specialised presentations
WCNV.GriPNV_10m_Avg | #N/A | WCNV. | GriPNV_10m_Avg | Converter P-N Voltage Grid side (avg) | Konverter P-N Spannung Netzseite (avg) | Tensión P-N del convertidor en el lado de la red eléctrica (avg) | Konwerter PN Nap. strona sieci (avg) | Voltage between phasesand neutral at the converter level (Grid side) | V | V | Average | Double | 10 minute tag | Common tags for analysis
WCNV.GriPNV_10m_Max | #N/A | WCNV. | GriPNV_10m_Max | Converter P-N Voltage Grid side (max) | Konverter P-N Spannung Netzseite (max) | Tensión P-N del convertidor en el lado de la red eléctrica (max) | Konwerter PN Nap. strona sieci (max) | Voltage between phasesand neutral at the converter level (Grid side) | V | V | Maximum | Double | 10 minute tag | Common tags for analysis
WCNV.GriPNV_10m_Min | #N/A | WCNV. | GriPNV_10m_Min | Converter P-N Voltage Grid side (min) | Konverter P-N Spannung Netzseite (min) | Tensión P-N del convertidor en el lado de la red eléctrica (min) | Konwerter PN Nap. strona sieci (min) | Voltage between phasesand neutral at the converter level (Grid side) | V | V | Minimum | Double | 10 minute tag | Common tags for analysis
WCNV.GriPNV_10m_Std | #N/A | WCNV. | GriPNV_10m_Std | Converter P-N Voltage Grid side (std) | Konverter P-N Spannung Netzseite (std) | Tensión P-N del convertidor en el lado de la red eléctrica (std) | Konwerter PN Nap. strona sieci (std) | Voltage between phasesand neutral at the converter level (Grid side) | V | V | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WCNV.GriPNV1 | #N/A | WCNV. | GriPNV1 | Converter P-N L1 Voltage Grid side | Konverter P-N L1 Spannung Netzseite | Tensión P-N L1 del convertidor en el lado de la red eléctrica | Konwerter P-N L1 Nap. strona sieci | Voltage between phase L1 and neutral at the converter level (Grid side) | V | V | Live Value | Double | Live Value | Used in some specialised presentations
WCNV.GriPNV1_10m_Avg | #N/A | WCNV. | GriPNV1_10m_Avg | Converter P-N L1 Voltage Grid side (avg) | Konverter P-N L1 Spannung Netzseite (avg) | Tensión P-N L1 del convertidor en el lado de la red eléctrica (avg) | Konwerter P-N L1 Nap. strona sieci (avg) | Voltage between phase L1 and neutral at the converter level (Grid side) | V | V | Average | Double | 10 minute tag | Common tags for analysis
WCNV.GriPNV1_10m_Max | #N/A | WCNV. | GriPNV1_10m_Max | Converter P-N L1 Voltage Grid side (max) | Konverter P-N L1 Spannung Netzseite (max) | Tensión P-N L1 del convertidor en el lado de la red eléctrica (max) | Konwerter P-N L1 Nap. strona sieci (max) | Voltage between phase L1 and neutral at the converter level (Grid side) | V | V | Maximum | Double | 10 minute tag | Common tags for analysis
WCNV.GriPNV1_10m_Min | #N/A | WCNV. | GriPNV1_10m_Min | Converter P-N L1 Voltage Grid side (min) | Konverter P-N L1 Spannung Netzseite (min) | Tensión P-N L1 del convertidor en el lado de la red eléctrica (min) | Konwerter P-N L1 Nap. strona sieci (min) | Voltage between phase L1 and neutral at the converter level (Grid side) | V | V | Minimum | Double | 10 minute tag | Common tags for analysis
WCNV.GriPNV1_10m_Std | #N/A | WCNV. | GriPNV1_10m_Std | Converter P-N L1 Voltage Grid side (std) | Konverter P-N L1 Spannung Netzseite (std) | Tensión P-N L1 del convertidor en el lado de la red eléctrica (std) | Konwerter P-N L1 Nap. strona sieci (std) | Voltage between phase L1 and neutral at the converter level (Grid side) | V | V | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WCNV.GriPNV2 | #N/A | WCNV. | GriPNV2 | Converter P-N L2 Voltage Grid side | Konverter P-N L2 Spannung Netzseite | Tensión P-N L2 del convertidor en el lado de la red eléctrica | Konwerter P-N L2 Nap. strona sieci | Voltage between phase L2 and neutral at the converter level (Grid side) | V | V | Live Value | Double | Live Value | Used in some specialised presentations
WCNV.GriPNV2_10m_Avg | #N/A | WCNV. | GriPNV2_10m_Avg | Converter P-N L2 Voltage Grid side (avg) | Konverter P-N L2 Spannung Netzseite (avg) | Tensión P-N L2 del convertidor en el lado de la red eléctrica (avg) | Konwerter P-N L2 Nap. strona sieci (avg) | Voltage between phase L2 and neutral at the converter level (Grid side) | V | V | Average | Double | 10 minute tag | Common tags for analysis
WCNV.GriPNV2_10m_Max | #N/A | WCNV. | GriPNV2_10m_Max | Converter P-N L2 Voltage Grid side (max) | Konverter P-N L2 Spannung Netzseite (max) | Tensión P-N L2 del convertidor en el lado de la red eléctrica (max) | Konwerter P-N L2 Nap. strona sieci (max) | Voltage between phase L2 and neutral at the converter level (Grid side) | V | V | Maximum | Double | 10 minute tag | Common tags for analysis
WCNV.GriPNV2_10m_Min | #N/A | WCNV. | GriPNV2_10m_Min | Converter P-N L2 Voltage Grid side (min) | Konverter P-N L2 Spannung Netzseite (min) | Tensión P-N L2 del convertidor en el lado de la red eléctrica (min) | Konwerter P-N L2 Nap. strona sieci (min) | Voltage between phase L2 and neutral at the converter level (Grid side) | V | V | Minimum | Double | 10 minute tag | Common tags for analysis
WCNV.GriPNV2_10m_Std | #N/A | WCNV. | GriPNV2_10m_Std | Converter P-N L2 Voltage Grid side (std) | Konverter P-N L2 Spannung Netzseite (std) | Tensión P-N L2 del convertidor en el lado de la red eléctrica (std) | Konwerter P-N L2 Nap. strona sieci (std) | Voltage between phase L2 and neutral at the converter level (Grid side) | V | V | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WCNV.GriPNV3 | #N/A | WCNV. | GriPNV3 | Converter P-N L3 Voltage Grid side | Konverter P-N L3 Spannung Netzseite | Tensión P-N L3 del convertidor en el lado de la red eléctrica | Konwerter P-N L3 Nap. strona sieci | Voltage between phase L3 and neutral at the converter level (Grid Side) | V | V | Live Value | Double | Live Value | Used in some specialised presentations
WCNV.GriPNV3_10m_Avg | #N/A | WCNV. | GriPNV3_10m_Avg | Converter P-N L3 Voltage Grid side (avg) | Konverter P-N L3 Spannung Netzseite (avg) | Tensión P-N L3 del convertidor en el lado de la red eléctrica (avg) | Konwerter P-N L3 Nap. strona sieci (avg) | Voltage between phase L3 and neutral at the converter level (Grid Side) | V | V | Average | Double | 10 minute tag | Common tags for analysis
WCNV.GriPNV3_10m_Max | #N/A | WCNV. | GriPNV3_10m_Max | Converter P-N L3 Voltage Grid side (max) | Konverter P-N L3 Spannung Netzseite (max) | Tensión P-N L3 del convertidor en el lado de la red eléctrica (max) | Konwerter P-N L3 Nap. strona sieci (max) | Voltage between phase L3 and neutral at the converter level (Grid Side) | V | V | Maximum | Double | 10 minute tag | Common tags for analysis
WCNV.GriPNV3_10m_Min | #N/A | WCNV. | GriPNV3_10m_Min | Converter P-N L3 Voltage Grid side (min) | Konverter P-N L3 Spannung Netzseite (min) | Tensión P-N L3 del convertidor en el lado de la red eléctrica (min) | Konwerter P-N L3 Nap. strona sieci (min) | Voltage between phase L3 and neutral at the converter level (Grid Side) | V | V | Minimum | Double | 10 minute tag | Common tags for analysis
WCNV.GriPNV3_10m_Std | #N/A | WCNV. | GriPNV3_10m_Std | Converter P-N L3 Voltage Grid side (std) | Konverter P-N L3 Spannung Netzseite (std) | Tensión P-N L3 del convertidor en el lado de la red eléctrica (std) | Konwerter P-N L3 Nap. strona sieci (std) | Voltage between phase L3 and neutral at the converter level (Grid Side) | V | V | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WCNV.GriPPV | WCNV.GriPPV | WCNV. | GriPPV | Converter P-P Voltage Grid side | Konverter P-P Spannung Netzseite | Tensión P-P del convertidor en el lado de la red eléctrica | Konwerter P-P Nap. strona sieci | Grid side 3 phase phase-to-phase voltage | V | V | Live Value | Double | Live Value
WCNV.GriPPV1 | #N/A | WCNV. | GriPPV1 | Converter P-P L1-L2 Voltage Grid side | Konverter P-P L1-L2 Spannung Netzseite | Tensión P-P L1-L2 del convertidor en el lado de la red eléctrica | Konwerter P-P L1-L2 Nap. strona sieci | Grid side L1 3 phase phase-to-phase voltage | V | V | Live Value | Double | Live Value
WCNV.GriPPV1_10m_Avg | #N/A | WCNV. | GriPPV1_10m_Avg | Converter P-P L1-L2 Voltage Grid side (avg) | Konverter P-P L1-L2 Spannung Netzseite (avg) | Tensión P-P L1-L2 del convertidor en el lado de la red eléctrica (avg) | Konwerter P-P L1-L2 Nap. strona sieci (avg) | Grid side L1 3 phase phase-to-phase voltage | V | V | Average | Double | 10 minute tag | Common tags for analysis
WCNV.GriPPV1_10m_Max | #N/A | WCNV. | GriPPV1_10m_Max | Converter P-P L1-L2 Voltage Grid side (max) | Konverter P-P L1-L2 Spannung Netzseite (max) | Tensión P-P L1-L2 del convertidor en el lado de la red eléctrica (max) | Konwerter P-P L1-L2 Nap. strona sieci (max) | Grid side L1 3 phase phase-to-phase voltage | V | V | Maximum | Double | 10 minute tag | Common tags for analysis
WCNV.GriPPV1_10m_Min | #N/A | WCNV. | GriPPV1_10m_Min | Converter P-P L1-L2 Voltage Grid side (min) | Konverter P-P L1-L2 Spannung Netzseite (min) | Tensión P-P L1-L2 del convertidor en el lado de la red eléctrica (min) | Konwerter P-P L1-L2 Nap. strona sieci (min) | Grid side L1 3 phase phase-to-phase voltage | V | V | Minimum | Double | 10 minute tag | Common tags for analysis
WCNV.GriPPV1_10m_Std | #N/A | WCNV. | GriPPV1_10m_Std | Converter P-P L1-L2 Voltage Grid side (std) | Konverter P-P L1-L2 Spannung Netzseite (std) | Tensión P-P L1-L2 del convertidor en el lado de la red eléctrica (std) | Konwerter P-P L1-L2 Nap. strona sieci (std) | Grid side L1 3 phase phase-to-phase voltage | V | V | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WCNV.GriPPV2 | #N/A | WCNV. | GriPPV2 | Converter P-P L2-L3 Voltage Grid side | Konverter P-P L2-L3 Spannung Netzseite | Tensión P-P L2-L3 del convertidor en el lado de la red eléctrica | Konwerter P-P L2-L3 Nap. strona sieci | Grid side L2 3 phase phase-to-phase voltage | V | V | Live Value | Double | Live Value
WCNV.GriPPV2_10m_Avg | #N/A | WCNV. | GriPPV2_10m_Avg | Converter P-P L2-L3 Voltage Grid side (avg) | Konverter P-P L2-L3 Spannung Netzseite (avg) | Tensión P-P L2-L3 del convertidor en el lado de la red eléctrica (avg) | Konwerter P-P L2-L3 Nap. strona sieci (avg) | Grid side L2 3 phase phase-to-phase voltage | V | V | Average | Double | 10 minute tag | Common tags for analysis
WCNV.GriPPV2_10m_Max | #N/A | WCNV. | GriPPV2_10m_Max | Converter P-P L2-L3 Voltage Grid side (max) | Konverter P-P L2-L3 Spannung Netzseite (max) | Tensión P-P L2-L3 del convertidor en el lado de la red eléctrica (max) | Konwerter P-P L2-L3 Nap. strona sieci (max) | Grid side L2 3 phase phase-to-phase voltage | V | V | Maximum | Double | 10 minute tag | Common tags for analysis
WCNV.GriPPV2_10m_Min | #N/A | WCNV. | GriPPV2_10m_Min | Converter P-P L2-L3 Voltage Grid side (min) | Konverter P-P L2-L3 Spannung Netzseite (min) | Tensión P-P L2-L3 del convertidor en el lado de la red eléctrica (min) | Konwerter P-P L2-L3 Nap. strona sieci (min) | Grid side L2 3 phase phase-to-phase voltage | V | V | Minimum | Double | 10 minute tag | Common tags for analysis
WCNV.GriPPV2_10m_Std | #N/A | WCNV. | GriPPV2_10m_Std | Converter P-P L2-L3 Voltage Grid side (std) | Konverter P-P L2-L3 Spannung Netzseite (std) | Tensión P-P L2-L3 del convertidor en el lado de la red eléctrica (std) | Konwerter P-P L2-L3 Nap. strona sieci (std) | Grid side L2 3 phase phase-to-phase voltage | V | V | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WCNV.GriPPV3 | #N/A | WCNV. | GriPPV3 | Converter P-P L3-L1 Voltage Grid side | Konverter P-P L3-L1 Spannung Netzseite | Tensión P-P L3-L1 del convertidor en el lado de la red eléctrica | Konwerter P-P L3-L1 Nap. strona sieci | Grid side L3 3 phase phase-to-phase voltage | V | V | Live Value | Double | Live Value
WCNV.GriPPV3_10m_Avg | #N/A | WCNV. | GriPPV3_10m_Avg | Converter P-P L3-L1 Voltage Grid side (avg) | Konverter P-P L3-L1 Spannung Netzseite (avg) | Tensión P-P L3-L1 del convertidor en el lado de la red eléctrica (avg) | Konwerter P-P L3-L1 Nap. strona sieci (avg) | Grid side L3 3 phase phase-to-phase voltage | V | V | Average | Double | 10 minute tag | Common tags for analysis
WCNV.GriPPV3_10m_Max | #N/A | WCNV. | GriPPV3_10m_Max | Converter P-P L3-L1 Voltage Grid side (max) | Konverter P-P L3-L1 Spannung Netzseite (max) | Tensión P-P L3-L1 del convertidor en el lado de la red eléctrica (max) | Konwerter P-P L3-L1 Nap. strona sieci (max) | Grid side L3 3 phase phase-to-phase voltage | V | V | Maximum | Double | 10 minute tag | Common tags for analysis
WCNV.GriPPV3_10m_Min | #N/A | WCNV. | GriPPV3_10m_Min | Converter P-P L3-L1 Voltage Grid side (min) | Konverter P-P L3-L1 Spannung Netzseite (min) | Tensión P-P L3-L1 del convertidor en el lado de la red eléctrica (min) | Konwerter P-P L3-L1 Nap. strona sieci (min) | Grid side L3 3 phase phase-to-phase voltage | V | V | Minimum | Double | 10 minute tag | Common tags for analysis
WCNV.GriPPV3_10m_Std | #N/A | WCNV. | GriPPV3_10m_Std | Converter P-P L3-L1 Voltage Grid side (std) | Konverter P-P L3-L1 Spannung Netzseite (std) | Tensión P-P L3-L1 del convertidor en el lado de la red eléctrica (std) | Konwerter P-P L3-L1 Nap. strona sieci (std) | Grid side L3 3 phase phase-to-phase voltage | V | V | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WCNV.GriTmp | WCNV.GriTmp | WCNV. | GriTmp | Converter Grid Side Temp | Konverter Netzseitige Temperatur | Temperatura del convertidor en el lado de la red eléctrica | Temp po stronie sieci konwertera | Converter temperature grid side | deg_c | °C | Live Value | Double | Live Value
WCNV.GriTmp_10m_Avg | #N/A | WCNV. | GriTmp_10m_Avg | Converter Grid Side Temp (avg) | Konverter Netzseitige Temperatur (avg) | Temperatura del convertidor en el lado de la red eléctrica (avg) | Temp po stronie sieci konwertera (avg) | Converter temperature grid side | deg_c | °C | Average | Double | 10 minute tag
WCNV.GriTmp_10m_Max | #N/A | WCNV. | GriTmp_10m_Max | Converter Grid Side Temp (max) | Konverter Netzseitige Temperatur (max) | Temperatura del convertidor en el lado de la red eléctrica (max) | Temp po stronie sieci konwertera (max) | Converter temperature grid side | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.GriTmp_10m_Min | #N/A | WCNV. | GriTmp_10m_Min | Converter Grid Side Temp (min) | Konverter Netzseitige Temperatur (min) | Temperatura del convertidor en el lado de la red eléctrica (min) | Temp po stronie sieci konwertera (min) | Converter temperature grid side | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.GriTmp_10m_Std | #N/A | WCNV. | GriTmp_10m_Std | Converter Grid Side Temp (std) | Konverter Netzseitige Temperatur (std) | Temperatura del convertidor en el lado de la red eléctrica (std) | Temp po stronie sieci konwertera (std) | Converter temperature grid side | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.GriTmp1 | #N/A | WCNV. | GriTmp1 | Converter Grid L1 Side Temp | Konverter Netz L1 Seite Temperatur | Temperatura del convertidor L1 en el lado de la red eléctrica | Konwerter L1 Temp. strona sieci | Converter temperature phase L1, grid side | deg_c | °C | Live Value | Double | Live Value
WCNV.GriTmp1_10m_Avg | #N/A | WCNV. | GriTmp1_10m_Avg | Converter Grid L1 Side Temp (avg) | Konverter Netz L1 Seite Temperatur (avg) | Temperatura del convertidor L1 en el lado de la red eléctrica (avg) | Konwerter L1 Temp. strona sieci (avg) | Converter temperature phase L1, grid side | deg_c | °C | Average | Double | 10 minute tag
WCNV.GriTmp1_10m_Max | #N/A | WCNV. | GriTmp1_10m_Max | Converter Grid L1 Side Temp (max) | Konverter Netz L1 Seite Temperatur (max) | Temperatura del convertidor L1 en el lado de la red eléctrica (max) | Konwerter L1 Temp. strona sieci (max) | Converter temperature phase L1, grid side | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.GriTmp1_10m_Min | #N/A | WCNV. | GriTmp1_10m_Min | Converter Grid L1 Side Temp (min) | Konverter Netz L1 Seite Temperatur (min) | Temperatura del convertidor L1 en el lado de la red eléctrica (min) | Konwerter L1 Temp. strona sieci (min) | Converter temperature phase L1, grid side | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.GriTmp1_10m_Std | #N/A | WCNV. | GriTmp1_10m_Std | Converter Grid L1 Side Temp (std) | Konverter Netz L1 Seite Temperatur (std) | Temperatura del convertidor L1 en el lado de la red eléctrica (std) | Konwerter L1 Temp. strona sieci (std) | Converter temperature phase L1, grid side | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.GriTmp2 | #N/A | WCNV. | GriTmp2 | Converter Grid L2 Side Temp | Konverter Netz L2 Seite Temperatur | Temperatura del convertidor L2 en el lado de la red eléctrica | Konwerter L2 Temp. strona sieci | Converter temperature phase L2, grid side | deg_c | °C | Live Value | Double | Live Value
WCNV.GriTmp2_10m_Avg | #N/A | WCNV. | GriTmp2_10m_Avg | Converter Grid L2 Side Temp (avg) | Konverter Netz L2 Seite Temperatur (avg) | Temperatura del convertidor L2 en el lado de la red eléctrica (avg) | Konwerter L2 Temp. strona sieci (avg) | Converter temperature phase L2, grid side | deg_c | °C | Average | Double | 10 minute tag
WCNV.GriTmp2_10m_Max | #N/A | WCNV. | GriTmp2_10m_Max | Converter Grid L2 Side Temp (max) | Konverter Netz L2 Seite Temperatur (max) | Temperatura del convertidor L2 en el lado de la red eléctrica (max) | Konwerter L2 Temp. strona sieci (max) | Converter temperature phase L2, grid side | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.GriTmp2_10m_Min | #N/A | WCNV. | GriTmp2_10m_Min | Converter Grid L2 Side Temp (min) | Konverter Netz L2 Seite Temperatur (min) | Temperatura del convertidor L2 en el lado de la red eléctrica (min) | Konwerter L2 Temp. strona sieci (min) | Converter temperature phase L2, grid side | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.GriTmp2_10m_Std | #N/A | WCNV. | GriTmp2_10m_Std | Converter Grid L2 Side Temp (std) | Konverter Netz L2 Seite Temperatur (std) | Temperatura del convertidor L2 en el lado de la red eléctrica (std) | Konwerter L2 Temp. strona sieci (std) | Converter temperature phase L2, grid side | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.GriTmp3 | #N/A | WCNV. | GriTmp3 | Converter Grid L3 Side Temp | Konverter Netz L3 Seite Temperatur | Temperatura del convertidor L3 en el lado de la red eléctrica | Konwerter L3 Temp. strona sieci | Converter temperature phase L3, grid side | deg_c | °C | Live Value | Double | Live Value
WCNV.GriTmp3_10m_Avg | #N/A | WCNV. | GriTmp3_10m_Avg | Converter Grid L3 Side Temp (avg) | Konverter Netz L3 Seite Temperatur (avg) | Temperatura del convertidor L3 en el lado de la red eléctrica (avg) | Konwerter L3 Temp. strona sieci (avg) | Converter temperature phase L3, grid side | deg_c | °C | Average | Double | 10 minute tag
WCNV.GriTmp3_10m_Max | #N/A | WCNV. | GriTmp3_10m_Max | Converter Grid L3 Side Temp (max) | Konverter Netz L3 Seite Temperatur (max) | Temperatura del convertidor L3 en el lado de la red eléctrica (max) | Konwerter L3 Temp. strona sieci (max) | Converter temperature phase L3, grid side | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.GriTmp3_10m_Min | #N/A | WCNV. | GriTmp3_10m_Min | Converter Grid L3 Side Temp (min) | Konverter Netz L3 Seite Temperatur (min) | Temperatura del convertidor L3 en el lado de la red eléctrica (min) | Konwerter L3 Temp. strona sieci (min) | Converter temperature phase L3, grid side | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.GriTmp3_10m_Std | #N/A | WCNV. | GriTmp3_10m_Std | Converter Grid L3 Side Temp (std) | Konverter Netz L3 Seite Temperatur (std) | Temperatura del convertidor L3 en el lado de la red eléctrica (std) | Konwerter L3 Temp. strona sieci (std) | Converter temperature phase L3, grid side | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.GriW | #N/A | WCNV. | GriW | Converter Active power grid side | Konverter Wirkleistung Netzseite | Potencia activa del convertidor en el lado de la red eléctrica | Konwerter Moc czynna strona sieci | Converter Active power grid side | W | W | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WCNV.HtSnkTmp | #N/A | WCNV. | HtSnkTmp | Converter Heat Sink Temp | Kühlkörpertemperatur des Konverters | Temperatura del disipador térmico del convertidor | Konwerer Temp. radiatora | Converter Heat Sink Temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.HtSnkTmp_10m_Avg | #N/A | WCNV. | HtSnkTmp_10m_Avg | Converter Heat Sink Temp (avg) | Kühlkörpertemperatur des Konverters (avg) | Temperatura del disipador térmico del convertidor (avg) | Konwerer Temp. radiatora (avg) | Converter Heat Sink Temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.HtSnkTmp_10m_Max | #N/A | WCNV. | HtSnkTmp_10m_Max | Converter Heat Sink Temp (max) | Kühlkörpertemperatur des Konverters (max) | Temperatura del disipador térmico del convertidor (max) | Konwerer Temp. radiatora (max) | Converter Heat Sink Temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.HtSnkTmp_10m_Min | #N/A | WCNV. | HtSnkTmp_10m_Min | Converter Heat Sink Temp (min) | Kühlkörpertemperatur des Konverters (min) | Temperatura del disipador térmico del convertidor (min) | Konwerer Temp. radiatora (min) | Converter Heat Sink Temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.HtSnkTmp_10m_Std | #N/A | WCNV. | HtSnkTmp_10m_Std | Converter Heat Sink Temp (std) | Kühlkörpertemperatur des Konverters (std) | Temperatura del disipador térmico del convertidor (std) | Konwerer Temp. radiatora (std) | Converter Heat Sink Temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.MainPnlFanCnt | #N/A | WCNV. | MainPnlFanCnt | Number of activations of main panel fan | Anzahl der Aktivierungen des Hauptpanellüfters | Número de activaciones del ventilador del panel principal | Liczba aktywacji wentylatora głównego panelu | Number of activations of main panel fan | count | Count | Total Counter | Long | Live Value
WCNV.MainPnlFanCnt_10m_End | #N/A | WCNV. | MainPnlFanCnt_10m_End | Number of activations of main panel fan (end) | Anzahl der Aktivierungen des Hauptpanellüfters (end) | Número de activaciones del ventilador del panel principal (end) | Liczba aktywacji wentylatora głównego panelu (end) | Number of activations of main panel fan | count | Count | Endvalue | Long | 10 minute tag
WCNV.MainPnlFanTms | #N/A | WCNV. | MainPnlFanTms | Time main panel fan has been activated | Zeit, in der der Lüfter des Hauptpanels aktiviert wurde | Tiempo que el ventilador del panel principal ha estado activado | Czas aktywacji wentylatora panelu głów. | Time main panel fan has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.MainPnlFanTms_10m_End | #N/A | WCNV. | MainPnlFanTms_10m_End | Time main panel fan has been activated (end) | Zeit, in der der Lüfter des Hauptpanels aktiviert wurde (end) | Tiempo que el ventilador del panel principal ha estado activado (end) | Czas aktywacji wentylatora panelu głów. (end) | Time main panel fan has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.MainPnlHtCnt | #N/A | WCNV. | MainPnlHtCnt | Number of activations of main panel heat | Anzahl der Aktivierungen der Hauptpanelheizung | Número de activaciones del calentador del panel principal | Liczba aktywacji ogrz. panelu głównego | Number of activations of main panel heat | count | Count | Total Counter | Long | Live Value
WCNV.MainPnlHtCnt_10m_End | #N/A | WCNV. | MainPnlHtCnt_10m_End | Number of activations of main panel heat (end) | Anzahl der Aktivierungen der Hauptpanelheizung (end) | Número de activaciones del calentador del panel principal (end) | Liczba aktywacji ogrz. panelu głównego (end) | Number of activations of main panel heat | count | Count | Endvalue | Long | 10 minute tag
WCNV.MainPnlHtTms | #N/A | WCNV. | MainPnlHtTms | Time main panel heat has been activated | Zeit, in der die Heizung des Hauptpanels aktiviert wurde | Tiempo que el calentador del panel principal ha estado activado | Czas aktywacji ogrzew. panelu głów. | Time main panel heat has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.MainPnlHtTms_10m_End | #N/A | WCNV. | MainPnlHtTms_10m_End | Time main panel heat has been activated (end) | Zeit, in der die Heizung des Hauptpanels aktiviert wurde (end) | Tiempo que el calentador del panel principal ha estado activado (end) | Czas aktywacji ogrzew. panelu głów. (end) | Time main panel heat has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.MainPnlTmp | #N/A | WCNV. | MainPnlTmp | Main Panel Temp | Hauptpanel-Temperatur | Temperatura del panel principal | Temp panelu głównego | Main panel temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.MainPnlTmp_10m_Avg | #N/A | WCNV. | MainPnlTmp_10m_Avg | Main Panel Temp (avg) | Hauptpanel-Temperatur (avg) | Temperatura del panel principal (avg) | Temp panelu głównego (avg) | Main panel temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.MainPnlTmp_10m_Max | #N/A | WCNV. | MainPnlTmp_10m_Max | Main Panel Temp (max) | Hauptpanel-Temperatur (max) | Temperatura del panel principal (max) | Temp panelu głównego (max) | Main panel temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.MainPnlTmp_10m_Min | #N/A | WCNV. | MainPnlTmp_10m_Min | Main Panel Temp (min) | Hauptpanel-Temperatur (min) | Temperatura del panel principal (min) | Temp panelu głównego (min) | Main panel temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.MainPnlTmp_10m_Std | #N/A | WCNV. | MainPnlTmp_10m_Std | Main Panel Temp (std) | Hauptpanel-Temperatur (std) | Temperatura del panel principal (std) | Temp panelu głównego (std) | Main panel temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.OpPnlTmp | #N/A | WCNV. | OpPnlTmp | Operation Panel Temp | Bedienpanel-Temperatur | Temperatura del panel operativo | Temp panelu operacyjnego | Operation panel temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.OpPnlTmp_10m_Avg | #N/A | WCNV. | OpPnlTmp_10m_Avg | Operation Panel Temp (avg) | Bedienpanel-Temperatur (avg) | Temperatura del panel operativo (avg) | Temp panelu operacyjnego (avg) | Operation panel temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.OpPnlTmp_10m_Max | #N/A | WCNV. | OpPnlTmp_10m_Max | Operation Panel Temp (max) | Bedienpanel-Temperatur (max) | Temperatura del panel operativo (max) | Temp panelu operacyjnego (max) | Operation panel temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.OpPnlTmp_10m_Min | #N/A | WCNV. | OpPnlTmp_10m_Min | Operation Panel Temp (min) | Bedienpanel-Temperatur (min) | Temperatura del panel operativo (min) | Temp panelu operacyjnego (min) | Operation panel temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.OpPnlTmp_10m_Std | #N/A | WCNV. | OpPnlTmp_10m_Std | Operation Panel Temp (std) | Bedienpanel-Temperatur (std) | Temperatura del panel operativo (std) | Temp panelu operacyjnego (std) | Operation panel temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.OpTmsRs | WCNV.OpTmsRs | WCNV. | OpTmsRs | Converter operation time | Betriebszeit des Konverters | Tiempo de funcionamiento del convertidor | Czas pracy konwertera | Converter operation time in seconds (vendor specific) | s | seconds | Total Counter | Long | Live Value
WCNV.PhsCmpCnt1 | #N/A | WCNV. | PhsCmpCnt1 | Number of activations of phase compensation step 1 | Anzahl der Aktivierungen der Phasenkompensationsstufe 1 | Número de activaciones del paso 1 de compensación de fase | Liczba aktywacji etapu kompensacji fazowej 1 | Number of activations of phase compensation step 1 | count | Count | Total Counter | Long | Live Value
WCNV.PhsCmpCnt1_10m_End | #N/A | WCNV. | PhsCmpCnt1_10m_End | Number of activations of phase compensation step 1 (end) | Anzahl der Aktivierungen der Phasenkompensationsstufe 1 (end) | Número de activaciones del paso 1 de compensación de fase (end) | Liczba aktywacji etapu kompensacji fazowej 1 (end) | Number of activations of phase compensation step 1 | count | Count | Endvalue | Long | 10 minute tag
WCNV.PhsCmpCnt10 | #N/A | WCNV. | PhsCmpCnt10 | Number of activations of phase compensation step 10 | Anzahl der Aktivierungen der Phasenkompensationsstufe 10 | Número de activaciones del paso 10 de compensación de fase | Liczba aktywacji etapu kompensacji fazowej 10 | Number of activations of phase compensation step 10 | count | Count | Total Counter | Long | Live Value
WCNV.PhsCmpCnt10_10m_End | #N/A | WCNV. | PhsCmpCnt10_10m_End | Number of activations of phase compensation step 10 (end) | Anzahl der Aktivierungen der Phasenkompensationsstufe 10 (end) | Número de activaciones del paso 10 de compensación de fase (end) | Liczba aktywacji etapu kompensacji fazowej 10 (end) | Number of activations of phase compensation step 10 | count | Count | Endvalue | Long | 10 minute tag
WCNV.PhsCmpCnt2 | #N/A | WCNV. | PhsCmpCnt2 | Number of activations of phase compensation step 2 | Anzahl der Aktivierungen der Phasenkompensationsstufe 2 | Número de activaciones del paso 2 de compensación de fase | Liczba aktywacji etapu kompensacji fazowej 2 | Number of activations of phase compensation step 2 | count | Count | Total Counter | Long | Live Value
WCNV.PhsCmpCnt2_10m_End | #N/A | WCNV. | PhsCmpCnt2_10m_End | Number of activations of phase compensation step 2 (end) | Anzahl der Aktivierungen der Phasenkompensationsstufe 2 (end) | Número de activaciones del paso 2 de compensación de fase (end) | Liczba aktywacji etapu kompensacji fazowej 2 (end) | Number of activations of phase compensation step 2 | count | Count | Endvalue | Long | 10 minute tag
WCNV.PhsCmpCnt3 | #N/A | WCNV. | PhsCmpCnt3 | Number of activations of phase compensation step 3 | Anzahl der Aktivierungen der Phasenkompensationsstufe 3 | Número de activaciones del paso 3 de compensación de fase | Liczba aktywacji etapu kompensacji fazowej 3 | Number of activations of phase compensation step 3 | count | Count | Total Counter | Long | Live Value
WCNV.PhsCmpCnt3_10m_End | #N/A | WCNV. | PhsCmpCnt3_10m_End | Number of activations of phase compensation step 3 (end) | Anzahl der Aktivierungen der Phasenkompensationsstufe 3 (end) | Número de activaciones del paso 3 de compensación de fase (end) | Liczba aktywacji etapu kompensacji fazowej 3 (end) | Number of activations of phase compensation step 3 | count | Count | Endvalue | Long | 10 minute tag
WCNV.PhsCmpCnt4 | #N/A | WCNV. | PhsCmpCnt4 | Number of activations of phase compensation step 4 | Anzahl der Aktivierungen der Phasenkompensationsstufe 4 | Número de activaciones del paso 4 de compensación de fase | Liczba aktywacji etapu kompensacji fazowej 4 | Number of activations of phase compensation step 4 | count | Count | Total Counter | Long | Live Value
WCNV.PhsCmpCnt4_10m_End | #N/A | WCNV. | PhsCmpCnt4_10m_End | Number of activations of phase compensation step 4 (end) | Anzahl der Aktivierungen der Phasenkompensationsstufe 4 (end) | Número de activaciones del paso 4 de compensación de fase (end) | Liczba aktywacji etapu kompensacji fazowej 4 (end) | Number of activations of phase compensation step 4 | count | Count | Endvalue | Long | 10 minute tag
WCNV.PhsCmpCnt5 | #N/A | WCNV. | PhsCmpCnt5 | Number of activations of phase compensation step 5 | Anzahl der Aktivierungen der Phasenkompensationsstufe 5 | Número de activaciones del paso 5 de compensación de fase | Liczba aktywacji etapu kompensacji fazowej 5 | Number of activations of phase compensation step 5 | count | Count | Total Counter | Long | Live Value
WCNV.PhsCmpCnt5_10m_End | #N/A | WCNV. | PhsCmpCnt5_10m_End | Number of activations of phase compensation step 5 (end) | Anzahl der Aktivierungen der Phasenkompensationsstufe 5 (end) | Número de activaciones del paso 5 de compensación de fase (end) | Liczba aktywacji etapu kompensacji fazowej 5 (end) | Number of activations of phase compensation step 5 | count | Count | Endvalue | Long | 10 minute tag
WCNV.PhsCmpCnt6 | #N/A | WCNV. | PhsCmpCnt6 | Number of activations of phase compensation step 6 | Anzahl der Aktivierungen der Phasenkompensationsstufe 6 | Número de activaciones del paso 6 de compensación de fase | Liczba aktywacji etapu kompensacji fazowej 6 | Number of activations of phase compensation step 6 | count | Count | Total Counter | Long | Live Value
WCNV.PhsCmpCnt6_10m_End | #N/A | WCNV. | PhsCmpCnt6_10m_End | Number of activations of phase compensation step 6 (end) | Anzahl der Aktivierungen der Phasenkompensationsstufe 6 (end) | Número de activaciones del paso 6 de compensación de fase (end) | Liczba aktywacji etapu kompensacji fazowej 6 (end) | Number of activations of phase compensation step 6 | count | Count | Endvalue | Long | 10 minute tag
WCNV.PhsCmpCnt7 | #N/A | WCNV. | PhsCmpCnt7 | Number of activations of phase compensation step 7 | Anzahl der Aktivierungen der Phasenkompensationsstufe 7 | Número de activaciones del paso 7 de compensación de fase | Liczba aktywacji etapu kompensacji fazowej 7 | Number of activations of phase compensation step 7 | count | Count | Total Counter | Long | Live Value
WCNV.PhsCmpCnt7_10m_End | #N/A | WCNV. | PhsCmpCnt7_10m_End | Number of activations of phase compensation step 7 (end) | Anzahl der Aktivierungen der Phasenkompensationsstufe 7 (end) | Número de activaciones del paso 7 de compensación de fase (end) | Liczba aktywacji etapu kompensacji fazowej 7 (end) | Number of activations of phase compensation step 7 | count | Count | Endvalue | Long | 10 minute tag
WCNV.PhsCmpCnt8 | #N/A | WCNV. | PhsCmpCnt8 | Number of activations of phase compensation step 8 | Anzahl der Aktivierungen der Phasenkompensationsstufe 8 | Número de activaciones del paso 8 de compensación de fase | Liczba aktywacji etapu kompensacji fazowej 8 | Number of activations of phase compensation step 8 | count | Count | Total Counter | Long | Live Value
WCNV.PhsCmpCnt8_10m_End | #N/A | WCNV. | PhsCmpCnt8_10m_End | Number of activations of phase compensation step 8 (end) | Anzahl der Aktivierungen der Phasenkompensationsstufe 8 (end) | Número de activaciones del paso 8 de compensación de fase (end) | Liczba aktywacji etapu kompensacji fazowej 8 (end) | Number of activations of phase compensation step 8 | count | Count | Endvalue | Long | 10 minute tag
WCNV.PhsCmpCnt9 | #N/A | WCNV. | PhsCmpCnt9 | Number of activations of phase compensation step 9 | Anzahl der Aktivierungen der Phasenkompensationsstufe 9 | Número de activaciones del paso 9 de compensación de fase | Liczba aktywacji etapu kompensacji fazowej 9 | Number of activations of phase compensation step 9 | count | Count | Total Counter | Long | Live Value
WCNV.PhsCmpCnt9_10m_End | #N/A | WCNV. | PhsCmpCnt9_10m_End | Number of activations of phase compensation step 9 (end) | Anzahl der Aktivierungen der Phasenkompensationsstufe 9 (end) | Número de activaciones del paso 9 de compensación de fase (end) | Liczba aktywacji etapu kompensacji fazowej 9 (end) | Number of activations of phase compensation step 9 | count | Count | Endvalue | Long | 10 minute tag
WCNV.PhsCmpDclV | #N/A | WCNV. | PhsCmpDclV | PCS DC Link Voltage | Phasenkompensationsstufe Zwischenkreisspannung | Tensión del enlace CC PCS | Pcs DC Link Napięcie | Phase Compensation DC Link Voltage | V | V | Live Value | Double | Live Value
WCNV.PhsCmpDclV_10m_Avg | #N/A | WCNV. | PhsCmpDclV_10m_Avg | PCS DC Link Voltage (avg) | Phasenkompensationsstufe Zwischenkreisspannung (avg) | Tensión del enlace CC PCS (avg) | Pcs DC Link Napięcie (avg) | Phase Compensation DC Link Voltage | V | V | Average | Double | 10 minute tag
WCNV.PhsCmpDclV_10m_Max | #N/A | WCNV. | PhsCmpDclV_10m_Max | PCS DC Link Voltage (max) | Phasenkompensationsstufe Zwischenkreisspannung (max) | Tensión del enlace CC PCS (max) | Pcs DC Link Napięcie (max) | Phase Compensation DC Link Voltage | V | V | Maximum | Double | 10 minute tag
WCNV.PhsCmpDclV_10m_Min | #N/A | WCNV. | PhsCmpDclV_10m_Min | PCS DC Link Voltage (min) | Phasenkompensationsstufe Zwischenkreisspannung (min) | Tensión del enlace CC PCS (min) | Pcs DC Link Napięcie (min) | Phase Compensation DC Link Voltage | V | V | Minimum | Double | 10 minute tag
WCNV.PhsCmpDclV_10m_Std | #N/A | WCNV. | PhsCmpDclV_10m_Std | PCS DC Link Voltage (std) | Phasenkompensationsstufe Zwischenkreisspannung (std) | Tensión del enlace CC PCS (std) | Pcs DC Link Napięcie (std) | Phase Compensation DC Link Voltage | V | V | Standard Deviation | Double | 10 minute tag
WCNV.PhsCmpExtVArSpt | #N/A | WCNV. | PhsCmpExtVArSpt | PCS external Reactive Power | Phasenkompensationsstufe externe Blindleistung | Potencia reactiva externa PCS | Zewnętrzna moc bierna PCS | Phase Compensation external Reactive Power | VAr | VAr | Setpoint | Double | Live Value
WCNV.PhsCmpExtVArSpt_10m_Avg | #N/A | WCNV. | PhsCmpExtVArSpt_10m_Avg | PCS external Reactive Power (avg) | Phasenkompensationsstufe externe Blindleistung (avg) | Potencia reactiva externa PCS (avg) | Zewnętrzna moc bierna PCS (avg) | Phase Compensation external Reactive Power | VAr | VAr | Average | Double | 10 minute tag
WCNV.PhsCmpExtVArSpt_10m_Max | #N/A | WCNV. | PhsCmpExtVArSpt_10m_Max | PCS external Reactive Power (max) | Phasenkompensationsstufe externe Blindleistung (max) | Potencia reactiva externa PCS (max) | Zewnętrzna moc bierna PCS (max) | Phase Compensation external Reactive Power | VAr | VAr | Maximum | Double | 10 minute tag
WCNV.PhsCmpExtVArSpt_10m_Min | #N/A | WCNV. | PhsCmpExtVArSpt_10m_Min | PCS external Reactive Power (min) | Phasenkompensationsstufe externe Blindleistung (min) | Potencia reactiva externa PCS (min) | Zewnętrzna moc bierna PCS (min) | Phase Compensation external Reactive Power | VAr | VAr | Minimum | Double | 10 minute tag
WCNV.PhsCmpExtVArSpt_10m_Std | #N/A | WCNV. | PhsCmpExtVArSpt_10m_Std | PCS external Reactive Power (std) | Phasenkompensationsstufe externe Blindleistung (std) | Potencia reactiva externa PCS (std) | Zewnętrzna moc bierna PCS (std) | Phase Compensation external Reactive Power | VAr | VAr | Standard Deviation | Double | 10 minute tag
WCNV.PhsCmpFanCnt | #N/A | WCNV. | PhsCmpFanCnt | Number of activations of the phase compensation fan | Anzahl der Aktivierungen des Phasenausgleichslüfters | Número de activaciones del ventilador de compensación de fase | Liczba aktywacji wentylatora kompensacji fazy | Number of activations of the phase compensation fan | count | Count | Total Counter | Long | Live Value
WCNV.PhsCmpFanCnt_10m_End | #N/A | WCNV. | PhsCmpFanCnt_10m_End | Number of activations of the phase compensation fan (end) | Anzahl der Aktivierungen des Phasenausgleichslüfters (end) | Número de activaciones del ventilador de compensación de fase (end) | Liczba aktywacji wentylatora kompensacji fazy (end) | Number of activations of the phase compensation fan | count | Count | Endvalue | Long | 10 minute tag
WCNV.PhsCmpFanTms | #N/A | WCNV. | PhsCmpFanTms | Time phase compensation fan has been activated | Zeit, in der der Phasenausgleichslüfter aktiviert wurde | Tiempo que el ventilador de compensación de fase ha estado activado | Czas aktywacji kompensacji fazowej | Time phase compensation fan has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.PhsCmpFanTms_10m_End | #N/A | WCNV. | PhsCmpFanTms_10m_End | Time phase compensation fan has been activated (end) | Zeit, in der der Phasenausgleichslüfter aktiviert wurde (end) | Tiempo que el ventilador de compensación de fase ha estado activado (end) | Czas aktywacji kompensacji fazowej (end) | Time phase compensation fan has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.PhsCmpHtCnt | #N/A | WCNV. | PhsCmpHtCnt | Number of activations of the phase compensation heat | Anzahl der Aktivierungen der Phasenkompensationswärme | Número de activaciones del calentador de compensación de fase | Liczba aktywacji ogrz. kompensacji fazowej | Number of activations of the phase compensation heat | count | Count | Total Counter | Long | Live Value
WCNV.PhsCmpHtCnt_10m_End | #N/A | WCNV. | PhsCmpHtCnt_10m_End | Number of activations of the phase compensation heat (end) | Anzahl der Aktivierungen der Phasenkompensationswärme (end) | Número de activaciones del calentador de compensación de fase (end) | Liczba aktywacji ogrz. kompensacji fazowej (end) | Number of activations of the phase compensation heat | count | Count | Endvalue | Long | 10 minute tag
WCNV.PhsCmpHtSnkTmp | #N/A | WCNV. | PhsCmpHtSnkTmp | PCS Heat Sink Temperature | Phasenkompensationsstufe Kühlkörpertemperatur | Temperatura del disipador térmico de PCS | Temp radiatora PCS | Phase Compensation Heat Sink Temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.PhsCmpHtSnkTmp_10m_Avg | #N/A | WCNV. | PhsCmpHtSnkTmp_10m_Avg | PCS Heat Sink Temperature (avg) | Phasenkompensationsstufe Kühlkörpertemperatur (avg) | Temperatura del disipador térmico de PCS (avg) | Temp radiatora PCS (avg) | Phase Compensation Heat Sink Temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.PhsCmpHtSnkTmp_10m_Max | #N/A | WCNV. | PhsCmpHtSnkTmp_10m_Max | PCS Heat Sink Temperature (max) | Phasenkompensationsstufe Kühlkörpertemperatur (max) | Temperatura del disipador térmico de PCS (max) | Temp radiatora PCS (max) | Phase Compensation Heat Sink Temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.PhsCmpHtSnkTmp_10m_Min | #N/A | WCNV. | PhsCmpHtSnkTmp_10m_Min | PCS Heat Sink Temperature (min) | Phasenkompensationsstufe Kühlkörpertemperatur (min) | Temperatura del disipador térmico de PCS (min) | Temp radiatora PCS (min) | Phase Compensation Heat Sink Temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.PhsCmpHtSnkTmp_10m_Std | #N/A | WCNV. | PhsCmpHtSnkTmp_10m_Std | PCS Heat Sink Temperature (std) | Phasenkompensationsstufe Kühlkörpertemperatur (std) | Temperatura del disipador térmico de PCS (std) | Temp radiatora PCS (std) | Phase Compensation Heat Sink Temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.PhsCmpHtTms | #N/A | WCNV. | PhsCmpHtTms | Time phase compensation heat has been activated | Zeit, in der die Phasenkompensationswärme aktiviert wurde | Tiempo que el calentador de compensación de fase ha estado activado | Czas aktywacji ogrz. kompensacji fazowej | Time phase compensation heat has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.PhsCmpHtTms_10m_End | #N/A | WCNV. | PhsCmpHtTms_10m_End | Time phase compensation heat has been activated (end) | Zeit, in der die Phasenkompensationswärme aktiviert wurde (end) | Tiempo que el calentador de compensación de fase ha estado activado (end) | Czas aktywacji ogrz. kompensacji fazowej (end) | Time phase compensation heat has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.PhsCmpPFSpt | #N/A | WCNV. | PhsCmpPFSpt | PCS Cos phi Set Point | Phasenkompensationsstufe Cos phi Sollwert | Punto de ajuste de cosphi de PCS | Nastawa PCS Cos phi | Phase Compensation Cos phi Set Point | pf | pf | Setpoint | Double | Live Value
WCNV.PhsCmpPFSpt_10m_Avg | #N/A | WCNV. | PhsCmpPFSpt_10m_Avg | PCS Cos phi Set Point (avg) | Phasenkompensationsstufe Cos phi Sollwert (avg) | Punto de ajuste de cosphi de PCS (avg) | Nastawa PCS Cos phi (avg) | Phase Compensation Cos phi Set Point | pf | pf | Average | Double | 10 minute tag
WCNV.PhsCmpPFSpt_10m_Max | #N/A | WCNV. | PhsCmpPFSpt_10m_Max | PCS Cos phi Set Point (max) | Phasenkompensationsstufe Cos phi Sollwert (max) | Punto de ajuste de cosphi de PCS (max) | Nastawa PCS Cos phi (max) | Phase Compensation Cos phi Set Point | pf | pf | Maximum | Double | 10 minute tag
WCNV.PhsCmpPFSpt_10m_Min | #N/A | WCNV. | PhsCmpPFSpt_10m_Min | PCS Cos phi Set Point (min) | Phasenkompensationsstufe Cos phi Sollwert (min) | Punto de ajuste de cosphi de PCS (min) | Nastawa PCS Cos phi (min) | Phase Compensation Cos phi Set Point | pf | pf | Minimum | Double | 10 minute tag
WCNV.PhsCmpPFSpt_10m_Std | #N/A | WCNV. | PhsCmpPFSpt_10m_Std | PCS Cos phi Set Point (std) | Phasenkompensationsstufe Cos phi Sollwert (std) | Punto de ajuste de cosphi de PCS (std) | Nastawa PCS Cos phi (std) | Phase Compensation Cos phi Set Point | pf | pf | Standard Deviation | Double | 10 minute tag
WCNV.PhsCmpPnlTmp | #N/A | WCNV. | PhsCmpPnlTmp | Phase Compensation Panel Temp | Phasenkompensation Panel Temperatur | Temperatura del panel de compensación de fase | Temp panelu kompensacji fazy | Phase compensation panel temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.PhsCmpPnlTmp_10m_Avg | #N/A | WCNV. | PhsCmpPnlTmp_10m_Avg | Phase Compensation Panel Temp (avg) | Phasenkompensation Panel Temperatur (avg) | Temperatura del panel de compensación de fase (avg) | Temp panelu kompensacji fazy (avg) | Phase compensation panel temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.PhsCmpPnlTmp_10m_Max | #N/A | WCNV. | PhsCmpPnlTmp_10m_Max | Phase Compensation Panel Temp (max) | Phasenkompensation Panel Temperatur (max) | Temperatura del panel de compensación de fase (max) | Temp panelu kompensacji fazy (max) | Phase compensation panel temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.PhsCmpPnlTmp_10m_Min | #N/A | WCNV. | PhsCmpPnlTmp_10m_Min | Phase Compensation Panel Temp (min) | Phasenkompensation Panel Temperatur (min) | Temperatura del panel de compensación de fase (min) | Temp panelu kompensacji fazy (min) | Phase compensation panel temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.PhsCmpPnlTmp_10m_Std | #N/A | WCNV. | PhsCmpPnlTmp_10m_Std | Phase Compensation Panel Temp (std) | Phasenkompensation Panel Temperatur (std) | Temperatura del panel de compensación de fase (std) | Temp panelu kompensacji fazy (std) | Phase compensation panel temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.PhsCmpPnlTmp1 | #N/A | WCNV. | PhsCmpPnlTmp1 | Phase Compensation Panel Temp 1 | Phasenkompensation Panel Temperatur 1 | Temperatura 1 del panel de compensación de fase | Panel kompensacji fazy Temp 1 | Phase compensation panel temperature 1 | deg_c | °C | Live Value | Double | Live Value
WCNV.PhsCmpPnlTmp1_10m_Avg | #N/A | WCNV. | PhsCmpPnlTmp1_10m_Avg | Phase Compensation Panel Temp 1 (avg) | Phasenkompensation Panel Temperatur 1 (avg) | Temperatura 1 del panel de compensación de fase (avg) | Panel kompensacji fazy Temp 1 (avg) | Phase compensation panel temperature 1 | deg_c | °C | Average | Double | 10 minute tag
WCNV.PhsCmpPnlTmp1_10m_Max | #N/A | WCNV. | PhsCmpPnlTmp1_10m_Max | Phase Compensation Panel Temp 1 (max) | Phasenkompensation Panel Temperatur 1 (max) | Temperatura 1 del panel de compensación de fase (max) | Panel kompensacji fazy Temp 1 (max) | Phase compensation panel temperature 1 | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.PhsCmpPnlTmp1_10m_Min | #N/A | WCNV. | PhsCmpPnlTmp1_10m_Min | Phase Compensation Panel Temp 1 (min) | Phasenkompensation Panel Temperatur 1 (min) | Temperatura 1 del panel de compensación de fase (min) | Panel kompensacji fazy Temp 1 (min) | Phase compensation panel temperature 1 | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.PhsCmpPnlTmp1_10m_Std | #N/A | WCNV. | PhsCmpPnlTmp1_10m_Std | Phase Compensation Panel Temp 1 (std) | Phasenkompensation Panel Temperatur 1 (std) | Temperatura 1 del panel de compensación de fase (std) | Panel kompensacji fazy Temp 1 (std) | Phase compensation panel temperature 1 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.PhsCmpPnlTmp2 | #N/A | WCNV. | PhsCmpPnlTmp2 | Phase Compensation Panel Temp 2 | Phasenkompensation Panel Temperatur 2 | Temperatura 2 del panel de compensación de fase | Panel kompensacji fazy Temp 2 | Phase compensation panel temperature 2 | deg_c | °C | Live Value | Double | Live Value
WCNV.PhsCmpPnlTmp2_10m_Avg | #N/A | WCNV. | PhsCmpPnlTmp2_10m_Avg | Phase Compensation Panel Temp 2 (avg) | Phasenkompensation Panel Temperatur 2 (avg) | Temperatura 2 del panel de compensación de fase (avg) | Panel kompensacji fazy Temp 2 (avg) | Phase compensation panel temperature 2 | deg_c | °C | Average | Double | 10 minute tag
WCNV.PhsCmpPnlTmp2_10m_Max | #N/A | WCNV. | PhsCmpPnlTmp2_10m_Max | Phase Compensation Panel Temp 2 (max) | Phasenkompensation Panel Temperatur 2 (max) | Temperatura 2 del panel de compensación de fase (max) | Panel kompensacji fazy Temp 2 (max) | Phase compensation panel temperature 2 | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.PhsCmpPnlTmp2_10m_Min | #N/A | WCNV. | PhsCmpPnlTmp2_10m_Min | Phase Compensation Panel Temp 2 (min) | Phasenkompensation Panel Temperatur 2 (min) | Temperatura 2 del panel de compensación de fase (min) | Panel kompensacji fazy Temp 2 (min) | Phase compensation panel temperature 2 | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.PhsCmpPnlTmp2_10m_Std | #N/A | WCNV. | PhsCmpPnlTmp2_10m_Std | Phase Compensation Panel Temp 2 (std) | Phasenkompensation Panel Temperatur 2 (std) | Temperatura 2 del panel de compensación de fase (std) | Panel kompensacji fazy Temp 2 (std) | Phase compensation panel temperature 2 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.PhsCmpPnlTmp3 | #N/A | WCNV. | PhsCmpPnlTmp3 | Phase Compensation Panel Temp 3 | Phasenkompensation Panel Temperatur 3 | Temperatura 3 del panel de compensación de fase | Panel kompensacji fazy Temp 3 | Phase compensation panel temperature 3 | deg_c | °C | Live Value | Double | Live Value
WCNV.PhsCmpPnlTmp3_10m_Avg | #N/A | WCNV. | PhsCmpPnlTmp3_10m_Avg | Phase Compensation Panel Temp 3 (avg) | Phasenkompensation Panel Temperatur 3 (avg) | Temperatura 3 del panel de compensación de fase (avg) | Panel kompensacji fazy Temp 3 (avg) | Phase compensation panel temperature 3 | deg_c | °C | Average | Double | 10 minute tag
WCNV.PhsCmpPnlTmp3_10m_Max | #N/A | WCNV. | PhsCmpPnlTmp3_10m_Max | Phase Compensation Panel Temp 3 (max) | Phasenkompensation Panel Temperatur 3 (max) | Temperatura 3 del panel de compensación de fase (max) | Panel kompensacji fazy Temp 3 (max) | Phase compensation panel temperature 3 | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.PhsCmpPnlTmp3_10m_Min | #N/A | WCNV. | PhsCmpPnlTmp3_10m_Min | Phase Compensation Panel Temp 3 (min) | Phasenkompensation Panel Temperatur 3 (min) | Temperatura 3 del panel de compensación de fase (min) | Panel kompensacji fazy Temp 3 (min) | Phase compensation panel temperature 3 | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.PhsCmpPnlTmp3_10m_Std | #N/A | WCNV. | PhsCmpPnlTmp3_10m_Std | Phase Compensation Panel Temp 3 (std) | Phasenkompensation Panel Temperatur 3 (std) | Temperatura 3 del panel de compensación de fase (std) | Panel kompensacji fazy Temp 3 (std) | Phase compensation panel temperature 3 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.PhsCmpPnlTmp4 | #N/A | WCNV. | PhsCmpPnlTmp4 | Phase Compensation Panel Temp 4 | Phasenkompensation Panel Temperatur 4 | Temperatura 4 del panel de compensación de fase | Panel kompensacji fazy Temp 4 | Phase compensation panel temperature 4 | deg_c | °C | Live Value | Double | Live Value
WCNV.PhsCmpPnlTmp4_10m_Avg | #N/A | WCNV. | PhsCmpPnlTmp4_10m_Avg | Phase Compensation Panel Temp 4 (avg) | Phasenkompensation Panel Temperatur 4 (avg) | Temperatura 4 del panel de compensación de fase (avg) | Panel kompensacji fazy Temp 4 (avg) | Phase compensation panel temperature 4 | deg_c | °C | Average | Double | 10 minute tag
WCNV.PhsCmpPnlTmp4_10m_Max | #N/A | WCNV. | PhsCmpPnlTmp4_10m_Max | Phase Compensation Panel Temp 4 (max) | Phasenkompensation Panel Temperatur 4 (max) | Temperatura 4 del panel de compensación de fase (max) | Panel kompensacji fazy Temp 4 (max) | Phase compensation panel temperature 4 | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.PhsCmpPnlTmp4_10m_Min | #N/A | WCNV. | PhsCmpPnlTmp4_10m_Min | Phase Compensation Panel Temp 4 (min) | Phasenkompensation Panel Temperatur 4 (min) | Temperatura 4 del panel de compensación de fase (min) | Panel kompensacji fazy Temp 4 (min) | Phase compensation panel temperature 4 | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.PhsCmpPnlTmp4_10m_Std | #N/A | WCNV. | PhsCmpPnlTmp4_10m_Std | Phase Compensation Panel Temp 4 (std) | Phasenkompensation Panel Temperatur 4 (std) | Temperatura 4 del panel de compensación de fase (std) | Panel kompensacji fazy Temp 4 (std) | Phase compensation panel temperature 4 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.PhsCmpPnlTmp5 | #N/A | WCNV. | PhsCmpPnlTmp5 | Phase Compensation Panel Temp 5 | Phasenkompensation Panel Temperatur 5 | Temperatura 5 del panel de compensación de fase | Panel kompensacji fazy Temp 5 | Phase compensation panel temperature 5 | deg_c | °C | Live Value | Double | Live Value
WCNV.PhsCmpPnlTmp5_10m_Avg | #N/A | WCNV. | PhsCmpPnlTmp5_10m_Avg | Phase Compensation Panel Temp 5 (avg) | Phasenkompensation Panel Temperatur 5 (avg) | Temperatura 5 del panel de compensación de fase (avg) | Panel kompensacji fazy Temp 5 (avg) | Phase compensation panel temperature 5 | deg_c | °C | Average | Double | 10 minute tag
WCNV.PhsCmpPnlTmp5_10m_Max | #N/A | WCNV. | PhsCmpPnlTmp5_10m_Max | Phase Compensation Panel Temp 5 (max) | Phasenkompensation Panel Temperatur 5 (max) | Temperatura 5 del panel de compensación de fase (max) | Panel kompensacji fazy Temp 5 (max) | Phase compensation panel temperature 5 | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.PhsCmpPnlTmp5_10m_Min | #N/A | WCNV. | PhsCmpPnlTmp5_10m_Min | Phase Compensation Panel Temp 5 (min) | Phasenkompensation Panel Temperatur 5 (min) | Temperatura 5 del panel de compensación de fase (min) | Panel kompensacji fazy Temp 5 (min) | Phase compensation panel temperature 5 | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.PhsCmpPnlTmp5_10m_Std | #N/A | WCNV. | PhsCmpPnlTmp5_10m_Std | Phase Compensation Panel Temp 5 (std) | Phasenkompensation Panel Temperatur 5 (std) | Temperatura 5 del panel de compensación de fase (std) | Panel kompensacji fazy Temp 5 (std) | Phase compensation panel temperature 5 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.PhsCmpSt | #N/A | WCNV. | PhsCmpSt | PCS State | Status der Phasenkompensationsstufe | Estado de PCS | Stan PCS | Phase Compensation State | Enum | Enum | Live Value | Double | Live Value
WCNV.PhsCmpSt_10m_Avg | #N/A | WCNV. | PhsCmpSt_10m_Avg | PCS State (avg) | Status der Phasenkompensationsstufe (avg) | Estado de PCS (avg) | Stan PCS (avg) | Phase Compensation State | Enum | Enum | Average | Double | 10 minute tag
WCNV.PhsCmpSt_10m_Max | #N/A | WCNV. | PhsCmpSt_10m_Max | PCS State (max) | Status der Phasenkompensationsstufe (max) | Estado de PCS (max) | Stan PCS (max) | Phase Compensation State | Enum | Enum | Maximum | Double | 10 minute tag
WCNV.PhsCmpSt_10m_Min | #N/A | WCNV. | PhsCmpSt_10m_Min | PCS State (min) | Status der Phasenkompensationsstufe (min) | Estado de PCS (min) | Stan PCS (min) | Phase Compensation State | Enum | Enum | Minimum | Double | 10 minute tag
WCNV.PhsCmpSt_10m_Std | #N/A | WCNV. | PhsCmpSt_10m_Std | PCS State (std) | Status der Phasenkompensationsstufe (std) | Estado de PCS (std) | Stan PCS (std) | Phase Compensation State | Enum | Enum | Standard Deviation | Double | 10 minute tag
WCNV.PhsCmpTms1 | #N/A | WCNV. | PhsCmpTms1 | Time phase compensation 1 has been activated | Zeitphasenkompensation 1 wurde aktiviert | Tiempo que la compensación de fase 1 ha estado activada | Czas aktywacji kompensacji fazy 1 | Time phase compensation 1 has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.PhsCmpTms1_10m_End | #N/A | WCNV. | PhsCmpTms1_10m_End | Time phase compensation 1 has been activated (end) | Zeitphasenkompensation 1 wurde aktiviert (end) | Tiempo que la compensación de fase 1 ha estado activada (end) | Czas aktywacji kompensacji fazy 1 (end) | Time phase compensation 1 has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.PhsCmpTms10 | #N/A | WCNV. | PhsCmpTms10 | Time phase compensation 10 has been activated | Zeitphasenkompensation 10 wurde aktiviert | Tiempo que la compensación de fase 10 ha estado activada | Czas aktywacji kompensacji fazy 10 | Time phase compensation 10 has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.PhsCmpTms10_10m_End | #N/A | WCNV. | PhsCmpTms10_10m_End | Time phase compensation 10 has been activated (end) | Zeitphasenkompensation 10 wurde aktiviert (end) | Tiempo que la compensación de fase 10 ha estado activada (end) | Czas aktywacji kompensacji fazy 10 (end) | Time phase compensation 10 has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.PhsCmpTms2 | #N/A | WCNV. | PhsCmpTms2 | Time phase compensation 2 has been activated | Zeitphasenkompensation 2 wurde aktiviert | Tiempo que la compensación de fase 2 ha estado activada | Czas aktywacji kompensacji fazy 2 | Time phase compensation 2 has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.PhsCmpTms2_10m_End | #N/A | WCNV. | PhsCmpTms2_10m_End | Time phase compensation 2 has been activated (end) | Zeitphasenkompensation 2 wurde aktiviert (end) | Tiempo que la compensación de fase 2 ha estado activada (end) | Czas aktywacji kompensacji fazy 2 (end) | Time phase compensation 2 has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.PhsCmpTms3 | #N/A | WCNV. | PhsCmpTms3 | Time phase compensation 3 has been activated | Zeitphasenkompensation 3 wurde aktiviert | Tiempo que la compensación de fase 3 ha estado activada | Czas aktywacji kompensacji fazy 3 | Time phase compensation 3 has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.PhsCmpTms3_10m_End | #N/A | WCNV. | PhsCmpTms3_10m_End | Time phase compensation 3 has been activated (end) | Zeitphasenkompensation 3 wurde aktiviert (end) | Tiempo que la compensación de fase 3 ha estado activada (end) | Czas aktywacji kompensacji fazy 3 (end) | Time phase compensation 3 has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.PhsCmpTms4 | #N/A | WCNV. | PhsCmpTms4 | Time phase compensation 4 has been activated | Zeitphasenkompensation 4 wurde aktiviert | Tiempo que la compensación de fase 4 ha estado activada | Czas aktywacji kompensacji fazy 4 | Time phase compensation 4 has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.PhsCmpTms4_10m_End | #N/A | WCNV. | PhsCmpTms4_10m_End | Time phase compensation 4 has been activated (end) | Zeitphasenkompensation 4 wurde aktiviert (end) | Tiempo que la compensación de fase 4 ha estado activada (end) | Czas aktywacji kompensacji fazy 4 (end) | Time phase compensation 4 has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.PhsCmpTms5 | #N/A | WCNV. | PhsCmpTms5 | Time phase compensation 5 has been activated | Zeitphasenkompensation 5 wurde aktiviert | Tiempo que la compensación de fase 5 ha estado activada | Czas aktywacji kompensacji fazy 5 | Time phase compensation 5 has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.PhsCmpTms5_10m_End | #N/A | WCNV. | PhsCmpTms5_10m_End | Time phase compensation 5 has been activated (end) | Zeitphasenkompensation 5 wurde aktiviert (end) | Tiempo que la compensación de fase 5 ha estado activada (end) | Czas aktywacji kompensacji fazy 5 (end) | Time phase compensation 5 has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.PhsCmpTms6 | #N/A | WCNV. | PhsCmpTms6 | Time phase compensation 6 has been activated | Zeitphasenkompensation 6 wurde aktiviert | Tiempo que la compensación de fase 6 ha estado activada | Czas aktywacji kompensacji fazy 6 | Time phase compensation 6 has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.PhsCmpTms6_10m_End | #N/A | WCNV. | PhsCmpTms6_10m_End | Time phase compensation 6 has been activated (end) | Zeitphasenkompensation 6 wurde aktiviert (end) | Tiempo que la compensación de fase 6 ha estado activada (end) | Czas aktywacji kompensacji fazy 6 (end) | Time phase compensation 6 has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.PhsCmpTms7 | #N/A | WCNV. | PhsCmpTms7 | Time phase compensation 7 has been activated | Zeitphasenkompensation 7 wurde aktiviert | Tiempo que la compensación de fase 7 ha estado activada | Czas aktywacji kompensacji fazy 7 | Time phase compensation 7 has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.PhsCmpTms7_10m_End | #N/A | WCNV. | PhsCmpTms7_10m_End | Time phase compensation 7 has been activated (end) | Zeitphasenkompensation 7 wurde aktiviert (end) | Tiempo que la compensación de fase 7 ha estado activada (end) | Czas aktywacji kompensacji fazy 7 (end) | Time phase compensation 7 has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.PhsCmpTms8 | #N/A | WCNV. | PhsCmpTms8 | Time phase compensation 8 has been activated | Zeitphasenkompensation 8 wurde aktiviert | Tiempo que la compensación de fase 8 ha estado activada | Czas aktywacji kompensacji fazy 8 | Time phase compensation 8 has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.PhsCmpTms8_10m_End | #N/A | WCNV. | PhsCmpTms8_10m_End | Time phase compensation 8 has been activated (end) | Zeitphasenkompensation 8 wurde aktiviert (end) | Tiempo que la compensación de fase 8 ha estado activada (end) | Czas aktywacji kompensacji fazy 8 (end) | Time phase compensation 8 has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.PhsCmpTms9 | #N/A | WCNV. | PhsCmpTms9 | Time phase compensation 9 has been activated | Zeitphasenkompensation 9 wurde aktiviert | Tiempo que la compensación de fase 9 ha estado activada | Czas aktywacji kompensacji fazy 9 | Time phase compensation 9 has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.PhsCmpTms9_10m_End | #N/A | WCNV. | PhsCmpTms9_10m_End | Time phase compensation 9 has been activated (end) | Zeitphasenkompensation 9 wurde aktiviert (end) | Tiempo que la compensación de fase 9 ha estado activada (end) | Czas aktywacji kompensacji fazy 9 (end) | Time phase compensation 9 has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.PhsCmpV | #N/A | WCNV. | PhsCmpV | PCS Mains Voltage | Phasenkompensationsstufe Netzspannung | Tensión de red de PCS | Napięcie sieciowe PCS | Phase Compensation Mains Voltage | V | V | Live Value | Double | Live Value
WCNV.PhsCmpV_10m_Avg | #N/A | WCNV. | PhsCmpV_10m_Avg | PCS Mains Voltage (avg) | Phasenkompensationsstufe Netzspannung (avg) | Tensión de red de PCS (avg) | Napięcie sieciowe PCS (avg) | Phase Compensation Mains Voltage | V | V | Average | Double | 10 minute tag
WCNV.PhsCmpV_10m_Max | #N/A | WCNV. | PhsCmpV_10m_Max | PCS Mains Voltage (max) | Phasenkompensationsstufe Netzspannung (max) | Tensión de red de PCS (max) | Napięcie sieciowe PCS (max) | Phase Compensation Mains Voltage | V | V | Maximum | Double | 10 minute tag
WCNV.PhsCmpV_10m_Min | #N/A | WCNV. | PhsCmpV_10m_Min | PCS Mains Voltage (min) | Phasenkompensationsstufe Netzspannung (min) | Tensión de red de PCS (min) | Napięcie sieciowe PCS (min) | Phase Compensation Mains Voltage | V | V | Minimum | Double | 10 minute tag
WCNV.PhsCmpV_10m_Std | #N/A | WCNV. | PhsCmpV_10m_Std | PCS Mains Voltage (std) | Phasenkompensationsstufe Netzspannung (std) | Tensión de red de PCS (std) | Napięcie sieciowe PCS (std) | Phase Compensation Mains Voltage | V | V | Standard Deviation | Double | 10 minute tag
WCNV.PhsCmpVAr | #N/A | WCNV. | PhsCmpVAr | PCS Reactive power | Phasenkompensationsstufe Blindleistung | Potencia reactiva de PCS | Moc bierna PCS | Phase Compensation Reactive power | VAr | VAr | Live Value | Double | Live Value
WCNV.PhsCmpVAr_10m_Avg | #N/A | WCNV. | PhsCmpVAr_10m_Avg | PCS Reactive power (avg) | Phasenkompensationsstufe Blindleistung (avg) | Potencia reactiva de PCS (avg) | Moc bierna PCS (avg) | Phase Compensation Reactive power | VAr | VAr | Average | Double | 10 minute tag
WCNV.PhsCmpVAr_10m_Max | #N/A | WCNV. | PhsCmpVAr_10m_Max | PCS Reactive power (max) | Phasenkompensationsstufe Blindleistung (max) | Potencia reactiva de PCS (max) | Moc bierna PCS (max) | Phase Compensation Reactive power | VAr | VAr | Maximum | Double | 10 minute tag
WCNV.PhsCmpVAr_10m_Min | #N/A | WCNV. | PhsCmpVAr_10m_Min | PCS Reactive power (min) | Phasenkompensationsstufe Blindleistung (min) | Potencia reactiva de PCS (min) | Moc bierna PCS (min) | Phase Compensation Reactive power | VAr | VAr | Minimum | Double | 10 minute tag
WCNV.PhsCmpVAr_10m_Std | #N/A | WCNV. | PhsCmpVAr_10m_Std | PCS Reactive power (std) | Phasenkompensationsstufe Blindleistung (std) | Potencia reactiva de PCS (std) | Moc bierna PCS (std) | Phase Compensation Reactive power | VAr | VAr | Standard Deviation | Double | 10 minute tag
WCNV.PhsCmpVArSpt | #N/A | WCNV. | PhsCmpVArSpt | PCS Reactive Power Set Point | Phasenkompensationsstufe Blindleistungssollwert | Punto de ajuste de la potencia reactiva de PCS | Nastawa mocy biernej PCS | Phase Compensation Reactive Power Set Point | VAr | VAr | Setpoint | Double | Live Value
WCNV.PhsCmpVArSpt_10m_Avg | #N/A | WCNV. | PhsCmpVArSpt_10m_Avg | PCS Reactive Power Set Point (avg) | Phasenkompensationsstufe Blindleistungssollwert (avg) | Punto de ajuste de la potencia reactiva de PCS (avg) | Nastawa mocy biernej PCS (avg) | Phase Compensation Reactive Power Set Point | VAr | VAr | Average | Double | 10 minute tag
WCNV.PhsCmpVArSpt_10m_Max | #N/A | WCNV. | PhsCmpVArSpt_10m_Max | PCS Reactive Power Set Point (max) | Phasenkompensationsstufe Blindleistungssollwert (max) | Punto de ajuste de la potencia reactiva de PCS (max) | Nastawa mocy biernej PCS (max) | Phase Compensation Reactive Power Set Point | VAr | VAr | Maximum | Double | 10 minute tag
WCNV.PhsCmpVArSpt_10m_Min | #N/A | WCNV. | PhsCmpVArSpt_10m_Min | PCS Reactive Power Set Point (min) | Phasenkompensationsstufe Blindleistungssollwert (min) | Punto de ajuste de la potencia reactiva de PCS (min) | Nastawa mocy biernej PCS (min) | Phase Compensation Reactive Power Set Point | VAr | VAr | Minimum | Double | 10 minute tag
WCNV.PhsCmpVArSpt_10m_Std | #N/A | WCNV. | PhsCmpVArSpt_10m_Std | PCS Reactive Power Set Point (std) | Phasenkompensationsstufe Blindleistungssollwert (std) | Punto de ajuste de la potencia reactiva de PCS (std) | Nastawa mocy biernej PCS (std) | Phase Compensation Reactive Power Set Point | VAr | VAr | Standard Deviation | Double | 10 minute tag
WCNV.ReactTmp1_10m_Avg | #N/A | WCNV. | ReactTmp1_10m_Avg | Converter Reactor L1 Temp (avg) | Konverter Reaktor L1 Temperatur (avg) | Temperatura L1 del reactor del convertidor (avg) | Konwerter Reaktor L1 Temp (avg) | Converter reactor temperature phase L1 | deg_c | °C | Average | Double | 10 minute tag
WCNV.ReactTmp1_10m_Max | #N/A | WCNV. | ReactTmp1_10m_Max | Converter Reactor L1 Temp (max) | Konverter Reaktor L1 Temperatur (max) | Temperatura L1 del reactor del convertidor (max) | Konwerter Reaktor L1 Temp (max) | Converter reactor temperature phase L1 | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.ReactTmp1_10m_Min | #N/A | WCNV. | ReactTmp1_10m_Min | Converter Reactor L1 Temp (min) | Konverter Reaktor L1 Temperatur (min) | Temperatura L1 del reactor del convertidor (min) | Konwerter Reaktor L1 Temp (min) | Converter reactor temperature phase L1 | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.ReactTmp1_10m_Std | #N/A | WCNV. | ReactTmp1_10m_Std | Converter Reactor L1 Temp (std) | Konverter Reaktor L1 Temperatur (std) | Temperatura L1 del reactor del convertidor (std) | Konwerter Reaktor L1 Temp (std) | Converter reactor temperature phase L1 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.ReactTmp2_10m_Avg | #N/A | WCNV. | ReactTmp2_10m_Avg | Converter Reactor L2 Temp (avg) | Konverter Reaktor L2 Temperatur (avg) | Temperatura L2 del reactor del convertidor (avg) | Konwerter Reaktor L2 Temp (avg) | Converter reactor temperature phase L2 | deg_c | °C | Average | Double | 10 minute tag
WCNV.ReactTmp2_10m_Max | #N/A | WCNV. | ReactTmp2_10m_Max | Converter Reactor L2 Temp (max) | Konverter Reaktor L2 Temperatur (max) | Temperatura L2 del reactor del convertidor (max) | Konwerter Reaktor L2 Temp (max) | Converter reactor temperature phase L2 | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.ReactTmp2_10m_Min | #N/A | WCNV. | ReactTmp2_10m_Min | Converter Reactor L2 Temp (min) | Konverter Reaktor L2 Temperatur (min) | Temperatura L2 del reactor del convertidor (min) | Konwerter Reaktor L2 Temp (min) | Converter reactor temperature phase L2 | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.ReactTmp2_10m_Std | #N/A | WCNV. | ReactTmp2_10m_Std | Converter Reactor L2 Temp (std) | Konverter Reaktor L2 Temperatur (std) | Temperatura L2 del reactor del convertidor (std) | Konwerter Reaktor L2 Temp (std) | Converter reactor temperature phase L2 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.ReactTmp3_10m_Avg | #N/A | WCNV. | ReactTmp3_10m_Avg | Converter Reactor L3 Temp (avg) | Konverter Reaktor L3 Temperatur (avg) | Temperatura L3 del reactor del convertidor (avg) | Konwerter Reaktor L3 Temp (avg) | Converter reactor temperature phase L3 | deg_c | °C | Average | Double | 10 minute tag
WCNV.ReactTmp3_10m_Max | #N/A | WCNV. | ReactTmp3_10m_Max | Converter Reactor L3 Temp (max) | Konverter Reaktor L3 Temperatur (max) | Temperatura L3 del reactor del convertidor (max) | Konwerter Reaktor L3 Temp (max) | Converter reactor temperature phase L3 | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.ReactTmp3_10m_Min | #N/A | WCNV. | ReactTmp3_10m_Min | Converter Reactor L3 Temp (min) | Konverter Reaktor L3 Temperatur (min) | Temperatura L3 del reactor del convertidor (min) | Konwerter Reaktor L3 Temp (min) | Converter reactor temperature phase L3 | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.ReactTmp3_10m_Std | #N/A | WCNV. | ReactTmp3_10m_Std | Converter Reactor L3 Temp (std) | Konverter Reaktor L3 Temperatur (std) | Temperatura L3 del reactor del convertidor (std) | Konwerter Reaktor L3 Temp (std) | Converter reactor temperature phase L3 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.RectHtSnkTmp1 | #N/A | WCNV. | RectHtSnkTmp1 | Converter Rectifier Heat Sink 1 Temp | Konverter-Gleichrichter Kühlkörper 1 Temperatur | Temperatura del disipador térmico 1 del rectificador del convertidor | Konwerter Radiator prostownika 1 Temp | Converter Rectifier heat sink 1 temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.RectHtSnkTmp1_10m_Avg | #N/A | WCNV. | RectHtSnkTmp1_10m_Avg | Converter Rectifier Heat Sink 1 Temp (avg) | Konverter-Gleichrichter Kühlkörper 1 Temperatur (avg) | Temperatura del disipador térmico 1 del rectificador del convertidor (avg) | Konwerter Radiator prostownika 1 Temp (avg) | Converter Rectifier heat sink 1 temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.RectHtSnkTmp1_10m_Max | #N/A | WCNV. | RectHtSnkTmp1_10m_Max | Converter Rectifier Heat Sink 1 Temp (max) | Konverter-Gleichrichter Kühlkörper 1 Temperatur (max) | Temperatura del disipador térmico 1 del rectificador del convertidor (max) | Konwerter Radiator prostownika 1 Temp (max) | Converter Rectifier heat sink 1 temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.RectHtSnkTmp1_10m_Min | #N/A | WCNV. | RectHtSnkTmp1_10m_Min | Converter Rectifier Heat Sink 1 Temp (min) | Konverter-Gleichrichter Kühlkörper 1 Temperatur (min) | Temperatura del disipador térmico 1 del rectificador del convertidor (min) | Konwerter Radiator prostownika 1 Temp (min) | Converter Rectifier heat sink 1 temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.RectHtSnkTmp1_10m_Std | #N/A | WCNV. | RectHtSnkTmp1_10m_Std | Converter Rectifier Heat Sink 1 Temp (std) | Konverter-Gleichrichter Kühlkörper 1 Temperatur (std) | Temperatura del disipador térmico 1 del rectificador del convertidor (std) | Konwerter Radiator prostownika 1 Temp (std) | Converter Rectifier heat sink 1 temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.RectHtSnkTmp2 | #N/A | WCNV. | RectHtSnkTmp2 | Converter Rectifier Heat Sink 1 Temp | Konverter-Gleichrichter Kühlkörper 1 Temperatur | Temperatura del disipador térmico 1 del rectificador del convertidor | Konwerter Radiator prostownika 1 Temp | Converter Rectifier heat sink 1 temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.RectHtSnkTmp2_10m_Avg | #N/A | WCNV. | RectHtSnkTmp2_10m_Avg | Converter Rectifier Heat Sink 1 Temp (avg) | Konverter-Gleichrichter Kühlkörper 1 Temperatur (avg) | Temperatura del disipador térmico 1 del rectificador del convertidor (avg) | Konwerter Radiator prostownika 1 Temp (avg) | Converter Rectifier heat sink 1 temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.RectHtSnkTmp2_10m_Max | #N/A | WCNV. | RectHtSnkTmp2_10m_Max | Converter Rectifier Heat Sink 1 Temp (max) | Konverter-Gleichrichter Kühlkörper 1 Temperatur (max) | Temperatura del disipador térmico 1 del rectificador del convertidor (max) | Konwerter Radiator prostownika 1 Temp (max) | Converter Rectifier heat sink 1 temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.RectHtSnkTmp2_10m_Min | #N/A | WCNV. | RectHtSnkTmp2_10m_Min | Converter Rectifier Heat Sink 1 Temp (min) | Konverter-Gleichrichter Kühlkörper 1 Temperatur (min) | Temperatura del disipador térmico 1 del rectificador del convertidor (min) | Konwerter Radiator prostownika 1 Temp (min) | Converter Rectifier heat sink 1 temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.RectHtSnkTmp2_10m_Std | #N/A | WCNV. | RectHtSnkTmp2_10m_Std | Converter Rectifier Heat Sink 1 Temp (std) | Konverter-Gleichrichter Kühlkörper 1 Temperatur (std) | Temperatura del disipador térmico 1 del rectificador del convertidor (std) | Konwerter Radiator prostownika 1 Temp (std) | Converter Rectifier heat sink 1 temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.RectPnlTmp | #N/A | WCNV. | RectPnlTmp | Converter Rectifier Panel Temp | Konverter Gleichrichter Panel Temperatur | Temperatura del panel del rectificador del convertidor | Temp panelu prostownika konwertera | Converter Rectifier panel temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.RectPnlTmp_10m_Avg | #N/A | WCNV. | RectPnlTmp_10m_Avg | Converter Rectifier Panel Temp (avg) | Konverter Gleichrichter Panel Temperatur (avg) | Temperatura del panel del rectificador del convertidor (avg) | Temp panelu prostownika konwertera (avg) | Converter Rectifier panel temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.RectPnlTmp_10m_Max | #N/A | WCNV. | RectPnlTmp_10m_Max | Converter Rectifier Panel Temp (max) | Konverter Gleichrichter Panel Temperatur (max) | Temperatura del panel del rectificador del convertidor (max) | Temp panelu prostownika konwertera (max) | Converter Rectifier panel temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.RectPnlTmp_10m_Min | #N/A | WCNV. | RectPnlTmp_10m_Min | Converter Rectifier Panel Temp (min) | Konverter Gleichrichter Panel Temperatur (min) | Temperatura del panel del rectificador del convertidor (min) | Temp panelu prostownika konwertera (min) | Converter Rectifier panel temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.RectPnlTmp_10m_Std | #N/A | WCNV. | RectPnlTmp_10m_Std | Converter Rectifier Panel Temp (std) | Konverter Gleichrichter Panel Temperatur (std) | Temperatura del panel del rectificador del convertidor (std) | Temp panelu prostownika konwertera (std) | Converter Rectifier panel temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.RotA | #N/A | WCNV. | RotA | Converter Rotor Side Current | Konverter rotorseitiger Strom | Corriente del convertidor en el lado del rotor | Konwerter Prąd strona rotora | Converter current rotor side | A | A | Live Value | Double | Live Value
WCNV.RotA_10m_Avg | #N/A | WCNV. | RotA_10m_Avg | Converter Rotor Side Current (avg) | Konverter rotorseitiger Strom (avg) | Corriente del convertidor en el lado del rotor (avg) | Konwerter Prąd strona rotora (avg) | Converter current rotor side | A | A | Average | Double | 10 minute tag
WCNV.RotA_10m_Max | #N/A | WCNV. | RotA_10m_Max | Converter Rotor Side Current (max) | Konverter rotorseitiger Strom (max) | Corriente del convertidor en el lado del rotor (max) | Konwerter Prąd strona rotora (max) | Converter current rotor side | A | A | Maximum | Double | 10 minute tag
WCNV.RotA_10m_Min | #N/A | WCNV. | RotA_10m_Min | Converter Rotor Side Current (min) | Konverter rotorseitiger Strom (min) | Corriente del convertidor en el lado del rotor (min) | Konwerter Prąd strona rotora (min) | Converter current rotor side | A | A | Minimum | Double | 10 minute tag
WCNV.RotA_10m_Std | #N/A | WCNV. | RotA_10m_Std | Converter Rotor Side Current (std) | Konverter rotorseitiger Strom (std) | Corriente del convertidor en el lado del rotor (std) | Konwerter Prąd strona rotora (std) | Converter current rotor side | A | A | Standard Deviation | Double | 10 minute tag
WCNV.RotA1_10m_Avg | #N/A | WCNV. | RotA1_10m_Avg | Converter Rotor Side 1 Current (avg) | Konverter rotorseitiger 1 Strom (avg) | Corriente 1 del convertidor en el lado del rotor (avg) | Konwerter strona rotora 1 prąd (avg) | Converter current rotor side 1 | A | A | Average | Double | 10 minute tag
WCNV.RotA1_10m_Max | #N/A | WCNV. | RotA1_10m_Max | Converter Rotor Side 1 Current (max) | Konverter rotorseitiger 1 Strom (max) | Corriente 1 del convertidor en el lado del rotor (max) | Konwerter strona rotora 1 prąd (max) | Converter current rotor side 1 | A | A | Maximum | Double | 10 minute tag
WCNV.RotA2_10m_Avg | #N/A | WCNV. | RotA2_10m_Avg | Converter Rotor Side 2 Current (avg) | Konverter rotorseitiger 2 Strom (avg) | Corriente 2 del convertidor en el lado del rotor (avg) | Konwerter strona rotora 2 Prąd (avg) | Converter current rotor side 2 | A | A | Average | Double | 10 minute tag
WCNV.RotA2_10m_Max | #N/A | WCNV. | RotA2_10m_Max | Converter Rotor Side 2 Current (max) | Konverter rotorseitiger 2 Strom (max) | Corriente 2 del convertidor en el lado del rotor (max) | Konwerter strona rotora 2 Prąd (max) | Converter current rotor side 2 | A | A | Maximum | Double | 10 minute tag
WCNV.RotA3_10m_Avg | #N/A | WCNV. | RotA3_10m_Avg | Converter Rotor Side 3 Current (avg) | Konverter rotorseitiger 3 Strom (avg) | Corriente 3 del convertidor en el lado del rotor (avg) | Konwerter strona rotora 3 prąd (avg) | Converter current rotor side 3 | A | A | Average | Double | 10 minute tag
WCNV.RotA3_10m_Max | #N/A | WCNV. | RotA3_10m_Max | Converter Rotor Side 3 Current (max) | Konverter rotorseitiger 3 Strom (max) | Corriente 3 del convertidor en el lado del rotor (max) | Konwerter strona rotora 3 prąd (max) | Converter current rotor side 3 | A | A | Maximum | Double | 10 minute tag
WCNV.RotChokTmp | #N/A | WCNV. | RotChokTmp | Converter Rotor Choke Temp | Konverter Rotor Drosseltemperatur | Temperatura del cebador del rotor del convertidor | Konwerter Rotor Dławik Temp | Converter rotor choke temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.RotChokTmp_10m_Avg | #N/A | WCNV. | RotChokTmp_10m_Avg | Converter Rotor Choke Temp (avg) | Konverter Rotor Drosseltemperatur (avg) | Temperatura del cebador del rotor del convertidor (avg) | Konwerter Rotor Dławik Temp (avg) | Converter rotor choke temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.RotChokTmp_10m_Max | #N/A | WCNV. | RotChokTmp_10m_Max | Converter Rotor Choke Temp (max) | Konverter Rotor Drosseltemperatur (max) | Temperatura del cebador del rotor del convertidor (max) | Konwerter Rotor Dławik Temp (max) | Converter rotor choke temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.RotChokTmp_10m_Min | #N/A | WCNV. | RotChokTmp_10m_Min | Converter Rotor Choke Temp (min) | Konverter Rotor Drosseltemperatur (min) | Temperatura del cebador del rotor del convertidor (min) | Konwerter Rotor Dławik Temp (min) | Converter rotor choke temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.RotTmp1 | #N/A | WCNV. | RotTmp1 | Converter Rotor L1 Side Temp | Konverter Rotor L1-seitige Temperatur | Temperatura del convertidor en el lado L1 del rotor | Konwerter Rotor L1 Temp. | Converter temperature L1 , rotor side | deg_c | °C | Live Value | Double | Live Value
WCNV.RotTmp1_10m_Avg | #N/A | WCNV. | RotTmp1_10m_Avg | Converter Rotor L1 Side Temp (avg) | Konverter Rotor L1-seitige Temperatur (avg) | Temperatura del convertidor en el lado L1 del rotor (avg) | Konwerter Rotor L1 Temp (avg) | Converter temperature L1 , rotor side | deg_c | °C | Average | Double | 10 minute tag
WCNV.RotTmp1_10m_Max | #N/A | WCNV. | RotTmp1_10m_Max | Converter Rotor Side 1 Temp (max) | Konverter rotorseitige 1 Temperatur (max) | Temperatura del convertidor en el lado 1 del rotor (max) | Konwerter strona rotora 1 Temp (max) | Converter temperature rotor side 1 | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.RotTmp1_10m_Min | #N/A | WCNV. | RotTmp1_10m_Min | Converter Rotor Side 1 Temp (min) | Konverter rotorseitige 1 Temperatur (min) | Temperatura del convertidor en el lado 1 del rotor (min) | Konwerter strona rotora 1 Temp (min) | Converter temperature rotor side 1 | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.RotTmp2 | #N/A | WCNV. | RotTmp2 | Converter Rotor L2 Side Temp | Konverter Rotor L2-seitige Temperatur | Temperatura del convertidor en el lado L2 del rotor | Konwerter Rotor L2 Temp. | Converter temperature L2 , rotor side | deg_c | °C | Live Value | Double | Live Value
WCNV.RotTmp2_10m_Avg | #N/A | WCNV. | RotTmp2_10m_Avg | Converter Rotor L2 Side Temp (avg) | Konverter Rotor L2-seitige Temperatur (avg) | Temperatura del convertidor en el lado L2 del rotor (avg) | Konwerter Rotor L2 Temp. (avg) | Converter temperature L2 , rotor side | deg_c | °C | Average | Double | 10 minute tag
WCNV.RotTmp2_10m_Max | #N/A | WCNV. | RotTmp2_10m_Max | Converter Rotor Side 2 Temp (max) | Konverter rotorseitige 2 Temperatur (max) | Temperatura del convertidor en el lado 2 del rotor (max) | Konwerter strona rotora 2 Temp (max) | Converter temperature rotor side 2 | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.RotTmp2_10m_Min | #N/A | WCNV. | RotTmp2_10m_Min | Converter Rotor Side 2 Temp (min) | Konverter rotorseitige 2 Temperatur (min) | Temperatura del convertidor en el lado 2 del rotor (min) | Konwerter strona rotora 2 Temp (min) | Converter temperature rotor side 2 | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.RotTmp3 | #N/A | WCNV. | RotTmp3 | Converter Rotor L3 Side Temp | Konverter Rotor L3-seitige Temperatur | Temperatura del convertidor en el lado L3 del rotor | Konwerter Rotor L3 Temp. | Converter temperature L3 , rotor side | deg_c | °C | Live Value | Double | Live Value
WCNV.RotTmp3_10m_Avg | #N/A | WCNV. | RotTmp3_10m_Avg | Converter Rotor L3 Side Temp (avg) | Konverter Rotor L3-seitige Temperatur (avg) | Temperatura del convertidor en el lado L3 del rotor (avg) | Konwerter Rotor L3 Temp. (avg) | Converter temperature L3 , rotor side | deg_c | °C | Average | Double | 10 minute tag
WCNV.RotTmp3_10m_Max | #N/A | WCNV. | RotTmp3_10m_Max | Converter Rotor Side 3 Temp (max) | Konverter rotorseitige 3 Temperatur (max) | Temperatura del convertidor en el lado 3 del rotor (max) | Konwerter strona rotora 3 Temp (max) | Converter temperature rotor side 3 | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.RotTmp3_10m_Min | #N/A | WCNV. | RotTmp3_10m_Min | Converter Rotor Side 3 Temp (min) | Konverter rotorseitige 3 Temperatur (min) | Temperatura del convertidor en el lado 3 del rotor (min) | Konwerter strona rotora 3 Temp (min) | Converter temperature rotor side 3 | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.SttFilPnlTmp | #N/A | WCNV. | SttFilPnlTmp | Stator Filter Panel Temp | Stator Filter Panel Temperatur | Temperatura del panel del filtro del estátor | Temp panelu filtra stojana | Stator filter panel temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.SttFilPnlTmp_10m_Avg | #N/A | WCNV. | SttFilPnlTmp_10m_Avg | Stator Filter Panel Temp (avg) | Stator Filter Panel Temperatur (avg) | Temperatura del panel del filtro del estátor (avg) | Temp panelu filtra stojana (avg) | Stator filter panel temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.SttFilPnlTmp_10m_Max | #N/A | WCNV. | SttFilPnlTmp_10m_Max | Stator Filter Panel Temp (max) | Stator Filter Panel Temperatur (max) | Temperatura del panel del filtro del estátor (max) | Temp panelu filtra stojana (max) | Stator filter panel temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.SttFilPnlTmp_10m_Min | #N/A | WCNV. | SttFilPnlTmp_10m_Min | Stator Filter Panel Temp (min) | Stator Filter Panel Temperatur (min) | Temperatura del panel del filtro del estátor (min) | Temp panelu filtra stojana (min) | Stator filter panel temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.SttFilPnlTmp_10m_Std | #N/A | WCNV. | SttFilPnlTmp_10m_Std | Stator Filter Panel Temp (std) | Stator Filter Panel Temperatur (std) | Temperatura del panel del filtro del estátor (std) | Temp panelu filtra stojana (std) | Stator filter panel temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.SttSynSwTmp | #N/A | WCNV. | SttSynSwTmp | Stator Sync Switch Temp | Stator Synchronisationsschalter Temperatur | Temperatura del interruptor sync del estátor | Temp przełącznika synchronizacji stojana | Stator sync switch temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.SttSynSwTmp_10m_Avg | #N/A | WCNV. | SttSynSwTmp_10m_Avg | Stator Sync Switch Temp (avg) | Stator Synchronisationsschalter Temperatur (avg) | Temperatura del interruptor sync del estátor (avg) | Temp przełącznika synchronizacji stojana (avg) | Stator sync switch temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.SttSynSwTmp_10m_Max | #N/A | WCNV. | SttSynSwTmp_10m_Max | Stator Sync Switch Temp (max) | Stator Synchronisationsschalter Temperatur (max) | Temperatura del interruptor sync del estátor (max) | Temp przełącznika synchronizacji stojana (max) | Stator sync switch temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.SttSynSwTmp_10m_Min | #N/A | WCNV. | SttSynSwTmp_10m_Min | Stator Sync Switch Temp (min) | Stator Synchronisationsschalter Temperatur (min) | Temperatura del interruptor sync del estátor (min) | Temp przełącznika synchronizacji stojana (min) | Stator sync switch temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.SttSynSwTmp_10m_Std | #N/A | WCNV. | SttSynSwTmp_10m_Std | Stator Sync Switch Temp (std) | Stator Synchronisationsschalter Temperatur (std) | Temperatura del interruptor sync del estátor (std) | Temp przełącznika synchronizacji stojana (std) | Stator sync switch temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.ThyrCnt | #N/A | WCNV. | ThyrCnt | Number of activations of the thyristors | Anzahl der Aktivierungen der Thyristoren | Número de activaciones de los tiristores | Liczba aktywacji tyrystory | Number of activations of the thyristors | count | Count | Total Counter | Long | Live Value
WCNV.ThyrCnt_10m_End | #N/A | WCNV. | ThyrCnt_10m_End | Number of activations of the thyristors (end) | Anzahl der Aktivierungen der Thyristoren (end) | Número de activaciones de los tiristores (end) | Liczba aktywacji tyrystory (end) | Number of activations of the thyristors | count | Count | Endvalue | Long | 10 minute tag
WCNV.ThyrFanCnt | #N/A | WCNV. | ThyrFanCnt | Number of activations of the thyristor fan | Anzahl der Aktivierungen des Thyristorlüfters | Número de activaciones del tiristor del ventilador | Liczba aktywacji wentylatora tyrystorowego | Number of activations of the thyristor fan | count | Count | Total Counter | Long | Live Value
WCNV.ThyrFanCnt_10m_End | #N/A | WCNV. | ThyrFanCnt_10m_End | Number of activations of the thyristor fan (end) | Anzahl der Aktivierungen des Thyristorlüfters (end) | Número de activaciones del tiristor del ventilador (end) | Liczba aktywacji wentylatora tyrystorowego (end) | Number of activations of the thyristor fan | count | Count | Endvalue | Long | 10 minute tag
WCNV.ThyrFanTms | #N/A | WCNV. | ThyrFanTms | Time the thyristor fan has been activated | Zeit, in der der Thyristorlüfter aktiviert wurde | Tiempo que el tiristor del ventilador ha estado activado | Czas aktywacji wentylatora tyrystorowego | Time the thyristor fan has been activated | s | seconds | Total Counter | Long | Live Value
WCNV.ThyrFanTms_10m_End | #N/A | WCNV. | ThyrFanTms_10m_End | Time the thyristor fan has been activated (end) | Zeit, in der der Thyristorlüfter aktiviert wurde (end) | Tiempo que el tiristor del ventilador ha estado activado (end) | Czas aktywacji wentylatora tyrystorowego (end) | Time the thyristor fan has been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.ThyrTmp | #N/A | WCNV. | ThyrTmp | Thyrister Temp | Thyristortemperatur | Temperatura del tiristor | Tyrystor Temp | Thyrister temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.ThyrTmp_10m_Avg | #N/A | WCNV. | ThyrTmp_10m_Avg | Thyrister Temp (avg) | Thyristortemperatur (avg) | Temperatura del tiristor (avg) | Tyrystor Temp (avg) | Thyrister temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.ThyrTmp_10m_Max | #N/A | WCNV. | ThyrTmp_10m_Max | Thyrister Temp (max) | Thyristortemperatur (max) | Temperatura del tiristor (max) | Tyrystor Temp (max) | Thyrister temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.ThyrTmp_10m_Min | #N/A | WCNV. | ThyrTmp_10m_Min | Thyrister Temp (min) | Thyristortemperatur (min) | Temperatura del tiristor (min) | Tyrystor Temp (min) | Thyrister temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.ThyrTmp_10m_Std | #N/A | WCNV. | ThyrTmp_10m_Std | Thyrister Temp (std) | Thyristortemperatur (std) | Temperatura del tiristor (std) | Tyrystor Temp (std) | Thyrister temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.ThyrTms | #N/A | WCNV. | ThyrTms | Time the thyristors have been activated | Zeit, in der der Thyristor aktiviert wurden | Tiempo que los tiristores han estado activados | Czas aktywacji tyrystorów | Time the thyristors have been activated | s | seconds | Total Counter | Long | Live Value
WCNV.ThyrTms_10m_End | #N/A | WCNV. | ThyrTms_10m_End | Time the thyristors have been activated (end) | Zeit, in der der Thyristor aktiviert wurden (end) | Tiempo que los tiristores han estado activados (end) | Czas aktywacji tyrystorów (end) | Time the thyristors have been activated | s | seconds | Endvalue | Long | 10 minute tag
WCNV.Torq | WCNV.Torq | WCNV. | Torq | Converter Torque | Konverter Drehmoment | Torsión del convertidor | Moment obrotowy konwertera | Converter Torque | Enum | Enum | Live Value | Double | Live Value
WCNV.Torq_10m_Avg | #N/A | WCNV. | Torq_10m_Avg | Converter Torque (avg) | Konverter Drehmoment (avg) | Torsión del convertidor (avg) | Moment obrotowy konwertera (avg) | Converter Torque | Enum | Enum | Average | Double | 10 minute tag
WCNV.Torq_10m_Max | #N/A | WCNV. | Torq_10m_Max | Converter Torque (max) | Konverter Drehmoment (max) | Torsión del convertidor (max) | Moment obrotowy konwertera (max) | Converter Torque | Enum | Enum | Maximum | Double | 10 minute tag
WCNV.Torq_10m_Min | #N/A | WCNV. | Torq_10m_Min | Converter Torque (min) | Konverter Drehmoment (min) | Torsión del convertidor (min) | Moment obrotowy konwertera (min) | Converter Torque | Enum | Enum | Minimum | Double | 10 minute tag
WCNV.Torq_10m_Std | #N/A | WCNV. | Torq_10m_Std | Converter Torque (std) | Konverter Drehmoment (std) | Torsión del convertidor (std) | Moment obrotowy konwertera (std) | Converter Torque | Enum | Enum | Standard Deviation | Double | 10 minute tag
WCNV.VAr | #N/A | WCNV. | VAr | Converter Reactive power | Konverter Blindleistung | Potencia reactiva del convertidor | Moc bierna konwertera | Converter Reactive power | VAr | VAr | Live Value | Double | Live Value
WCNV.VAr_10m_Avg | #N/A | WCNV. | VAr_10m_Avg | Converter Reactive power (avg) | Konverter Blindleistung (avg) | Potencia reactiva del convertidor (avg) | Moc bierna konwertera (avg) | Converter Reactive power | VAr | VAr | Average | Double | 10 minute tag
WCNV.VAr_10m_Max | #N/A | WCNV. | VAr_10m_Max | Converter Reactive power (max) | Konverter Blindleistung (max) | Potencia reactiva del convertidor (max) | Moc bierna konwertera (max) | Converter Reactive power | VAr | VAr | Maximum | Double | 10 minute tag
WCNV.VAr_10m_Min | #N/A | WCNV. | VAr_10m_Min | Converter Reactive power (min) | Konverter Blindleistung (min) | Potencia reactiva del convertidor (min) | Moc bierna konwertera (min) | Converter Reactive power | VAr | VAr | Minimum | Double | 10 minute tag
WCNV.VAr_10m_Std | #N/A | WCNV. | VAr_10m_Std | Converter Reactive power (std) | Konverter Blindleistung (std) | Potencia reactiva del convertidor (std) | Moc bierna konwertera (std) | Converter Reactive power | VAr | VAr | Standard Deviation | Double | 10 minute tag
WCNV.W | #N/A | WCNV. | W | Converter Active power | Konverter Wirkleistung | Potencia activa del convertidor | Moc czynna konwertera | Converter Active power | W | W | Live Value | Double | Live Value
WCNV.W_10m_Avg | #N/A | WCNV. | W_10m_Avg | Converter Active power (avg) | Konverter Wirkleistung (avg) | Potencia activa del convertidor (avg) | Moc czynna konwertera (avg) | Converter Active power | W | W | Average | Double | 10 minute tag
WCNV.W_10m_Max | #N/A | WCNV. | W_10m_Max | Converter Active power (max) | Konverter Wirkleistung (max) | Potencia activa del convertidor (max) | Moc czynna konwertera (max) | Converter Active power | W | W | Maximum | Double | 10 minute tag
WCNV.W_10m_Min | #N/A | WCNV. | W_10m_Min | Converter Active power (min) | Konverter Wirkleistung (min) | Potencia activa del convertidor (min) | Moc czynna konwertera (min) | Converter Active power | W | W | Minimum | Double | 10 minute tag
WCNV.W_10m_Std | #N/A | WCNV. | W_10m_Std | Converter Active power (std) | Konverter Wirkleistung (std) | Potencia activa del convertidor (std) | Moc czynna konwertera (std) | Converter Active power | W | W | Standard Deviation | Double | 10 minute tag
WGEN.BrgDETmp | #N/A | WGEN. | BrgDETmp | Generator Bearing DE Temp | Generator-Lager DE Temperatur | Temperatura del cojinete DE del generador | Łożysko generatora DE Temp | Generator bearing temperature at the drive end | deg_c | °C | Live Value | Double | Live Value
WGEN.BrgDETmp_10m_Avg | #N/A | WGEN. | BrgDETmp_10m_Avg | Generator Bearing DE Temp (avg) | Generator-Lager DE Temperatur (avg) | Temperatura del cojinete DE del generador (avg) | Łożysko generatora DE Temp (avg) | Generator bearing temperature at the drive end | deg_c | °C | Average | Double | 10 minute tag
WGEN.BrgDETmp_10m_Max | #N/A | WGEN. | BrgDETmp_10m_Max | Generator Bearing DE Temp (max) | Generator-Lager DE Temperatur (max) | Temperatura del cojinete DE del generador (max) | Łożysko generatora DE Temp (max) | Generator bearing temperature at the drive end | deg_c | °C | Maximum | Double | 10 minute tag
WGEN.BrgDETmp_10m_Min | #N/A | WGEN. | BrgDETmp_10m_Min | Generator Bearing DE Temp (min) | Generator-Lager DE Temperatur (min) | Temperatura del cojinete DE del generador (min) | Łożysko generatora DE Temp (min) | Generator bearing temperature at the drive end | deg_c | °C | Minimum | Double | 10 minute tag
WGEN.BrgDETmp_10m_Std | #N/A | WGEN. | BrgDETmp_10m_Std | Generator Bearing DE Temp (std) | Generator-Lager DE Temperatur (std) | Temperatura del cojinete DE del generador (std) | Łożysko generatora DE Temp (std) | Generator bearing temperature at the drive end | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN.BrgNDETmp | #N/A | WGEN. | BrgNDETmp | Generator Bearing NDE Temp | Generator-Lager NDE Temperatur | Temperatura del cojinete NDE del generador | Łożysko generatora NDE Temp | Generator bearing temperature at the non-drive end | deg_c | °C | Live Value | Double | Live Value
WGEN.BrgNDETmp_10m_Avg | #N/A | WGEN. | BrgNDETmp_10m_Avg | Generator Bearing NDE Temp (avg) | Generator-Lager NDE Temperatur (avg) | Temperatura del cojinete NDE del generador (avg) | Łożysko generatora NDE Temp (avg) | Generator bearing temperature at the non-drive end | deg_c | °C | Average | Double | 10 minute tag
WGEN.BrgNDETmp_10m_Max | #N/A | WGEN. | BrgNDETmp_10m_Max | Generator Bearing NDE Temp (max) | Generator-Lager NDE Temperatur (max) | Temperatura del cojinete NDE del generador (max) | Łożysko generatora NDE Temp (max) | Generator bearing temperature at the non-drive end | deg_c | °C | Maximum | Double | 10 minute tag
WGEN.BrgNDETmp_10m_Min | #N/A | WGEN. | BrgNDETmp_10m_Min | Generator Bearing NDE Temp (min) | Generator-Lager NDE Temperatur (min) | Temperatura del cojinete NDE del generador (min) | Łożysko generatora NDE Temp (min) | Generator bearing temperature at the non-drive end | deg_c | °C | Minimum | Double | 10 minute tag
WGEN.BrgNDETmp_10m_Std | #N/A | WGEN. | BrgNDETmp_10m_Std | Generator Bearing NDE Temp (std) | Generator-Lager NDE Temperatur (std) | Temperatura del cojinete NDE del generador (std) | Łożysko generatora NDE Temp (std) | Generator bearing temperature at the non-drive end | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN.BrgTmp1 | #N/A | WGEN. | BrgTmp1 | Generator Bearing 1 Temp | Generator-Lager 1 Temperatur | Temperatura del cojinete 1 del generador | Łożysko generatora 1 Temp | Generator bearing temperature 1 | deg_c | °C | Live Value | Double | Live Value | Used in some specialised presentations
WGEN.BrgTmp1_10m_Avg | #N/A | WGEN. | BrgTmp1_10m_Avg | Generator Bearing 1 Temp (avg) | Generator-Lager 1 Temperatur (avg) | Temperatura del cojinete 1 del generador (avg) | Łożysko generatora 1 Temp (avg) | Generator bearing temperature 1 | deg_c | °C | Average | Double | 10 minute tag | Common tags for analysis
WGEN.BrgTmp1_10m_Max | #N/A | WGEN. | BrgTmp1_10m_Max | Generator Bearing 1 Temp (max) | Generator-Lager 1 Temperatur (max) | Temperatura del cojinete 1 del generador (max) | Łożysko generatora 1 Temp (max) | Generator bearing temperature 1 | deg_c | °C | Maximum | Double | 10 minute tag | Common tags for analysis
WGEN.BrgTmp1_10m_Min | #N/A | WGEN. | BrgTmp1_10m_Min | Generator Bearing 1 Temp (min) | Generator-Lager 1 Temperatur (min) | Temperatura del cojinete 1 del generador (min) | Łożysko generatora 1 Temp (min) | Generator bearing temperature 1 | deg_c | °C | Minimum | Double | 10 minute tag | Common tags for analysis
WGEN.BrgTmp1_10m_Std | #N/A | WGEN. | BrgTmp1_10m_Std | Generator Bearing 1 Temp (std) | Generator-Lager 1 Temperatur (std) | Temperatura del cojinete 1 del generador (std) | Łożysko generatora 1 Temp (std) | Generator bearing temperature 1 | deg_c | °C | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WGEN.BrgTmp2 | #N/A | WGEN. | BrgTmp2 | Generator Bearing 2 Temp | Generator-Lager 2 Temperatur | Temperatura del cojinete 2 del generador | Łożysko generatora 2 Temp | Generator bearing temperature 2 | deg_c | °C | Live Value | Double | Live Value | Used in some specialised presentations
WGEN.BrgTmp2_10m_Avg | #N/A | WGEN. | BrgTmp2_10m_Avg | Generator Bearing 2 Temp (avg) | Generator-Lager 2 Temperatur (avg) | Temperatura del cojinete 2 del generador (avg) | Łożysko generatora 2 Temp (avg) | Generator bearing temperature 2 | deg_c | °C | Average | Double | 10 minute tag | Common tags for analysis
WGEN.BrgTmp2_10m_Max | #N/A | WGEN. | BrgTmp2_10m_Max | Generator Bearing 2 Temp (max) | Generator-Lager 2 Temperatur (max) | Temperatura del cojinete 2 del generador (max) | Łożysko generatora 2 Temp (max) | Generator bearing temperature 2 | deg_c | °C | Maximum | Double | 10 minute tag | Common tags for analysis
WGEN.BrgTmp2_10m_Min | #N/A | WGEN. | BrgTmp2_10m_Min | Generator Bearing 2 Temp (min) | Generator-Lager 2 Temperatur (min) | Temperatura del cojinete 2 del generador (min) | Łożysko generatora 2 Temp (min) | Generator bearing temperature 2 | deg_c | °C | Minimum | Double | 10 minute tag | Common tags for analysis
WGEN.BrgTmp2_10m_Std | #N/A | WGEN. | BrgTmp2_10m_Std | Generator Bearing 2 Temp (std) | Generator-Lager 2 Temperatur (std) | Temperatura del cojinete 2 del generador (std) | Łożysko generatora 2 Temp (std) | Generator bearing temperature 2 | deg_c | °C | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WGEN.CabTmp | #N/A | WGEN. | CabTmp | Generator Cable Temp | Kabeltemperatur des Generators | Temperatura del cable del generador | Temp generatora | Generator cable temperature | deg_c | °C | Live Value | Double | Live Value
WGEN.CabTmp_10m_Avg | #N/A | WGEN. | CabTmp_10m_Avg | Generator Cable Temp (avg) | Kabeltemperatur des Generators (avg) | Temperatura del cable del generador (avg) | Temp generatora (avg) | Generator cable temperature | deg_c | °C | Average | Double | 10 minute tag
WGEN.CabTmp_10m_Max | #N/A | WGEN. | CabTmp_10m_Max | Generator Cable Temp (max) | Kabeltemperatur des Generators (max) | Temperatura del cable del generador (max) | Temp generatora (max) | Generator cable temperature | deg_c | °C | Maximum | Double | 10 minute tag
WGEN.CabTmp_10m_Min | #N/A | WGEN. | CabTmp_10m_Min | Generator Cable Temp (min) | Kabeltemperatur des Generators (min) | Temperatura del cable del generador (min) | Temp generatora (min) | Generator cable temperature | deg_c | °C | Minimum | Double | 10 minute tag
WGEN.CabTmp_10m_Std | #N/A | WGEN. | CabTmp_10m_Std | Generator Cable Temp (std) | Kabeltemperatur des Generators (std) | Temperatura del cable del generador (std) | Temp generatora (std) | Generator cable temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN.ClAirTmp | #N/A | WGEN. | ClAirTmp | Generator Cooling Air Temp | Kühllufttemperatur des Generators | Temperatura del aire de refrigeración del generador | Generator Pow. chodz. Temp | Generator cooling air temperature | deg_c | °C | Live Value | Double | Live Value
WGEN.ClAirTmp_10m_Avg | #N/A | WGEN. | ClAirTmp_10m_Avg | Generator Cooling Air Temp (avg) | Kühllufttemperatur des Generators (avg) | Temperatura del aire de refrigeración del generador (avg) | Generator Pow. chodz. Temp (avg) | Generator cooling air temperature | deg_c | °C | Average | Double | 10 minute tag
WGEN.ClAirTmp_10m_Max | #N/A | WGEN. | ClAirTmp_10m_Max | Generator Cooling Air Temp (max) | Kühllufttemperatur des Generators (max) | Temperatura del aire de refrigeración del generador (max) | Generator Pow. chodz. Temp (max) | Generator cooling air temperature | deg_c | °C | Maximum | Double | 10 minute tag
WGEN.ClAirTmp_10m_Min | #N/A | WGEN. | ClAirTmp_10m_Min | Generator Cooling Air Temp (min) | Kühllufttemperatur des Generators (min) | Temperatura del aire de refrigeración del generador (min) | Generator Pow. chodz. Temp (min) | Generator cooling air temperature | deg_c | °C | Minimum | Double | 10 minute tag
WGEN.ClAirTmp_10m_Std | #N/A | WGEN. | ClAirTmp_10m_Std | Generator Cooling Air Temp (std) | Kühllufttemperatur des Generators (std) | Temperatura del aire de refrigeración del generador (std) | Generator Pow. chodz. Temp (std) | Generator cooling air temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN.ClSt | WGEN.ClSt | WGEN. | ClSt | Generator Cooling system Status | Status des Generatorkühlsystems | Estado del sistema de refrigeración del generador | Stan systemu chłodzenia generatora | Status of generator cooling system | Enum | Enum | Live Value | Long | Live Value
WGEN.ClWtrFanOp | #N/A | WGEN. | ClWtrFanOp | Start fans Generator Cooling water | Start Lüfter des Generatorkühlwassers | Iniciar ventiladores de agua de refrigeración del generador | Start went. Generator Woda chłodząca | Start fans GEN (Cooling water) | Enum | Enum | Live Value | Long | Live Value
WGEN.ClWtrFanSpd | #N/A | WGEN. | ClWtrFanSpd | Speed fan Generator Cooling water | Drehzahl Lüfter des Generatorkühlwassers | Velocidad del ventilador de agua de refrigeración del generador | Prędkość wentylatora Generator Woda chłodząca | Speed fans GEN (Cooling water) | rpm | RPM | Live Value | Double | Live Value
WGEN.ClWtrFanSt1 | #N/A | WGEN. | ClWtrFanSt1 | Running fan 1 Generator Cooling water | Laufendes Gebläse 1 Generator Kühlwasser | Ventilador 1 de agua de refrigeración del generador funcionando | Wentylator aktywny 1 Generator Woda chłodząca | Running fan 1 GEN (Cooling water) | Enum | Enum | Live Value | Long | Live Value
WGEN.ClWtrFanSt2 | #N/A | WGEN. | ClWtrFanSt2 | Running fan 2 Generator Cooling water | Laufendes Gebläse 2 Generator Kühlwasser | Ventilador 2 de agua de refrigeración del generador funcionando | Wentylator aktywny 2 Generator Woda chłodząca | Running fan 2 GEN (Cooling water) | Enum | Enum | Live Value | Long | Live Value
WGEN.ClWtrLev | #N/A | WGEN. | ClWtrLev | Generator Cooling Water Level | Generator-Kühlwasserstand | Nivel de agua de refrigeración del generador | Poziom wody chłodzącej generatora | Generator cooling water level | Enum | Enum | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WGEN.ClWtrLevSt | #N/A | WGEN. | ClWtrLevSt | Generator/Converter cooling water level | Generator/Konverter Kühlwasserstand | Nivel de agua de refrigeración del generador/convertidor | Poziom wody chłodzącej generator/konwerter | Level Generator/Converter cooling water | Enum | Enum | Live Value | Long | Live Value
WGEN.ClWtrPmpPres | #N/A | WGEN. | ClWtrPmpPres | Generator Cooling Water Pump Pressure | Druck der Kühlwasserpumpe des Generator | Presión de la bomba de agua de refrigeración del generador | Generator ciśnienie pompy wody chłodz. | Generator cooling water pump pressure | bar | bar | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WGEN.ClWtrPmpPres_10m_Avg | #N/A | WGEN. | ClWtrPmpPres_10m_Avg | Generator Cooling Water Pump Pressure (avg) | Druck der Kühlwasserpumpe des Generator (avg) | Presión de la bomba de agua de refrigeración del generador (avg) | Generator ciśnienie pompy wody chłodz. (avg) | Generator cooling water pump pressure | bar | bar | Average | Double | 10 minute tag
WGEN.ClWtrPmpPres_10m_Max | #N/A | WGEN. | ClWtrPmpPres_10m_Max | Generator Cooling Water Pump Pressure (max) | Druck der Kühlwasserpumpe des Generator (max) | Presión de la bomba de agua de refrigeración del generador (max) | Generator ciśnienie pompy wody chłodz. (max) | Generator cooling water pump pressure | bar | bar | Maximum | Double | 10 minute tag
WGEN.ClWtrPmpPres_10m_Min | #N/A | WGEN. | ClWtrPmpPres_10m_Min | Generator Cooling Water Pump Pressure (min) | Druck der Kühlwasserpumpe des Generator (min) | Presión de la bomba de agua de refrigeración del generador (min) | Generator ciśnienie pompy wody chłodz. (min) | Generator cooling water pump pressure | bar | bar | Minimum | Double | 10 minute tag
WGEN.ClWtrPmpPres_10m_Std | #N/A | WGEN. | ClWtrPmpPres_10m_Std | Generator Cooling Water Pump Pressure (std) | Druck der Kühlwasserpumpe des Generator (std) | Presión de la bomba de agua de refrigeración del generador (std) | Generator ciśnienie pompy wody chłodz. (std) | Generator cooling water pump pressure | bar | bar | Standard Deviation | Double | 10 minute tag
WGEN.ClWtrPmpSt | #N/A | WGEN. | ClWtrPmpSt | Waterpump Generator/Converter | Wasserpumpe Generator/Konverter | Bomba de agua del generador/convertidor | Generator/konwerter pompa wodna | Feedback Waterpump Generator + Converter | Enum | Enum | Live Value | Long | Live Value
WGEN.ClWtrTmp | #N/A | WGEN. | ClWtrTmp | Generator Cooling Water Temp | Kühlwassertemperatur des Generators | Temperatura de agua de refrigeración del generador | Generator wody chłodz. temp | Generator cooling water temperature | deg_c | °C | Live Value | Double | Live Value
WGEN.ClWtrTmp_10m_Avg | #N/A | WGEN. | ClWtrTmp_10m_Avg | Generator Cooling Water Temp (avg) | Kühlwassertemperatur des Generators (avg) | Temperatura de agua de refrigeración del generador (avg) | Generator wody chłodz. temp (avg) | Generator cooling water temperature | deg_c | °C | Average | Double | 10 minute tag
WGEN.ClWtrTmp_10m_Max | #N/A | WGEN. | ClWtrTmp_10m_Max | Generator Cooling Water Temp (max) | Kühlwassertemperatur des Generators (max) | Temperatura de agua de refrigeración del generador (max) | Generator wody chłodz. temp (max) | Generator cooling water temperature | deg_c | °C | Maximum | Double | 10 minute tag
WGEN.ClWtrTmp_10m_Min | #N/A | WGEN. | ClWtrTmp_10m_Min | Generator Cooling Water Temp (min) | Kühlwassertemperatur des Generators (min) | Temperatura de agua de refrigeración del generador (min) | Generator wody chłodz. temp (min) | Generator cooling water temperature | deg_c | °C | Minimum | Double | 10 minute tag
WGEN.ClWtrTmp_10m_Std | #N/A | WGEN. | ClWtrTmp_10m_Std | Generator Cooling Water Temp (std) | Kühlwassertemperatur des Generators (std) | Temperatura de agua de refrigeración del generador (std) | Generator wody chłodz. temp (std) | Generator cooling water temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN.ClWtrTnkPres | #N/A | WGEN. | ClWtrTnkPres | Generator Cooling Water Tank Pressure | Druck im Kühlwassertank des Generators | Presión del depósito de agua de refrigeración del generador | Generator ciśn. zbiornika wody chłodz. | Generator cooling water tank pressure | bar | bar | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WGEN.ClWtrTnkPres_10m_Avg | #N/A | WGEN. | ClWtrTnkPres_10m_Avg | Generator Cooling Water Tank Pressure (avg) | Druck im Kühlwassertank des Generators (avg) | Presión del depósito de agua de refrigeración del generador (avg) | Generator ciśn. zbiornika wody chłodz. (avg) | Generator cooling water tank pressure | bar | bar | Average | Double | 10 minute tag
WGEN.ClWtrTnkPres_10m_Max | #N/A | WGEN. | ClWtrTnkPres_10m_Max | Generator Cooling Water Tank Pressure (max) | Druck im Kühlwassertank des Generators (max) | Presión del depósito de agua de refrigeración del generador (max) | Generator ciśn. zbiornika wody chłodz. (max) | Generator cooling water tank pressure | bar | bar | Maximum | Double | 10 minute tag
WGEN.ClWtrTnkPres_10m_Min | #N/A | WGEN. | ClWtrTnkPres_10m_Min | Generator Cooling Water Tank Pressure (min) | Druck im Kühlwassertank des Generators (min) | Presión del depósito de agua de refrigeración del generador (min) | Generator ciśn. zbiornika wody chłodz. (min) | Generator cooling water tank pressure | bar | bar | Minimum | Double | 10 minute tag
WGEN.ClWtrTnkPres_10m_Std | #N/A | WGEN. | ClWtrTnkPres_10m_Std | Generator Cooling Water Tank Pressure (std) | Druck im Kühlwassertank des Generators (std) | Presión del depósito de agua de refrigeración del generador (std) | Generator ciśn. zbiornika wody chłodz. (std) | Generator cooling water tank pressure | bar | bar | Standard Deviation | Double | 10 minute tag
WGEN.DmdRotSpdStp | #N/A | WGEN. | DmdRotSpdStp | Generator RPM Setpoint | Drehzahlsollwert des Generators | Punto de ajuste de RPM del generador | Nastawa obrotów generatora | Generator speed setpoint | rpm | RPM | Live Value | Double | Live Value
WGEN.DmdRotSpdStp_10m_Avg | #N/A | WGEN. | DmdRotSpdStp_10m_Avg | Generator RPM Setpoint (avg) | Drehzahlsollwert des Generators (avg) | Punto de ajuste de RPM del generador (avg) | Nastawa obrotów generatora (avg) | Generator speed setpoint | rpm | RPM | Average | Double | 10 minute tag
WGEN.DmdRotSpdStp_10m_Max | #N/A | WGEN. | DmdRotSpdStp_10m_Max | Generator RPM Setpoint (max) | Drehzahlsollwert des Generators (max) | Punto de ajuste de RPM del generador (max) | Nastawa obrotów generatora (max) | Generator speed setpoint | rpm | RPM | Maximum | Double | 10 minute tag
WGEN.DmdRotSpdStp_10m_Min | #N/A | WGEN. | DmdRotSpdStp_10m_Min | Generator RPM Setpoint (min) | Drehzahlsollwert des Generators (min) | Punto de ajuste de RPM del generador (min) | Nastawa obrotów generatora (min) | Generator speed setpoint | rpm | RPM | Minimum | Double | 10 minute tag
WGEN.DmdRotSpdStp_10m_Std | #N/A | WGEN. | DmdRotSpdStp_10m_Std | Generator RPM Setpoint (std) | Drehzahlsollwert des Generators (std) | Punto de ajuste de RPM del generador (std) | Nastawa obrotów generatora (std) | Generator speed setpoint | rpm | RPM | Standard Deviation | Double | 10 minute tag
WGEN.DmdSttVArStp | #N/A | WGEN. | DmdSttVArStp | Generator stator reactive power setpoint | Stator-Blindleistungssollwert des Generators | Punto de ajuste de potencia reactiva del estátor del generador | Nastawa mocy biernej stojana generatora | Reactive power at generator stator setpoint | VAr | VAr | Live Value | Double | Live Value
WGEN.DmdSttVArStp_10m_Avg | #N/A | WGEN. | DmdSttVArStp_10m_Avg | Generator stator reactive power setpoint (avg) | Stator-Blindleistungssollwert des Generators (avg) | Punto de ajuste de potencia reactiva del estátor del generador (avg) | Nastawa mocy biernej stojana generatora (avg) | Reactive power at generator stator setpoint | VAr | VAr | Average | Double | 10 minute tag
WGEN.DmdSttVArStp_10m_Max | #N/A | WGEN. | DmdSttVArStp_10m_Max | Generator stator reactive power setpoint (max) | Stator-Blindleistungssollwert des Generators (max) | Punto de ajuste de potencia reactiva del estátor del generador (max) | Nastawa mocy biernej stojana generatora (max) | Reactive power at generator stator setpoint | VAr | VAr | Maximum | Double | 10 minute tag
WGEN.DmdSttVArStp_10m_Min | #N/A | WGEN. | DmdSttVArStp_10m_Min | Generator stator reactive power setpoint (min) | Stator-Blindleistungssollwert des Generators (min) | Punto de ajuste de potencia reactiva del estátor del generador (min) | Nastawa mocy biernej stojana generatora (min) | Reactive power at generator stator setpoint | VAr | VAr | Minimum | Double | 10 minute tag
WGEN.DmdSttVArStp_10m_Std | #N/A | WGEN. | DmdSttVArStp_10m_Std | Generator stator reactive power setpoint (std) | Stator-Blindleistungssollwert des Generators (std) | Punto de ajuste de potencia reactiva del estátor del generador (std) | Nastawa mocy biernej stojana generatora (std) | Reactive power at generator stator setpoint | VAr | VAr | Standard Deviation | Double | 10 minute tag
WGEN.DmdSttWStp | #N/A | WGEN. | DmdSttWStp | Generator stator Active power setpoint | Stator-Wirkleistungssollwert des Generators | Punto de ajuste de potencia activa del estátor del generador | Stojan generatora Aktywny nastawa mocy | Active power at generator stator setpoint | W | W | Live Value | Double | Live Value
WGEN.DmdSttWStp_10m_Avg | #N/A | WGEN. | DmdSttWStp_10m_Avg | Generator stator Active power setpoint (avg) | Stator-Wirkleistungssollwert des Generators (avg) | Punto de ajuste de potencia activa del estátor del generador (avg) | Stojan generatora Aktywny nastawa mocy (avg) | Active power at generator stator setpoint | W | W | Average | Double | 10 minute tag
WGEN.DmdSttWStp_10m_Max | #N/A | WGEN. | DmdSttWStp_10m_Max | Generator stator Active power setpoint (max) | Stator-Wirkleistungssollwert des Generators (max) | Punto de ajuste de potencia activa del estátor del generador (max) | Stojan generatora Aktywny nastawa mocy (max) | Active power at generator stator setpoint | W | W | Maximum | Double | 10 minute tag
WGEN.DmdSttWStp_10m_Min | #N/A | WGEN. | DmdSttWStp_10m_Min | Generator stator Active power setpoint (min) | Stator-Wirkleistungssollwert des Generators (min) | Punto de ajuste de potencia activa del estátor del generador (min) | Stojan generatora Aktywny nastawa mocy (min) | Active power at generator stator setpoint | W | W | Minimum | Double | 10 minute tag
WGEN.DmdSttWStp_10m_Std | #N/A | WGEN. | DmdSttWStp_10m_Std | Generator stator Active power setpoint (std) | Stator-Wirkleistungssollwert des Generators (std) | Punto de ajuste de potencia activa del estátor del generador (std) | Stojan generatora Aktywny nastawa mocy (std) | Active power at generator stator setpoint | W | W | Standard Deviation | Double | 10 minute tag
WGEN.DrtOpTms | #N/A | WGEN. | DrtOpTms | Operation time with derated active power setpoint | Betriebszeit mit reduziertem Wirkleistungssollwert | Tiempo de funcionamiento con punto de ajuste de potencia activo disminuido | Czas pracy ze zmniejszoną nastawą mocy czynnej | Operation time with derated active power setpoint | s | seconds | Total Counter | Long | Live Value
WGEN.DrtOpTms_10m_Sum | #N/A | WGEN. | DrtOpTms_10m_Sum | Operation time with derated active power setpoint (sum) | Betriebszeit mit reduziertem Wirkleistungssollwert (sum) | Tiempo de funcionamiento con punto de ajuste de potencia activo disminuido (sum) | Czas pracy ze zmniejszoną nastawą mocy czynnej (sum) | Operation time with derated active power setpoint | s | seconds | Summation | Long | 10 minute tag
WGEN.Gn1Gn2Cnt | #N/A | WGEN. | Gn1Gn2Cnt | Number of activations of G -> g | Anzahl der Aktivierungen von G -> g | Número de activaciones de G -> g | Liczba aktywacji G -> g | Number of activations of G -> g | count | Count | Total Counter | Long | Live Value
WGEN.Gn1Gn2Cnt_10m_End | #N/A | WGEN. | Gn1Gn2Cnt_10m_End | Number of activations of G -> g (end) | Anzahl der Aktivierungen von G -> g (end) | Número de activaciones de G -> g (end) | Liczba aktywacji G -> g (end) | Number of activations of G -> g | count | Count | Endvalue | Long | 10 minute tag
WGEN.Gn2Gn1Cnt | #N/A | WGEN. | Gn2Gn1Cnt | Number of activations of g -> G | Anzahl der Aktivierungen von g -> G | Número de activaciones de g -> G | Liczba aktywacji g -> G | Number of activations of g -> G | count | Count | Total Counter | Long | Live Value
WGEN.Gn2Gn1Cnt_10m_End | #N/A | WGEN. | Gn2Gn1Cnt_10m_End | Number of activations of g -> G (end) | Anzahl der Aktivierungen von g -> G (end) | Número de activaciones de g -> G (end) | Liczba aktywacji g -> G (end) | Number of activations of g -> G | count | Count | Endvalue | Long | 10 minute tag
WGEN.GnOpSt | WGEN.GnOpSt | WGEN. | GnOpSt | Generator Status | Generator-Status | Estado del generador | Stan generatora | Status of generator | Enum | Enum | Live Value | Long | Live Value
WGEN.GnOpSt_10m_End | #N/A | WGEN. | GnOpSt_10m_End | Generator Cut-in Status (end) | Generator Einschaltstatus (end) | Estado de corte del generador (end) | Stan odcięcia generatora (end) | Generator cut-in (will be TRUE (1) if a generator is connected the whole 10 minute period) | Enum | Enum | Endvalue | Long | 10 minute tag
WGEN.GnOpStStr | #N/A | WGEN. | GnOpStStr | Generator status text | Statustext des Generators | Texto del estado del generador | Tekst stanu generatora | Status of generator text | String | String | Live Value | String | Live Value
WGEN.GriA | #N/A | WGEN. | GriA | Generator Current | Generator Strom | Corriente del generador | Prąd generatora | Generator current | A | A | Live Value | Double | Live Value
WGEN.GriA_10m_Avg | #N/A | WGEN. | GriA_10m_Avg | Generator Current (avg) | Generator Strom (avg) | Corriente del generador (avg) | Prąd generatora (avg) | Generator current | A | A | Average | Double | 10 minute tag
WGEN.GriA_10m_Max | #N/A | WGEN. | GriA_10m_Max | Generator Current (max) | Generator Strom (max) | Corriente del generador (max) | Prąd generatora (max) | Generator current | A | A | Maximum | Double | 10 minute tag
WGEN.GriA_10m_Min | #N/A | WGEN. | GriA_10m_Min | Generator Current (min) | Generator Strom (min) | Corriente del generador (min) | Prąd generatora (min) | Generator current | A | A | Minimum | Double | 10 minute tag
WGEN.GriA_10m_Std | #N/A | WGEN. | GriA_10m_Std | Generator Current (std) | Generator Strom (std) | Corriente del generador (std) | Prąd generatora (std) | Generator current | A | A | Standard Deviation | Double | 10 minute tag
WGEN.GsLev | #N/A | WGEN. | GsLev | Grease level in the generator bearing lubrication tank | Fettstand im Schmiermittelbehälter der Generatorlager | Nivel de grasa del depósito de lubricación del cojinete del generador | Poziom smaru w zbiorniku smarowym łożyska generatora | Grease level in the generator bearing lubrication tank | percent | percent | Live Value | Double | Live Value
WGEN.GsLev_10m_Avg | #N/A | WGEN. | GsLev_10m_Avg | Grease level in the generator bearing lubrication tank (avg) | Fettstand im Schmiermittelbehälter der Generatorlager (avg) | Nivel de grasa del depósito de lubricación del cojinete del generador (avg) | Poziom smaru w zbiorniku smarowym łożyska generatora (avg) | Grease level in the generator bearing lubrication tank | percent | percent | Average | Double | 10 minute tag
WGEN.GsLev_10m_Max | #N/A | WGEN. | GsLev_10m_Max | Grease level in the generator bearing lubrication tank (max) | Fettstand im Schmiermittelbehälter der Generatorlager (max) | Nivel de grasa del depósito de lubricación del cojinete del generador (max) | Poziom smaru w zbiorniku smarowym łożyska generatora (max) | Grease level in the generator bearing lubrication tank | percent | percent | Maximum | Double | 10 minute tag
WGEN.GsLev_10m_Min | #N/A | WGEN. | GsLev_10m_Min | Grease level in the generator bearing lubrication tank (min) | Fettstand im Schmiermittelbehälter der Generatorlager (min) | Nivel de grasa del depósito de lubricación del cojinete del generador (min) | Poziom smaru w zbiorniku smarowym łożyska generatora (min) | Grease level in the generator bearing lubrication tank | percent | percent | Minimum | Double | 10 minute tag
WGEN.GsLev_10m_Std | #N/A | WGEN. | GsLev_10m_Std | Grease level in the generator bearing lubrication tank (std) | Fettstand im Schmiermittelbehälter der Generatorlager (std) | Nivel de grasa del depósito de lubricación del cojinete del generador (std) | Poziom smaru w zbiorniku smarowym łożyska generatora (std) | Grease level in the generator bearing lubrication tank | percent | percent | Standard Deviation | Double | 10 minute tag
WGEN.HtCnt | #N/A | WGEN. | HtCnt | Number of activations of generator heater | Anzahl der Aktivierungen der Generatorheizung | Número de activaciones del calentador del generador | Liczba aktywacji nagrzewnicy generatora | Number of activations of generator heater | count | Count | Total Counter | Long | Live Value
WGEN.HtCnt_10m_End | #N/A | WGEN. | HtCnt_10m_End | Number of activations of generator heater (end) | Anzahl der Aktivierungen der Generatorheizung (end) | Número de activaciones del calentador del generador (end) | Liczba aktywacji nagrzewnicy generatora (end) | Number of activations of generator heater | count | Count | Endvalue | Long | 10 minute tag
WGEN.HtTms | #N/A | WGEN. | HtTms | Time the generator heater has been activated | Zeit, in der die Heizung des Generators aktiviert wurde | Tiempo que el calentador del generador ha estado activado | Czas aktywacji nagrzewnicy generatora | Time the generator heater has been activated | s | seconds | Total Counter | Long | Live Value
WGEN.HtTms_10m_End | #N/A | WGEN. | HtTms_10m_End | Time the generator heater has been activated (end) | Zeit, in der die Heizung des Generators aktiviert wurde (end) | Tiempo que el calentador del generador ha estado activado (end) | Czas aktywacji nagrzewnicy generatora (end) | Time the generator heater has been activated | s | seconds | Endvalue | Long | 10 minute tag
WGEN.InLetTmp | WGEN.InletTmp | WGEN. | InLetTmp | Generator Water Inlet Temp | Generator Wassereintrittstemperatur | Temperatura de entrada del agua del generador | Generator Temp wlotu wody | Generator Water inlet temperature | deg_c | Degrees | Live Value | Double | Live Value
WGEN.InLetTmp_10m_Avg | #N/A | WGEN. | InLetTmp_10m_Avg | Generator Water Inlet Temp (avg) | Generator Wassereintrittstemperatur (avg) | Temperatura de entrada del agua del generador (avg) | Generator Temp wlotu wody (avg) | Generator Water inlet temperature | deg_c | Degrees | Average | Double | 10 minute tag
WGEN.InLetTmp_10m_Max | #N/A | WGEN. | InLetTmp_10m_Max | Generator Water Inlet Temp (max) | Generator Wassereintrittstemperatur (max) | Temperatura de entrada del agua del generador (max) | Generator Temp wlotu wody (max) | Generator Water inlet temperature | deg_c | Degrees | Maximum | Double | 10 minute tag
WGEN.InLetTmp_10m_Min | #N/A | WGEN. | InLetTmp_10m_Min | Generator Water Inlet Temp (min) | Generator Wassereintrittstemperatur (min) | Temperatura de entrada del agua del generador (min) | Generator Temp wlotu wody (min) | Generator Water inlet temperature | deg_c | Degrees | Minimum | Double | 10 minute tag
WGEN.InLetTmp_10m_Std | #N/A | WGEN. | InLetTmp_10m_Std | Generator Water Inlet Temp (std) | Generator Wassereintrittstemperatur (std) | Temperatura de entrada del agua del generador (std) | Generator Temp wlotu wody (std) | Generator Water inlet temperature | deg_c | Degrees | Standard Deviation | Double | 10 minute tag
WGEN.OpTms | #N/A | WGEN. | OpTms | Time with generator cut-in in | Zeit mit Generatorzuschaltung | Tiempo de corte del generador | Czas z odcięciem generatora | Time with generator cut-in in | s | seconds | Total Counter | Long | Live Value
WGEN.OpTms_10m_End | #N/A | WGEN. | OpTms_10m_End | Time with generator cut-in in (end) | Zeit mit Generatorzuschaltung (end) | Tiempo de corte del generador (end) | Czas z odcięciem generatora (end) | Time with generator cut-in in | s | seconds | Endvalue | Long | 10 minute tag
WGEN.OpTms_10m_Sum | #N/A | WGEN. | OpTms_10m_Sum | Time with generator cut-in (sum) | Zeit mit Generatorzuschaltung (sum) | Tiempo de corte del generador (sum) | Czas z odcięciem generatora (sum) | Time with generator cut-in in each 10 minute period i.e. 0-600 seconds | s | seconds | Summation | Long | 10 minute tag
WGEN.OpTms_Dly_Sum | #N/A | WGEN. | OpTms_Dly_Sum | Time with generator cut-in (sum) | Zeit mit Generatorzuschaltung (sum) | Tiempo de corte del generador (sum) | Czas z odcięciem generatora (sum) | Time with generator cut-in in each Daily period i.e. 0-86400 seconds | s | seconds | Summation | Long | Daily tag
WGEN.OpTms_Mly_Sum | #N/A | WGEN. | OpTms_Mly_Sum | Time with generator cut-in (sum) | Zeit mit Generatorzuschaltung (sum) | Tiempo de corte del generador (sum) | Czas z odcięciem generatora (sum) | Time with generator cut-in in each Monthly period | s | seconds | Summation | Long | Monthly tag
WGEN.OpTms1 | #N/A | WGEN. | OpTms1 | Hours Generator 1 operational | Stunden Generator 1 in Betrieb | Horas de funcionamiento del Generador 1 | Generator 2 godz. pracy | Hours Generator 1 operational | s | seconds | Total Counter | Long | Live Value |  |  | New Vestas UA TAG
WGEN.OpTms2 | #N/A | WGEN. | OpTms2 | Hours Generator 2 operational | Stunden Generator 2 in Betrieb | Horas de funcionamiento del Generador 2 | Generator 1 godz. pracy | Hours Generator 2 operational | s | seconds | Total Counter | Long | Live Value |  |  | New Vestas UA TAG
WGEN.OpTmsRs | WGEN.OpTmsRs | WGEN. | OpTmsRs | Generator operation time | Betriebszeit des Generators | Tiempo de funcionamiento del generador | Czas pracy generatora | Generator operation time in seconds (vendor specific) | s | seconds | Total Counter | Long | Live Value
WGEN.OutLetTmp | #N/A | WGEN. | OutLetTmp | Generator Water Outlet Temp | Generator Wasseraustrittstemperatur | Temperatura del agua de salida del generador | Generator ujście wody temp. | Generator Water outlet temperature | deg_c | Degrees | Live Value | Double | Live Value
WGEN.OutLetTmp_10m_Avg | #N/A | WGEN. | OutLetTmp_10m_Avg | Generator Water Outlet Temp (avg) | Generator Wasseraustrittstemperatur (avg) | Temperatura del agua de salida del generador (avg) | Generator ujście wody temp. (avg) | Generator Water outlet temperature | deg_c | Degrees | Average | Double | 10 minute tag
WGEN.OutLetTmp_10m_Max | #N/A | WGEN. | OutLetTmp_10m_Max | Generator Water Outlet Temp (max) | Generator Wasseraustrittstemperatur (max) | Temperatura del agua de salida del generador (max) | Generator ujście wody temp. (max) | Generator Water outlet temperature | deg_c | Degrees | Maximum | Double | 10 minute tag
WGEN.OutLetTmp_10m_Min | #N/A | WGEN. | OutLetTmp_10m_Min | Generator Water Outlet Temp (min) | Generator Wasseraustrittstemperatur (min) | Temperatura del agua de salida del generador (min) | Generator ujście wody temp. (min) | Generator Water outlet temperature | deg_c | Degrees | Minimum | Double | 10 minute tag
WGEN.OutLetTmp_10m_Std | #N/A | WGEN. | OutLetTmp_10m_Std | Generator Water Outlet Temp (std) | Generator Wasseraustrittstemperatur (std) | Temperatura del agua de salida del generador (std) | Generator ujście wody temp. (std) | Generator Water outlet temperature | deg_c | Degrees | Standard Deviation | Double | 10 minute tag
WGEN.RotA | WGEN.RotA | WGEN. | RotA | Generator Rotor Current | Generatorrotorstrom | Corriente del rotor del generador | Prąd rotora generatora | Generator rotor 3 phase current | A | A | Live Value | Double | Live Value
WGEN.RotA_10m_Avg | #N/A | WGEN. | RotA_10m_Avg | Generator Rotor Current (avg) | Generatorrotorstrom (avg) | Corriente del rotor del generador (avg) | Prąd rotora generatora (avg) | Generator rotor 3 phase current | A | A | Average | Double | 10 minute tag
WGEN.RotA_10m_Max | #N/A | WGEN. | RotA_10m_Max | Generator Rotor Current (max) | Generatorrotorstrom (max) | Corriente del rotor del generador (max) | Prąd rotora generatora (max) | Generator rotor 3 phase current | A | A | Maximum | Double | 10 minute tag
WGEN.RotA_10m_Min | #N/A | WGEN. | RotA_10m_Min | Generator Rotor Current (min) | Generatorrotorstrom (min) | Corriente del rotor del generador (min) | Prąd rotora generatora (min) | Generator rotor 3 phase current | A | A | Minimum | Double | 10 minute tag
WGEN.RotA_10m_Std | #N/A | WGEN. | RotA_10m_Std | Generator Rotor Current (std) | Generatorrotorstrom (std) | Corriente del rotor del generador (std) | Prąd rotora generatora (std) | Generator rotor 3 phase current | A | A | Standard Deviation | Double | 10 minute tag
WGEN.RotExtAC | WGEN.RotExtAC | WGEN. | RotExtAC | Generator Rotor Excitation Alternating Current | Generator-Rotorerregung Wechselstrom | Corriente alterna de excitación del rotor del generador | Prąd przemienny wzbudzenia rotora generatora | Generator rotor alternating current excitation | A | A | Live Value | Double | Live Value
WGEN.RotExtDC | WGEN.RotExtDC | WGEN. | RotExtDC | Generator Rotor Excitation Direct Current | Generator-Rotorerregung Gleichstrom | Corriente directa de excitación del rotor del generador | Prąd wzbudzenia rotora generatora | Generator rotor direct current excitation | A | A | Live Value | Double | Live Value
WGEN.RotExtHtSnkTmp | #N/A | WGEN. | RotExtHtSnkTmp | Generator Excitation Heat Sink Temp | Generator-Erregung Kühlkörpertemperatur | Temperatura del disipador térmico de excitación del generador | Generator Wzbudzenie Radiator Temp | Generator Temperature excitation heat sink | deg_c | °C | Live Value | Double | Live Value
WGEN.RotExtHtSnkTmp_10m_Avg | #N/A | WGEN. | RotExtHtSnkTmp_10m_Avg | Generator Excitation Heat Sink Temp (avg) | Generator-Erregung Kühlkörpertemperatur (avg) | Temperatura del disipador térmico de excitación del generador (avg) | Generator Wzbudzenie Radiator Temp (avg) | Generator Temperature excitation heat sink | deg_c | °C | Average | Double | 10 minute tag | Rare tags for analysis
WGEN.RotExtPnlTmp | #N/A | WGEN. | RotExtPnlTmp | Generator Excitation Control Cabinet Temp | Generator Erregung Schaltschranktemperatur | Temperatura del armario eléctrico de excitación del generador | Generator Wzbudzenia szafa sterownicza Temp | Generator excitation control panel temperature | deg_c | °C | Live Value | Double | Live Value
WGEN.RotExtPnlTmp_10m_Avg | #N/A | WGEN. | RotExtPnlTmp_10m_Avg | Generator Excitation Control Cabinet Temp (avg) | Generator Erregung Schaltschranktemperatur (avg) | Temperatura del armario eléctrico de excitación del generador (avg) | Generator Wzbudzenia szafa sterownicza Temp (avg) | Generator excitation control panel temperature | deg_c | °C | Average | Double | 10 minute tag
WGEN.RotPNV | WGEN.RotPNV | WGEN. | RotPNV | Generator P-N Voltage Rotor side | Generator P-N Spannung Rotorseite | Tensión P-N en el lado del rotor del generador | Generator P-N Nap. po stronie rotora | Generator rotor 3 phase-to-neutral voltage | V | V | Live Value | Double | Live Value
WGEN.RotPNV1 | #N/A | WGEN. | RotPNV1 | Generator P-N L1 Voltage Rotor side | Generator P-N L1 Spannung Rotorseite | Tensión P-N L1 en el lado del rotor del generador | Generator P-N L1 Nap. po stronie rotora | Generator rotor phase1-to-neutral voltage | V | V | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WGEN.RotPNV2 | #N/A | WGEN. | RotPNV2 | Generator P-N L2 Voltage Rotor side | Generator P-N L2 Spannung Rotorseite | Tensión P-N L2 en el lado del rotor del generador | Generator P-N L2 Nap. po stronie rotora | Generator rotor phase2-to-neutral voltage | V | V | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WGEN.RotPNV3 | #N/A | WGEN. | RotPNV3 | Generator P-N L3 Voltage Rotor side | Generator P-N L3 Spannung Rotorseite | Tensión P-N L3 en el lado del rotor del generador | Generator P-N L3 Nap. po stronie rotora | Generator rotor phase3-to-neutral voltage | V | V | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WGEN.RotPPV | WGEN.RotPPV | WGEN. | RotPPV | Generator P-P Voltage Rotor side | Generator P-P Spannung Rotorseite | Tensión P-P en el lado del rotor del generador | Nap. po stronie rotora generatora P-P | Generator rotor 3 phase phase-to-phase voltage | V | V | Live Value | Double | Live Value
WGEN.RotSpd | WGEN.RotSpd | WGEN. | RotSpd | Generator RPM | Generatordrehzahl | RPM del generador | RPM generatora | Generator rotation speed | rpm | RPM | Live Value | Double | Live Value | Used in standard monitor Presentation
WGEN.RotSpd_10m_Avg | #N/A | WGEN. | RotSpd_10m_Avg | Generator RPM (avg) | Generatordrehzahl (avg) | RPM del generador (avg) | RPM generatora (avg) | Generator rotation speed | rpm | RPM | Average | Double | 10 minute tag | Common tags for analysis
WGEN.RotSpd_10m_Max | #N/A | WGEN. | RotSpd_10m_Max | Generator RPM (max) | Generatordrehzahl (max) | RPM del generador (max) | RPM generatora (max) | Generator rotation speed | rpm | RPM | Maximum | Double | 10 minute tag | Common tags for analysis
WGEN.RotSpd_10m_Min | #N/A | WGEN. | RotSpd_10m_Min | Generator RPM (min) | Generatordrehzahl (min) | RPM del generador (min) | RPM generatora (min) | Generator rotation speed | rpm | RPM | Minimum | Double | 10 minute tag | Common tags for analysis
WGEN.RotSpd_10m_Std | #N/A | WGEN. | RotSpd_10m_Std | Generator RPM (std) | Generatordrehzahl (std) | RPM del generador (std) | RPM generatora (std) | Generator rotation speed | rpm | RPM | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WGEN.RotSpd1 | #N/A | WGEN. | RotSpd1 | Generator RPM1 | Generatordrehzahl 1 | RPM1 del generador | Generator RPM1 | Generator rotation speed sensor 1 | rpm | RPM | Live Value | Double | Live Value | Used in standard monitor Presentation
WGEN.RotSpd1_10m_Avg | #N/A | WGEN. | RotSpd1_10m_Avg | Generator RPM1 (avg) | Generatordrehzahl 1 (avg) | RPM1 del generador (avg) | Generator RPM1 (avg) | Generator rotation speed sensor 1 | rpm | RPM | Average | Double | 10 minute tag | Common tags for analysis
WGEN.RotSpd1_10m_Max | #N/A | WGEN. | RotSpd1_10m_Max | Generator RPM1 (max) | Generatordrehzahl 1 (max) | RPM1 del generador (max) | Generator RPM1 (max) | Generator rotation speed sensor 1 | rpm | RPM | Maximum | Double | 10 minute tag | Common tags for analysis
WGEN.RotSpd1_10m_Min | #N/A | WGEN. | RotSpd1_10m_Min | Generator RPM1 (min) | Generatordrehzahl 1 (min) | RPM1 del generador (min) | Generator RPM1 (min) | Generator rotation speed sensor 1 | rpm | RPM | Minimum | Double | 10 minute tag | Common tags for analysis
WGEN.RotSpd1_10m_Std | #N/A | WGEN. | RotSpd1_10m_Std | Generator RPM1 (std) | Generatordrehzahl 1 (std) | RPM1 del generador (std) | Generator RPM1 (std) | Generator rotation speed sensor 1 | rpm | RPM | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WGEN.RotSpd2 | #N/A | WGEN. | RotSpd2 | Generator RPM2 | Generatordrehzahl 2 | RPM2 del generador | Generator RPM2 | Generator rotation speed sensor 2 | rpm | RPM | Live Value | Double | Live Value | Used in standard monitor Presentation
WGEN.RotSpd2_10m_Avg | #N/A | WGEN. | RotSpd2_10m_Avg | Generator RPM2 (avg) | Generatordrehzahl 2 (avg) | RPM2 del generador (avg) | Generator RPM2 (avg) | Generator rotation speed sensor 2 | rpm | RPM | Average | Double | 10 minute tag | Common tags for analysis
WGEN.RotSpd2_10m_Max | #N/A | WGEN. | RotSpd2_10m_Max | Generator RPM2 (max) | Generatordrehzahl 2 (max) | RPM2 del generador (max) | Generator RPM2 (max) | Generator rotation speed sensor 2 | rpm | RPM | Maximum | Double | 10 minute tag | Common tags for analysis
WGEN.RotSpd2_10m_Min | #N/A | WGEN. | RotSpd2_10m_Min | Generator RPM2 (min) | Generatordrehzahl 2 (min) | RPM2 del generador (min) | Generator RPM2 (min) | Generator rotation speed sensor 2 | rpm | RPM | Minimum | Double | 10 minute tag | Common tags for analysis
WGEN.RotSpd2_10m_Std | #N/A | WGEN. | RotSpd2_10m_Std | Generator RPM2 (std) | Generatordrehzahl 2 (std) | RPM2 del generador (std) | Generator RPM2 (std) | Generator rotation speed sensor 2 | rpm | RPM | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WGEN.RotSpdLim | #N/A | WGEN. | RotSpdLim | Generator RPM Speed Limit | Generatordrehzahl Grenzwert | Límite de velocidad de RPM del generador | Ograniczenie prędkości obrotowej obrotów generatora | Generator rotation speed limit | rpm | rpm | Live Value | Double | Live Value
WGEN.RotTmp | WGEN.RotTmp | WGEN. | RotTmp | Generator Rotor Temp | Generator Rotortemperatur | Temperatura del rotor del generador | Wirnik generatora Temp | Generator rotor temperature | deg_c | °C | Live Value | Double | Live Value
WGEN.RotTmp_10m_Avg | #N/A | WGEN. | RotTmp_10m_Avg | Generator Rotor Temp (avg) | Generator Rotortemperatur (avg) | Temperatura del rotor del generador (avg) | Wirnik generatora Temp (avg) | Generator rotor temperature | deg_c | °C | Average | Double | 10 minute tag | Rare tags for analysis
WGEN.RotTmp_10m_Max | #N/A | WGEN. | RotTmp_10m_Max | Generator Rotor Temp (max) | Generator Rotortemperatur (max) | Temperatura del rotor del generador (max) | Wirnik generatora Temp (max) | Generator rotor temperature | deg_c | °C | Maximum | Double | 10 minute tag | Rare tags for analysis
WGEN.RotTmp_10m_Min | #N/A | WGEN. | RotTmp_10m_Min | Generator Rotor Temp (min) | Generator Rotortemperatur (min) | Temperatura del rotor del generador (min) | Wirnik generatora Temp (min) | Generator rotor temperature | deg_c | °C | Minimum | Double | 10 minute tag | Rare tags for analysis
WGEN.RotTmp_10m_Std | #N/A | WGEN. | RotTmp_10m_Std | Generator Rotor Temp (std) | Generator Rotortemperatur (std) | Temperatura del rotor del generador (std) | Wirnik generatora Temp (std) | Generator rotor temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WGEN.RotTmp1 | #N/A | WGEN. | RotTmp1 | Generator Rotor Temp1 | Generator Rotortemperatur 1 | Temperatura 1 del rotor del generador | Wirnik generatora Temp1 | Generator rotor temperature 1 | deg_c | °C | Live Value | Double | Live Value
WGEN.RotTmp1_10m_Avg | #N/A | WGEN. | RotTmp1_10m_Avg | Generator Rotor Temp1 (avg) | Generator Rotortemperatur 1 (avg) | Temperatura 1 del rotor del generador (avg) | Wirnik generatora Temp1 (avg) | Generator rotor temperature 1 | deg_c | °C | Average | Double | 10 minute tag | Rare tags for analysis
WGEN.RotTmp1_10m_Max | #N/A | WGEN. | RotTmp1_10m_Max | Generator Rotor Temp1 (max) | Generator Rotortemperatur 1 (max) | Temperatura 1 del rotor del generador (max) | Wirnik generatora Temp1 (max) | Generator rotor temperature 1 | deg_c | °C | Maximum | Double | 10 minute tag
WGEN.RotTmp1_10m_Min | #N/A | WGEN. | RotTmp1_10m_Min | Generator Rotor Temp1 (min) | Generator Rotortemperatur 1 (min) | Temperatura 1 del rotor del generador (min) | Wirnik generatora Temp1 (min) | Generator rotor temperature 1 | deg_c | °C | Minimum | Double | 10 minute tag
WGEN.RotTmp1_10m_Std | #N/A | WGEN. | RotTmp1_10m_Std | Generator Rotor Temp1 (std) | Generator Rotortemperatur 1 (std) | Temperatura 1 del rotor del generador (std) | Wirnik generatora Temp1 (std) | Generator rotor temperature 1 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN.RotTmp2 | #N/A | WGEN. | RotTmp2 | Generator Rotor Temp2 | Generator Rotortemperatur 2 | Temperatura 2 del rotor del generador | Wirnik generatora Temp2 | Generator rotor temperature 2 | deg_c | °C | Live Value | Double | Live Value
WGEN.RotTmp2_10m_Avg | #N/A | WGEN. | RotTmp2_10m_Avg | Generator Rotor Temp2 (avg) | Generator Rotortemperatur 2 (avg) | Temperatura 2 del rotor del generador (avg) | Wirnik generatora Temp2 (avg) | Generator rotor temperature 2 | deg_c | °C | Average | Double | 10 minute tag | Rare tags for analysis
WGEN.RotTmp2_10m_Max | #N/A | WGEN. | RotTmp2_10m_Max | Generator Rotor Temp2 (max) | Generator Rotortemperatur 2 (max) | Temperatura 2 del rotor del generador (max) | Wirnik generatora Temp2 (max) | Generator rotor temperature 2 | deg_c | °C | Maximum | Double | 10 minute tag
WGEN.RotTmp2_10m_Min | #N/A | WGEN. | RotTmp2_10m_Min | Generator Rotor Temp2 (min) | Generator Rotortemperatur 2 (min) | Temperatura 2 del rotor del generador (min) | Wirnik generatora Temp2 (min) | Generator rotor temperature 2 | deg_c | °C | Minimum | Double | 10 minute tag
WGEN.RotTmp2_10m_Std | #N/A | WGEN. | RotTmp2_10m_Std | Generator Rotor Temp2 (std) | Generator Rotortemperatur 2 (std) | Temperatura 2 del rotor del generador (std) | Wirnik generatora Temp2 (std) | Generator rotor temperature 2 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN.RotTmp3 | #N/A | WGEN. | RotTmp3 | Generator Rotor Temp3 | Generator Rotortemperatur 3 | Temperatura 3 del rotor del generador | Wirnik generatora Temp3 | Temperature measurements for generator rotor, phase 3 | deg_c | °C | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WGEN.SlpRngTmp | #N/A | WGEN. | SlpRngTmp | Generator Slipring Temp | Generator Schleifring Temperatur | Temperatura del anillo colector del generador | Generator Pierśc. ślizg. Temp | Temperature of the generator slipring between rotor and stator | deg_c | °C | Live Value | Double | Live Value | Used in some specialised presentations
WGEN.SlpRngTmp_10m_Avg | #N/A | WGEN. | SlpRngTmp_10m_Avg | Generator Slipring Temp (avg) | Generator Schleifring Temperatur (avg) | Temperatura del anillo colector del generador (avg) | Generator Pierśc. ślizg. Temp (avg) | Temperature of the generator slipring between rotor and stator | deg_c | °C | Average | Double | 10 minute tag | Rare tags for analysis
WGEN.SlpRngTmp_10m_Max | #N/A | WGEN. | SlpRngTmp_10m_Max | Generator Slipring Temp (max) | Generator Schleifring Temperatur (max) | Temperatura del anillo colector del generador (max) | Generator Pierśc. ślizg. Temp (max) | Temperature of the generator slipring between rotor and stator | deg_c | °C | Maximum | Double | 10 minute tag | Rare tags for analysis
WGEN.SlpRngTmp_10m_Min | #N/A | WGEN. | SlpRngTmp_10m_Min | Generator Slipring Temp (min) | Generator Schleifring Temperatur (min) | Temperatura del anillo colector del generador (min) | Generator Pierśc. ślizg. Temp (min) | Temperature of the generator slipring between rotor and stator | deg_c | °C | Minimum | Double | 10 minute tag | Rare tags for analysis
WGEN.SlpRngTmp_10m_Std | #N/A | WGEN. | SlpRngTmp_10m_Std | Generator Slipring Temp (std) | Generator Schleifring Temperatur (std) | Temperatura del anillo colector del generador (std) | Generator Pierśc. ślizg. Temp (std) | Temperature of the generator slipring between rotor and stator | deg_c | °C | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WGEN.SlpRngTmp2 | #N/A | WGEN. | SlpRngTmp2 | Generator Slipring Top Chaimber Temp | Generator Schleifring Obere Kammertemperatur | Temperatura del compartimiento superior del anillo colector del generador | Generator Pierśc. ślizg. Górna komora Temp | Temperature of the generator slipring between rotor and stator, in top of chaimber | deg_c | °C | Live Value | Double | Live Value | Used in some specialised presentations
WGEN.SlpRngTmp2_10m_Avg | #N/A | WGEN. | SlpRngTmp2_10m_Avg | Generator Slipring Top Chaimber Temp (avg) | Generator Schleifring Obere Kammertemperatur (avg) | Temperatura del compartimiento superior del anillo colector del generador (avg) | Generator Pierśc. ślizg. Górna komora Temp (avg) | Temperature of the generator slipring between rotor and stator, in top of chaimber | deg_c | °C | Average | Double | 10 minute tag | Rare tags for analysis
WGEN.SlpRngTmp2_10m_Max | #N/A | WGEN. | SlpRngTmp2_10m_Max | Generator Slipring Top Chaimber Temp (max) | Generator Schleifring Obere Kammertemperatur (max) | Temperatura del compartimiento superior del anillo colector del generador (max) | Generator Pierśc. ślizg. Górna komora Temp (max) | Temperature of the generator slipring between rotor and stator, in top of chaimber | deg_c | °C | Maximum | Double | 10 minute tag | Rare tags for analysis
WGEN.SlpRngTmp2_10m_Min | #N/A | WGEN. | SlpRngTmp2_10m_Min | Generator Slipring Top Chaimber Temp (min) | Generator Schleifring Obere Kammertemperatur (min) | Temperatura del compartimiento superior del anillo colector del generador (min) | Generator Pierśc. ślizg. Górna komora Temp (min) | Temperature of the generator slipring between rotor and stator, in top of chaimber | deg_c | °C | Minimum | Double | 10 minute tag | Rare tags for analysis
WGEN.SlpRngTmp2_10m_Std | #N/A | WGEN. | SlpRngTmp2_10m_Std | Generator Slipring Top Chaimber Temp (std) | Generator Schleifring Obere Kammertemperatur (std) | Temperatura del compartimiento superior del anillo colector del generador (std) | Generator Pierśc. ślizg. Górna komora Temp (std) | Temperature of the generator slipring between rotor and stator, in top of chaimber | deg_c | °C | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WGEN.SttA | WGEN.SttA | WGEN. | SttA | Generator Stator Current | Generator Statorstrom | Corriente del estátor del generador | Prąd stojana generatora | Generator stator current | A | A | Live Value | Double | Live Value
WGEN.SttA_10m_Avg | #N/A | WGEN. | SttA_10m_Avg | Generator Stator Current (avg) | Generator Statorstrom (avg) | Corriente del estátor del generador (avg) | Prąd stojana generatora (avg) | Generator stator current | A | A | Average | Double | 10 minute tag | Rare tags for analysis
WGEN.SttA_10m_Max | #N/A | WGEN. | SttA_10m_Max | Generator Stator Current (max) | Generator Statorstrom (max) | Corriente del estátor del generador (max) | Prąd stojana generatora (max) | Generator stator current | A | A | Maximum | Double | 10 minute tag | Rare tags for analysis
WGEN.SttA_10m_Min | #N/A | WGEN. | SttA_10m_Min | Generator Stator Current (min) | Generator Statorstrom (min) | Corriente del estátor del generador (min) | Prąd stojana generatora (min) | Generator stator current | A | A | Minimum | Double | 10 minute tag | Rare tags for analysis
WGEN.SttA_10m_Std | #N/A | WGEN. | SttA_10m_Std | Generator Stator Current (std) | Generator Statorstrom (std) | Corriente del estátor del generador (std) | Prąd stojana generatora (std) | Generator stator current | A | A | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WGEN.SttPNV | WGEN.SttPNV | WGEN. | SttPNV | Generator P-N Voltage Stator side | Generator P-N Spannung Statorseite | Tensión P-N en el lado del estátor del generador | Generator P-N Strona stojana napięcia | Generator Stator phase to neutral voltage | V | V | Live Value | Double | Live Value
WGEN.SttPNV_10m_Avg | #N/A | WGEN. | SttPNV_10m_Avg | Generator P-N Voltage Stator side (avg) | Generator P-N Spannung Statorseite (avg) | Tensión P-N en el lado del estátor del generador (avg) | Generator P-N Strona stojana napięcia (avg) | Generator Stator phase to neutral voltage | V | V | Average | Double | 10 minute tag | Rare tags for analysis
WGEN.SttPNV_10m_Max | #N/A | WGEN. | SttPNV_10m_Max | Generator P-N Voltage Stator side (max) | Generator P-N Spannung Statorseite (max) | Tensión P-N en el lado del estátor del generador (max) | Generator P-N Strona stojana napięcia (max) | Generator Stator phase to neutral voltage | V | V | Maximum | Double | 10 minute tag | Rare tags for analysis
WGEN.SttPNV_10m_Min | #N/A | WGEN. | SttPNV_10m_Min | Generator P-N Voltage Stator side (min) | Generator P-N Spannung Statorseite (min) | Tensión P-N en el lado del estátor del generador (min) | Generator P-N Strona stojana napięcia (min) | Generator Stator phase to neutral voltage | V | V | Minimum | Double | 10 minute tag | Rare tags for analysis
WGEN.SttPNV_10m_Std | #N/A | WGEN. | SttPNV_10m_Std | Generator P-N Voltage Stator side (std) | Generator P-N Spannung Statorseite (std) | Tensión P-N en el lado del estátor del generador (std) | Generator P-N Strona stojana napięcia (std) | Generator Stator phase to neutral voltage | V | V | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WGEN.SttPPV | WGEN.SttPPV | WGEN. | SttPPV | Generator P-P Voltage Stator side | Generator P-P Spannung Statorseite | Tensión P-N en el lado del estátor del generador | Wentylator P-P Strona stojana napięcia | Generator stator 3 phase phase-to-phase voltage | V | V | Live Value | Double | Live Value
WGEN.SttTmp | WGEN.SttTmp | WGEN. | SttTmp | Generator Stator Temp | Generator Stator Temperatur | Temperatura del estátor del generador | Generator Stojan Temp | Generator stator temperature | deg_c | °C | Live Value | Double | Live Value
WGEN.SttTmp_10m_Avg | #N/A | WGEN. | SttTmp_10m_Avg | Generator Stator Temp (avg) | Generator Stator Temperatur (avg) | Temperatura del estátor del generador (avg) | Generator Stojan Temp (avg) | Generator stator temperature | deg_c | °C | Average | Double | 10 minute tag | Rare tags for analysis
WGEN.SttTmp_10m_Max | #N/A | WGEN. | SttTmp_10m_Max | Generator Stator Temp (max) | Generator Stator Temperatur (max) | Temperatura del estátor del generador (max) | Generator Stojan Temp (max) | Generator stator temperature | deg_c | °C | Maximum | Double | 10 minute tag | Rare tags for analysis
WGEN.SttTmp_10m_Min | #N/A | WGEN. | SttTmp_10m_Min | Generator Stator Temp (min) | Generator Stator Temperatur (min) | Temperatura del estátor del generador (min) | Generator Stojan Temp (min) | Generator stator temperature | deg_c | °C | Minimum | Double | 10 minute tag | Rare tags for analysis
WGEN.SttTmp_10m_Std | #N/A | WGEN. | SttTmp_10m_Std | Generator Stator Temp (std) | Generator Stator Temperatur (std) | Temperatura del estátor del generador (std) | Generator Stojan Temp (std) | Generator stator temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WGEN.SttTmp1 | #N/A | WGEN. | SttTmp1 | Generator Stator L1 Temp | Generator Stator L1 Temperatur | Temperatura del estátor L1 del generador | Generator Stojan L1 Temp | Generator stator phase L1 temperature | deg_c | °C | Live Value | Double | Live Value
WGEN.SttTmp1_10m_Avg | #N/A | WGEN. | SttTmp1_10m_Avg | Generator Stator L1 Temp (avg) | Generator Stator L1 Temperatur (avg) | Temperatura del estátor L1 del generador (avg) | Generator Stojan L1 Temp (avg) | Generator stator phase L1 temperature | deg_c | °C | Average | Double | 10 minute tag
WGEN.SttTmp1_10m_Max | #N/A | WGEN. | SttTmp1_10m_Max | Generator Stator L1 Temp (max) | Generator Stator L1 Temperatur (max) | Temperatura del estátor L1 del generador (max) | Generator Stojan L1 Temp (max) | Generator stator phase L1 temperature | deg_c | °C | Maximum | Double | 10 minute tag
WGEN.SttTmp1_10m_Min | #N/A | WGEN. | SttTmp1_10m_Min | Generator Stator L1 Temp (min) | Generator Stator L1 Temperatur (min) | Temperatura del estátor L1 del generador (min) | Generator Stojan L1 Temp (min) | Generator stator phase L1 temperature | deg_c | °C | Minimum | Double | 10 minute tag
WGEN.SttTmp1_10m_Std | #N/A | WGEN. | SttTmp1_10m_Std | Generator Stator L1 Temp (std) | Generator Stator L1 Temperatur (std) | Temperatura del estátor L1 del generador (std) | Generator Stojan L1 Temp (std) | Generator stator phase L1 temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN.SttTmp2 | #N/A | WGEN. | SttTmp2 | Generator Stator L2 Temp | Generator Stator L2 Temperatur | Temperatura del estátor L2 del generador | Generator Stojan L2 Temp | Generator stator phase L2 temperature | deg_c | °C | Live Value | Double | Live Value
WGEN.SttTmp2_10m_Avg | #N/A | WGEN. | SttTmp2_10m_Avg | Generator Stator L2 Temp (avg) | Generator Stator L2 Temperatur (avg) | Temperatura del estátor L2 del generador (avg) | Generator Stojan L2 Temp (avg) | Generator stator phase L2 temperature | deg_c | °C | Average | Double | 10 minute tag
WGEN.SttTmp2_10m_Max | #N/A | WGEN. | SttTmp2_10m_Max | Generator Stator L2 Temp (max) | Generator Stator L2 Temperatur (max) | Temperatura del estátor L2 del generador (max) | Generator Stojan L2 Temp (max) | Generator stator phase L2 temperature | deg_c | °C | Maximum | Double | 10 minute tag
WGEN.SttTmp2_10m_Min | #N/A | WGEN. | SttTmp2_10m_Min | Generator Stator L2 Temp (min) | Generator Stator L2 Temperatur (min) | Temperatura del estátor L2 del generador (min) | Generator Stojan L2 Temp (min) | Generator stator phase L2 temperature | deg_c | °C | Minimum | Double | 10 minute tag
WGEN.SttTmp2_10m_Std | #N/A | WGEN. | SttTmp2_10m_Std | Generator Stator L2 Temp (std) | Generator Stator L2 Temperatur (std) | Temperatura del estátor L2 del generador (std) | Generator Stojan L2 Temp (std) | Generator stator phase L2 temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN.SttTmp3 | #N/A | WGEN. | SttTmp3 | Generator Stator L3 Temp | Generator Stator L3 Temperatur | Temperatura del estátor L3 del generador | Generator Stojan L3 Temp | Generator stator phase L3 temperature | deg_c | °C | Live Value | Double | Live Value
WGEN.SttTmp3_10m_Avg | #N/A | WGEN. | SttTmp3_10m_Avg | Generator Stator L3 Temp (avg) | Generator Stator L3 Temperatur (avg) | Temperatura del estátor L3 del generador (avg) | Generator Stojan L3 Temp (avg) | Generator stator phase L3 temperature | deg_c | °C | Average | Double | 10 minute tag
WGEN.SttTmp3_10m_Max | #N/A | WGEN. | SttTmp3_10m_Max | Generator Stator L3 Temp (max) | Generator Stator L3 Temperatur (max) | Temperatura del estátor L3 del generador (max) | Generator Stojan L3 Temp (max) | Generator stator phase L3 temperature | deg_c | °C | Maximum | Double | 10 minute tag
WGEN.SttTmp3_10m_Min | #N/A | WGEN. | SttTmp3_10m_Min | Generator Stator L3 Temp (min) | Generator Stator L3 Temperatur (min) | Temperatura del estátor L3 del generador (min) | Generator Stojan L3 Temp (min) | Generator stator phase L3 temperature | deg_c | °C | Minimum | Double | 10 minute tag
WGEN.SttTmp3_10m_Std | #N/A | WGEN. | SttTmp3_10m_Std | Generator Stator L3 Temp (std) | Generator Stator L3 Temperatur (std) | Temperatura del estátor L3 del generador (std) | Generator Stojan L3 Temp (std) | Generator stator phase L3 temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN.SttVAr | #N/A | WGEN. | SttVAr | Generator stator reactive power | Stator-Blindleistung des Generators | Potencia reactiva del estátor del generador | Moc bierna stojana generatora | Reactive power at generator stator | VAr | VAr | Live Value | Double | Live Value
WGEN.SttVAr_10m_Avg | #N/A | WGEN. | SttVAr_10m_Avg | Generator stator reactive power (avg) | Stator-Blindleistung des Generators (avg) | Potencia reactiva del estátor del generador (avg) | Moc bierna stojana generatora (avg) | Reactive power at generator stator | VAr | VAr | Average | Double | 10 minute tag
WGEN.SttVAr_10m_Max | #N/A | WGEN. | SttVAr_10m_Max | Generator stator reactive power (max) | Stator-Blindleistung des Generators (max) | Potencia reactiva del estátor del generador (max) | Moc bierna stojana generatora (max) | Reactive power at generator stator | VAr | VAr | Maximum | Double | 10 minute tag
WGEN.SttVAr_10m_Min | #N/A | WGEN. | SttVAr_10m_Min | Generator stator reactive power (min) | Stator-Blindleistung des Generators (min) | Potencia reactiva del estátor del generador (min) | Moc bierna stojana generatora (min) | Reactive power at generator stator | VAr | VAr | Minimum | Double | 10 minute tag
WGEN.SttVAr_10m_Std | #N/A | WGEN. | SttVAr_10m_Std | Generator stator reactive power (std) | Stator-Blindleistung des Generators (std) | Potencia reactiva del estátor del generador (std) | Moc bierna stojana generatora (std) | Reactive power at generator stator | VAr | VAr | Standard Deviation | Double | 10 minute tag
WGEN.SttW | #N/A | WGEN. | SttW | Generator stator Active power | Stator-Wirkleistung des Generators | Potencia activa del estátor del generador | Stojan generatora Moc czynna | Active power at generator stator | W | W | Live Value | Double | Live Value
WGEN.SttW_10m_Avg | #N/A | WGEN. | SttW_10m_Avg | Generator stator Active power (avg) | Stator-Wirkleistung des Generators (avg) | Potencia activa del estátor del generador (avg) | Stojan generatora Moc czynna (avg) | Active power at generator stator | W | W | Average | Double | 10 minute tag
WGEN.SttW_10m_Max | #N/A | WGEN. | SttW_10m_Max | Generator stator Active power (max) | Stator-Wirkleistung des Generators (max) | Potencia activa del estátor del generador (max) | Stojan generatora Moc czynna (max) | Active power at generator stator | W | W | Maximum | Double | 10 minute tag
WGEN.SttW_10m_Min | #N/A | WGEN. | SttW_10m_Min | Generator stator Active power (min) | Stator-Wirkleistung des Generators (min) | Potencia activa del estátor del generador (min) | Stojan generatora Moc czynna (min) | Active power at generator stator | W | W | Minimum | Double | 10 minute tag
WGEN.SttW_10m_Std | #N/A | WGEN. | SttW_10m_Std | Generator stator Active power (std) | Stator-Wirkleistung des Generators (std) | Potencia activa del estátor del generador (std) | Stojan generatora Moc czynna (std) | Active power at generator stator | W | W | Standard Deviation | Double | 10 minute tag
WGEN.VAr | WGEN.VAr | WGEN. | VAr | Generator reactive power | Generatorblindleistung | Potencia reactiva del generador | Moc bierna generatora | Reactive power at generator | VAr | VAr | Live Value | Double | Live Value
WGEN.VAr_10m_Avg | #N/A | WGEN. | VAr_10m_Avg | Generator reactive power (avg) | Generatorblindleistung (avg) | Potencia reactiva del generador (avg) | Moc bierna generatora (avg) | Reactive power at generator | VAr | VAr | Average | Double | 10 minute tag
WGEN.VAr_10m_Max | #N/A | WGEN. | VAr_10m_Max | Generator reactive power (max) | Generatorblindleistung (max) | Potencia reactiva del generador (max) | Moc bierna generatora (max) | Reactive power at generator | VAr | VAr | Maximum | Double | 10 minute tag
WGEN.VAr_10m_Min | #N/A | WGEN. | VAr_10m_Min | Generator reactive power (min) | Generatorblindleistung (min) | Potencia reactiva del generador (min) | Moc bierna generatora (min) | Reactive power at generator | VAr | VAr | Minimum | Double | 10 minute tag
WGEN.VAr_10m_Std | #N/A | WGEN. | VAr_10m_Std | Generator reactive power (std) | Generatorblindleistung (std) | Potencia reactiva del generador (std) | Moc bierna generatora (std) | Reactive power at generator | VAr | VAr | Standard Deviation | Double | 10 minute tag
WGEN.W | WGEN.W | WGEN. | W | Generator Active power | Generatorwirkleistung | Potencia activa del generador | Generator Moc czynna | Active power at generator | W | W | Live Value | Double | Live Value
WGEN.W_10m_Avg | #N/A | WGEN. | W_10m_Avg | Generator Active power (avg) | Generatorwirkleistung (avg) | Potencia activa del generador (avg) | Generator Moc czynna (avg) | Active power at generator | W | W | Average | Double | 10 minute tag
WGEN.W_10m_Max | #N/A | WGEN. | W_10m_Max | Generator Active power (max) | Generatorwirkleistung (max) | Potencia activa del generador (max) | Generator Moc czynna (max) | Active power at generator | W | W | Maximum | Double | 10 minute tag
WGEN.W_10m_Min | #N/A | WGEN. | W_10m_Min | Generator Active power (min) | Generatorwirkleistung (min) | Potencia activa del generador (min) | Generator Moc czynna (min) | Active power at generator | W | W | Minimum | Double | 10 minute tag
WGEN.W_10m_Std | #N/A | WGEN. | W_10m_Std | Generator Active power (std) | Generatorwirkleistung (std) | Potencia activa del generador (std) | Generator Moc czynna (std) | Active power at generator | W | W | Standard Deviation | Double | 10 minute tag
WGEN.WtrPmpCnt_10m_End | #N/A | WGEN. | WtrPmpCnt_10m_End | Number of activations of generator cooling water pump (end) | Anzahl der Aktivierungen der Kühlwasserpumpe des Generators (end) | Número de activaciones de la bomba de agua de refrigeración del generador (end) | Liczba aktywacji generatora pompy wody chłodzącej (end) | Number of activations of generator cooling water pump | count | Count | Endvalue | Long | 10 minute tag
WGEN.WtrPmpTms_10m_End | #N/A | WGEN. | WtrPmpTms_10m_End | Time generator cooling water pump has been activated (end) | Zeit, in der die Kühlwasserpumpe des Generators aktiviert wurde (end) | Tiempo que la bomba de agua de refrigeración del generador ha estado activada (end) | Czas aktywacji pompy wody chłodz. gen. (end) | Time generator cooling water pump has been activated | s | seconds | Endvalue | Long | 10 minute tag
WGEN1.DmdVArh | #N/A | WGEN1. | DmdVArh | Reactive energy consumed by generator 1 | Von Generator 1 verbrauchte Blindenergie | Energía reactiva consumida por el generador 1 | Energia bierna zużywana przez generator 1 | Reactive energy consumed by generator G1 | VArh | VArh | Total Counter | Double | 10 minute tag
WGEN1.DmdVArh_10m_End | #N/A | WGEN1. | DmdVArh_10m_End | Reactive energy consumed by generator 1 (end) | Von Generator 1 verbrauchte Blindenergie (end) | Energía reactiva consumida por el generador 1 (end) | Energia bierna zużywana przez generator 1 (end) | Reactive energy consumed by generator G1 | VArh | VArh | Endvalue | Double | 10 minute tag
WGEN1.DmdVArh_10m_Sum | #N/A | WGEN1. | DmdVArh_10m_Sum | Reactive energy consumed by generator 1 (sum) | Von Generator 1 verbrauchte Blindenergie (sum) | Energía reactiva consumida por el generador 1 (sum) | Energia bierna zużywana przez generator 1 (sum) | Reactive energy consumed by generator G1 | VArh | VArh | Summation | Double | 10 minute tag
WGEN1.DmdVArh_Mly_Sum | #N/A | WGEN1. | DmdVArh_Mly_Sum | Reactive energy consumed by generator 1 (sum) | Von Generator 1 verbrauchte Blindenergie (sum) | Energía reactiva consumida por el generador 1 (sum) | Energia bierna zużywana przez generator 1 (sum) | Reactive energy consumed by generator G1 | VArh | VArh | Summation | Double | Monthly tag
WGEN1.DmdWh | #N/A | WGEN1. | DmdWh | Active energy consumed by generator 1 | Von Generator 1 verbrauchte Wirkenergie | Energía activa consumida por el generador 1 | Energia czynna zużywana przez generator 1 | Active (real) energy consumed by generator G1 | Wh | Wh | Total Counter | Double | Live Value
WGEN1.DmdWh_10m_End | #N/A | WGEN1. | DmdWh_10m_End | Active energy consumed by generator 1 (end) | Von Generator 1 verbrauchte Wirkenergie (end) | Energía activa consumida por el generador 1 (end) | Energia czynna zużywana przez generator 1 (end) | Active (real) energy consumed by generator G1 | Wh | Wh | Endvalue | Double | 10 minute tag
WGEN1.DmdWh_10m_Sum | #N/A | WGEN1. | DmdWh_10m_Sum | Active energy consumed by generator 1 (sum) | Von Generator 1 verbrauchte Wirkenergie (sum) | Energía activa consumida por el generador 1 (sum) | Energia czynna zużywana przez generator 1 (sum) | Active (real) energy consumed by generator G1 | Wh | Wh | Summation | Double | 10 minute tag
WGEN1.DmdWh_Mly_Sum | #N/A | WGEN1. | DmdWh_Mly_Sum | Active energy consumed by generator 1 (sum) | Von Generator 1 verbrauchte Wirkenergie (sum) | Energía activa consumida por el generador 1 (sum) | Energia czynna zużywana przez generator 1 (sum) | Active (real) energy consumed by generator G1 | Wh | Wh | Summation | Double | Monthly tag
WGEN1.GnOpSt | #N/A | WGEN1. | GnOpSt | Generator 1 State | Generator 1 Status | Estado del generador 1 | Generator 1 Stan | Generator 1 state | Enum | Enum | Live Value | Long | Live Value
WGEN1.OpTms | #N/A | WGEN1. | OpTms | Time generator 1 in production | Zeit Generator 1 in Betrieb | Tiempo del generador 1 en producción | Generator czasu 1 w produkcji | Time generator G1 production time i.e. time generator G1 has been producing power, or ready but low wind, used for real availability | s | seconds | Total Counter | Long | Live Value
WGEN1.OpTms_10m_End | #N/A | WGEN1. | OpTms_10m_End | Time with generator 1 on grid (end) | Zeit mit Generator 1 am Netz (end) | Tiempo con el generador 1 en la red eléctrica (end) | Czas z generatorem 1 w sieci (end) | Time with generator G1 on grid | s | seconds | Endvalue | Long | 10 minute tag
WGEN1.OpTms_10m_Sum | #N/A | WGEN1. | OpTms_10m_Sum | Time with generator 1 on grid (sum) | Zeit mit Generator 1 am Netz (sum) | Tiempo con el generador 1 en la red eléctrica (sum) | Czas z generatorem 1 w sieci (sum) | Time with generator G1 on grid in each 10 minute period i.e. 0-600 seconds | s | seconds | Summation | Long | 10 minute tag
WGEN1.OpTms_Dly_Sum | #N/A | WGEN1. | OpTms_Dly_Sum | Time with generator 1 on grid (sum) | Zeit mit Generator 1 am Netz (sum) | Tiempo con el generador 1 en la red eléctrica (sum) | Czas z generatorem 1 w sieci (sum) | Time with generator G1 on grid in each Daily period i.e. 0-86400 seconds | s | seconds | Summation | Long | Daily tag
WGEN1.OpTms_Mly_Sum | #N/A | WGEN1. | OpTms_Mly_Sum | Time with generator 1 on grid (sum) | Zeit mit Generator 1 am Netz (sum) | Tiempo con el generador 1 en la red eléctrica (sum) | Czas z generatorem 1 w sieci (sum) | Time with generator G1 on grid in each Monthly period | s | seconds | Summation | Long | Monthly tag
WGEN1.SttTmp | #N/A | WGEN1. | SttTmp | Generator 1 Temp | Generator 1 Temperatur | Temperatura del generador 1 | Generator 1 Temp | Generator temperature generator G1 | deg_c | °C | Live Value | Double | Live Value
WGEN1.SttTmp_10m_Avg | #N/A | WGEN1. | SttTmp_10m_Avg | Generator 1 Temp (avg) | Generator 1 Temperatur (avg) | Temperatura del generador 1 (avg) | Generator 1 Temp (avg) | Generator temperature generator G1 | deg_c | °C | Average | Double | 10 minute tag
WGEN1.SttTmp_10m_Max | #N/A | WGEN1. | SttTmp_10m_Max | Generator 1 Temp (max) | Generator 1 Temperatur (max) | Temperatura del generador 1 (max) | Generator 1 Temp (max) | Generator temperature generator G1 | deg_c | °C | Maximum | Double | 10 minute tag
WGEN1.SttTmp_10m_Min | #N/A | WGEN1. | SttTmp_10m_Min | Generator 1 Temp (min) | Generator 1 Temperatur (min) | Temperatura del generador 1 (min) | Generator 1 Temp (min) | Generator temperature generator G1 | deg_c | °C | Minimum | Double | 10 minute tag
WGEN1.SttTmp_10m_Std | #N/A | WGEN1. | SttTmp_10m_Std | Generator 1 Temp (std) | Generator 1 Temperatur (std) | Temperatura del generador 1 (std) | Generator 1 Temp (std) | Generator temperature generator G1 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN1.SttTmp1 | #N/A | WGEN1. | SttTmp1 | Generator 1 Stator L1 Temp | Generator 1 Stator L1 Temperatur | Temperatura del estátor L1 del generador 1 | Generator 1 Stojan L1 Temp | Generator stator phase L1 temperature generator G1 | deg_c | °C | Live Value | Double | Live Value
WGEN1.SttTmp1_10m_Avg | #N/A | WGEN1. | SttTmp1_10m_Avg | Generator 1 Stator L1 Temp (avg) | Generator 1 Stator L1 Temperatur (avg) | Temperatura del estátor L1 del generador 1 (avg) | Generator 1 Stojan L1 Temp (avg) | Generator stator phase L1 temperature generator G1 | deg_c | °C | Average | Double | 10 minute tag
WGEN1.SttTmp1_10m_Max | #N/A | WGEN1. | SttTmp1_10m_Max | Generator 1 Stator L1 Temp (max) | Generator 1 Stator L1 Temperatur (max) | Temperatura del estátor L1 del generador 1 (max) | Generator 1 Stojan L1 Temp (max) | Generator stator phase L1 temperature generator G1 | deg_c | °C | Maximum | Double | 10 minute tag
WGEN1.SttTmp1_10m_Min | #N/A | WGEN1. | SttTmp1_10m_Min | Generator 1 Stator L1 Temp (min) | Generator 1 Stator L1 Temperatur (min) | Temperatura del estátor L1 del generador 1 (min) | Generator 1 Stojan L1 Temp (min) | Generator stator phase L1 temperature generator G1 | deg_c | °C | Minimum | Double | 10 minute tag
WGEN1.SttTmp1_10m_Std | #N/A | WGEN1. | SttTmp1_10m_Std | Generator 1 Stator L1 Temp (std) | Generator 1 Stator L1 Temperatur (std) | Temperatura del estátor L1 del generador 1 (std) | Generator 1 Stojan L1 Temp (std) | Generator stator phase L1 temperature generator G1 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN1.SttTmp2 | #N/A | WGEN1. | SttTmp2 | Generator 1 Stator L2 Temp | Generator 1 Stator L2 Temperatur | Temperatura del estátor L2 del generador 1 | Generator 1 Stojan L2 Temp | Generator stator phase L2 temperature generator G1 | deg_c | °C | Live Value | Double | Live Value
WGEN1.SttTmp2_10m_Avg | #N/A | WGEN1. | SttTmp2_10m_Avg | Generator 1 Stator L2 Temp (avg) | Generator 1 Stator L2 Temperatur (avg) | Temperatura del estátor L2 del generador 1 (avg) | Generator 1 Stojan L2 Temp (avg) | Generator stator phase L2 temperature generator G1 | deg_c | °C | Average | Double | 10 minute tag
WGEN1.SttTmp2_10m_Max | #N/A | WGEN1. | SttTmp2_10m_Max | Generator 1 Stator L2 Temp (max) | Generator 1 Stator L2 Temperatur (max) | Temperatura del estátor L2 del generador 1 (max) | Generator 1 Stojan L2 Temp (max) | Generator stator phase L2 temperature generator G1 | deg_c | °C | Maximum | Double | 10 minute tag
WGEN1.SttTmp2_10m_Min | #N/A | WGEN1. | SttTmp2_10m_Min | Generator 1 Stator L2 Temp (min) | Generator 1 Stator L2 Temperatur (min) | Temperatura del estátor L2 del generador 1 (min) | Generator 1 Stojan L2 Temp (min) | Generator stator phase L2 temperature generator G1 | deg_c | °C | Minimum | Double | 10 minute tag
WGEN1.SttTmp2_10m_Std | #N/A | WGEN1. | SttTmp2_10m_Std | Generator 1 Stator L2 Temp (std) | Generator 1 Stator L2 Temperatur (std) | Temperatura del estátor L2 del generador 1 (std) | Generator 1 Stojan L2 Temp (std) | Generator stator phase L2 temperature generator G1 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN1.SttTmp3 | #N/A | WGEN1. | SttTmp3 | Generator 1 Stator L3 Temp | Generator 1 Stator L3 Temperatur | Temperatura del estátor L3 del generador 1 | Generator 1 Stojan L3 Temp | Generator stator phase L3 temperature generator G1 | deg_c | °C | Live Value | Double | Live Value
WGEN1.SttTmp3_10m_Avg | #N/A | WGEN1. | SttTmp3_10m_Avg | Generator 1 Stator L3 Temp (avg) | Generator 1 Stator L3 Temperatur (avg) | Temperatura del estátor L3 del generador 1 (avg) | Generator 1 Stojan L3 Temp (avg) | Generator stator phase L3 temperature generator G1 | deg_c | °C | Average | Double | 10 minute tag
WGEN1.SttTmp3_10m_Max | #N/A | WGEN1. | SttTmp3_10m_Max | Generator 1 Stator L3 Temp (max) | Generator 1 Stator L3 Temperatur (max) | Temperatura del estátor L3 del generador 1 (max) | Generator 1 Stojan L3 Temp (max) | Generator stator phase L3 temperature generator G1 | deg_c | °C | Maximum | Double | 10 minute tag
WGEN1.SttTmp3_10m_Min | #N/A | WGEN1. | SttTmp3_10m_Min | Generator 1 Stator L3 Temp (min) | Generator 1 Stator L3 Temperatur (min) | Temperatura del estátor L3 del generador 1 (min) | Generator 1 Stojan L3 Temp (min) | Generator stator phase L3 temperature generator G1 | deg_c | °C | Minimum | Double | 10 minute tag
WGEN1.SttTmp3_10m_Std | #N/A | WGEN1. | SttTmp3_10m_Std | Generator 1 Stator L3 Temp (std) | Generator 1 Stator L3 Temperatur (std) | Temperatura del estátor L3 del generador 1 (std) | Generator 1 Stojan L3 Temp (std) | Generator stator phase L3 temperature generator G1 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN1.SupVArh | #N/A | WGEN1. | SupVArh | Reactive energy supplied by generator 1 | Von Generator 1 gelieferte Blindenergie | Energía reactiva suministrada por el generador 1 | Energia bierna dostar. przez generator 1 | Reactive energy supplied by generator G1 | VArh | VArh | Total Counter | Double | 10 minute tag
WGEN1.SupVArh_10m_End | #N/A | WGEN1. | SupVArh_10m_End | Reactive energy supplied by generator 1 (end) | Von Generator 1 gelieferte Blindenergie (end) | Energía reactiva suministrada por el generador 1 (end) | Energia bierna dostar. przez generator 1 (end) | Reactive energy supplied by generator G1 | VArh | VArh | Endvalue | Double | 10 minute tag
WGEN1.SupVArh_10m_Sum | #N/A | WGEN1. | SupVArh_10m_Sum | Reactive energy supplied by generator 1 (sum) | Von Generator 1 gelieferte Blindenergie (sum) | Energía reactiva suministrada por el generador 1 (sum) | Energia bierna dostar. przez generator 1 (sum) | Reactive energy supplied by generator G1 | VArh | VArh | Summation | Double | 10 minute tag
WGEN1.SupVArh_Mly_Sum | #N/A | WGEN1. | SupVArh_Mly_Sum | Reactive energy supplied by generator 1 (sum) | Von Generator 1 gelieferte Blindenergie (sum) | Energía reactiva suministrada por el generador 1 (sum) | Energia bierna dostar. przez generator 1 (sum) | Reactive energy supplied by generator G1 | VArh | VArh | Summation | Double | Monthly tag
WGEN1.SupWh | #N/A | WGEN1. | SupWh | Active energy supply by generator 1 | Von Generator 1 gelieferte Wirkenergie | Energía activa suministrada por el generador 1 | Energia czynna dostar. przez generator 1 | Active (real) energy supply by generator G1 | Wh | Wh | Total Counter | Double | Live Value
WGEN1.SupWh_10m_End | #N/A | WGEN1. | SupWh_10m_End | Active energy supply by generator 1 (end) | Von Generator 1 gelieferte Wirkenergie (end) | Energía activa suministrada por el generador 2 (end) | Energia czynna dostar. przez generator 1 (end) | Active (real) energy supply by generator G1 | Wh | Wh | Endvalue | Double | 10 minute tag
WGEN1.SupWh_10m_Sum | #N/A | WGEN1. | SupWh_10m_Sum | Active energy supply by generator 1 (sum) | Von Generator 1 gelieferte Wirkenergie (sum) | Energía activa suministrada por el generador 3 (sum) | Energia czynna dostar. przez generator 1 (sum) | Active (real) energy supply by generator G1 | Wh | Wh | Summation | Double | 10 minute tag
WGEN1.SupWh_Mly_Sum | #N/A | WGEN1. | SupWh_Mly_Sum | Active energy supply by generator 1 (sum) | Von Generator 1 gelieferte Wirkenergie (sum) | Energía activa suministrada por el generador 4 (sum) | Energia czynna dostar. przez generator 1 (sum) | Active (real) energy supply by generator G1 | Wh | Wh | Summation | Double | Monthly tag
WGEN1.TotVArh | #N/A | WGEN1. | TotVArh | Total reactive energy production generator 1 | Gesamte Blindenergieerzeugung Generator 1 | Energía reactiva total producida por el generador 1 | Całk. energia bierna gen. 1 | Total (net) reactive energy production generator G1 | VArh | VArh | Total Counter | Double | 10 minute tag
WGEN1.TotVArh_10m_End | #N/A | WGEN1. | TotVArh_10m_End | Total reactive energy production generator 1 (end) | Gesamte Blindenergieerzeugung Generator 1 (end) | Energía reactiva total producida por el generador 1 (end) | Całk. energia bierna gen. 1 (end) | Total (net) reactive energy production generator G1 | VArh | VArh | Endvalue | Double | 10 minute tag
WGEN1.TotVArh_10m_Sum | #N/A | WGEN1. | TotVArh_10m_Sum | Total reactive energy production generator 1 (sum) | Gesamte Blindenergieerzeugung Generator 1 (sum) | Energía reactiva total producida por el generador 1 (sum) | Całk. energia bierna gen. 1 (sum) | Total (net) reactive energy production generator G1 | VArh | VArh | Summation | Double | 10 minute tag
WGEN1.TotVArh_Mly_Sum | #N/A | WGEN1. | TotVArh_Mly_Sum | Total reactive energy production generator 1 (sum) | Gesamte Blindenergieerzeugung Generator 1 (sum) | Energía reactiva total producida por el generador 1 (sum) | Całk. energia bierna gen. 1 (sum) | Total (net) reactive energy production generator G1 | VArh | VArh | Summation | Double | Monthly tag
WGEN1.TotWh | #N/A | WGEN1. | TotWh | Total active energy production generator 1 | Gesamte Wirkenergieerzeugung Generator 1 | Energía activa total producida por el generador 1 | Całk. energia czynna gen. 1 | Total (net) active energy production i.e. produced-consumed energy G1 | Wh | Wh | Total Counter | Double | Live Value
WGEN1.TotWh_10m_End | #N/A | WGEN1. | TotWh_10m_End | Total active energy production generator 1 (end) | Gesamte Wirkenergieerzeugung Generator 1 (end) | Energía activa total producida por el generador 1 (end) | Całk. energia czynna gen. 1 (end) | Total (net) active energy production i.e. produced-consumed energy G1 | Wh | Wh | Endvalue | Double | 10 minute tag
WGEN1.TotWh_10m_Sum | #N/A | WGEN1. | TotWh_10m_Sum | Total active energy production generator 1 (sum) | Gesamte Wirkenergieerzeugung Generator 1 (sum) | Energía activa total producida por el generador 1 (sum) | Całk. energia czynna gen. 1 (sum) | Total (net) active energy production i.e. produced-consumed energy G1 | Wh | Wh | Summation | Double | 10 minute tag
WGEN1.TotWh_Mly_Sum | #N/A | WGEN1. | TotWh_Mly_Sum | Total active energy production generator 1 (sum) | Gesamte Wirkenergieerzeugung Generator 1 (sum) | Energía activa total producida por el generador 1 (sum) | Całk. energia czynna gen. 1 (sum) | Total (net) active energy production i.e. produced-consumed energy G1 | Wh | Wh | Summation | Double | Monthly tag
WGEN2.DmdVArh | #N/A | WGEN2. | DmdVArh | Reactive energy consumed by generator 2 | Von Generator 2 verbrauchte Blindenergie | Energía reactiva consumida por el generador 2 | Energia bierna zużywana przez generator 2 | Reactive energy consumed by generator G2 | VArh | VArh | Total Counter | Double | 10 minute tag
WGEN2.DmdVArh_10m_End | #N/A | WGEN2. | DmdVArh_10m_End | Reactive energy consumed by generator 2 (end) | Von Generator 2 verbrauchte Blindenergie (end) | Energía reactiva consumida por el generador 2 (end) | Energia bierna zużywana przez generator 2 (end) | Reactive energy consumed by generator G2 | VArh | VArh | Endvalue | Double | 10 minute tag
WGEN2.DmdVArh_10m_Sum | #N/A | WGEN2. | DmdVArh_10m_Sum | Reactive energy consumed by generator 2 (sum) | Von Generator 2 verbrauchte Blindenergie (sum) | Energía reactiva consumida por el generador 2 (sum) | Energia bierna zużywana przez generator 2 (sum) | Reactive energy consumed by generator G2 | VArh | VArh | Summation | Double | 10 minute tag
WGEN2.DmdVArh_Mly_Sum | #N/A | WGEN2. | DmdVArh_Mly_Sum | Reactive energy consumed by generator 2 (sum) | Von Generator 2 verbrauchte Blindenergie (sum) | Energía reactiva consumida por el generador 2 (sum) | Energia bierna zużywana przez generator 2 (sum) | Reactive energy consumed by generator G2 | VArh | VArh | Summation | Double | Monthly tag
WGEN2.DmdWh | #N/A | WGEN2. | DmdWh | Active energy consumed by generator 2 | Von Generator 2 verbrauchte Wirkenergie | Energía activa consumida por el generador 2 | Energia czynna zużywana przez generator 2 | Active (real) energy consumed by generator G2 | Wh | Wh | Total Counter | Double | Live Value
WGEN2.DmdWh_10m_End | #N/A | WGEN2. | DmdWh_10m_End | Active energy consumed by generator 2 (end) | Von Generator 2 verbrauchte Wirkenergie (end) | Energía activa consumida por el generador 2 (end) | Energia czynna zużywana przez generator 2 (end) | Active (real) energy consumed by generator G2 | Wh | Wh | Endvalue | Double | 10 minute tag
WGEN2.DmdWh_10m_Sum | #N/A | WGEN2. | DmdWh_10m_Sum | Active energy consumed by generator 2 (sum) | Von Generator 2 verbrauchte Wirkenergie (sum) | Energía activa consumida por el generador 2 (sum) | Energia czynna zużywana przez generator 2 (sum) | Active (real) energy consumed by generator G2 | Wh | Wh | Summation | Double | 10 minute tag
WGEN2.DmdWh_Mly_Sum | #N/A | WGEN2. | DmdWh_Mly_Sum | Active energy consumed by generator 2 (sum) | Von Generator 2 verbrauchte Wirkenergie (sum) | Energía activa consumida por el generador 2 (sum) | Energia czynna zużywana przez generator 2 (sum) | Active (real) energy consumed by generator G2 | Wh | Wh | Summation | Double | Monthly tag
WGEN2.GnOpSt | #N/A | WGEN2. | GnOpSt | Generator 2 State | Generator 2 Status | Estado del generador 2 | Generator 2 Stan | Generator 2 state | Enum | Enum | Live Value | Long | Live Value
WGEN2.OpTms | #N/A | WGEN2. | OpTms | Time generator 2 in production | Zeit Generator 2 in Betrieb | Tiempo del generador 2 en producción | Generator czasu 2 w produkcji | Time generator g2 production time i.e. time generator g2 has been producing power, or ready but low wind, used with real availability | s | seconds | Total Counter | Long | Live Value
WGEN2.OpTms_10m_End | #N/A | WGEN2. | OpTms_10m_End | Time with generator 2 on grid (end) | Zeit mit Generator 2 am Netz (end) | Tiempo con el generador 2 en la red eléctrica (end) | Czas z generatorem 2 w sieci (end) | Time with generator g2 on grid | s | seconds | Endvalue | Long | 10 minute tag
WGEN2.OpTms_10m_Sum | #N/A | WGEN2. | OpTms_10m_Sum | Time with generator 2 on grid (sum) | Zeit mit Generator 2 am Netz (sum) | Tiempo con el generador 2 en la red eléctrica (sum) | Czas z generatorem 2 w sieci (sum) | Time with generator g2 on grid in each 10 minute period i.e. 0-600 seconds | s | seconds | Summation | Long | 10 minute tag
WGEN2.OpTms_Dly_Sum | #N/A | WGEN2. | OpTms_Dly_Sum | Time with generator 2 on grid (sum) | Zeit mit Generator 2 am Netz (sum) | Tiempo con el generador 2 en la red eléctrica (sum) | Czas z generatorem 2 w sieci (sum) | Time with generator g2 on grid in each Daily period i.e. 0-86400 seconds | s | seconds | Summation | Long | Daily tag
WGEN2.OpTms_Mly_Sum | #N/A | WGEN2. | OpTms_Mly_Sum | Time with generator 2 on grid (sum) | Zeit mit Generator 2 am Netz (sum) | Tiempo con el generador 2 en la red eléctrica (sum) | Czas z generatorem 2 w sieci (sum) | Time with generator g2 on grid in each Monthly period | s | seconds | Summation | Long | Monthly tag
WGEN2.SttTmp | #N/A | WGEN2. | SttTmp | Generator 2 Temp | Generator 2 Temperatur | Temperatura del generador 2 | Generator 2 Temp | Generator temperature generator g2 | deg_c | °C | Live Value | Double | Live Value
WGEN2.SttTmp_10m_Avg | #N/A | WGEN2. | SttTmp_10m_Avg | Generator 2 Temp (avg) | Generator 2 Temperatur (avg) | Temperatura del generador 2 (avg) | Generator 2 Temp (avg) | Generator temperature generator g2 | deg_c | °C | Average | Double | 10 minute tag
WGEN2.SttTmp_10m_Max | #N/A | WGEN2. | SttTmp_10m_Max | Generator 2 Temp (max) | Generator 2 Temperatur (max) | Temperatura del generador 2 (max) | Generator 2 Temp (max) | Generator temperature generator g2 | deg_c | °C | Maximum | Double | 10 minute tag
WGEN2.SttTmp_10m_Min | #N/A | WGEN2. | SttTmp_10m_Min | Generator 2 Temp (min) | Generator 2 Temperatur (min) | Temperatura del generador 2 (min) | Generator 2 Temp (min) | Generator temperature generator g2 | deg_c | °C | Minimum | Double | 10 minute tag
WGEN2.SttTmp_10m_Std | #N/A | WGEN2. | SttTmp_10m_Std | Generator 2 Temp (std) | Generator 2 Temperatur (std) | Temperatura del generador 2 (std) | Generator 2 Temp (std) | Generator temperature generator g2 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN2.SttTmp1 | #N/A | WGEN2. | SttTmp1 | Generator 2 Stator L1 Temp | Generator 2 Stator L1 Temperatur | Temperatura del estátor L1 del generador 2 | Generator 2 Stojan L1 Temp | Generator stator phase L1 temperature generator g2 | deg_c | °C | Live Value | Double | Live Value
WGEN2.SttTmp1_10m_Avg | #N/A | WGEN2. | SttTmp1_10m_Avg | Generator 2 Stator L1 Temp (avg) | Generator 2 Stator L1 Temperatur (avg) | Temperatura del estátor L1 del generador 2 (avg) | Generator 2 Stojan L1 Temp (avg) | Generator stator phase L1 temperature generator g2 | deg_c | °C | Average | Double | 10 minute tag
WGEN2.SttTmp1_10m_Max | #N/A | WGEN2. | SttTmp1_10m_Max | Generator 2 Stator L1 Temp (max) | Generator 2 Stator L1 Temperatur (max) | Temperatura del estátor L1 del generador 2 (max) | Generator 2 Stojan L1 Temp (max) | Generator stator phase L1 temperature generator g2 | deg_c | °C | Maximum | Double | 10 minute tag
WGEN2.SttTmp1_10m_Min | #N/A | WGEN2. | SttTmp1_10m_Min | Generator 2 Stator L1 Temp (min) | Generator 2 Stator L1 Temperatur (min) | Temperatura del estátor L1 del generador 2 (min) | Generator 2 Stojan L1 Temp (min) | Generator stator phase L1 temperature generator g2 | deg_c | °C | Minimum | Double | 10 minute tag
WGEN2.SttTmp1_10m_Std | #N/A | WGEN2. | SttTmp1_10m_Std | Generator 2 Stator L1 Temp (std) | Generator 2 Stator L1 Temperatur (std) | Temperatura del estátor L1 del generador 2 (std) | Generator 2 Stojan L1 Temp (std) | Generator stator phase L1 temperature generator g2 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN2.SttTmp2 | #N/A | WGEN2. | SttTmp2 | Generator 2 Stator L2 Temp | Generator 2 Stator L2 Temperatur | Temperatura del estátor L2 del generador 2 | Generator 2 Stojan L2 Temp | Generator stator phase L2 temperature generator g2 | deg_c | °C | Live Value | Double | Live Value
WGEN2.SttTmp2_10m_Avg | #N/A | WGEN2. | SttTmp2_10m_Avg | Generator 2 Stator L2 Temp (avg) | Generator 2 Stator L2 Temperatur (avg) | Temperatura del estátor L2 del generador 2 (avg) | Generator 2 Stojan L2 Temp (avg) | Generator stator phase L2 temperature generator g2 | deg_c | °C | Average | Double | 10 minute tag
WGEN2.SttTmp2_10m_Max | #N/A | WGEN2. | SttTmp2_10m_Max | Generator 2 Stator L2 Temp (max) | Generator 2 Stator L2 Temperatur (max) | Temperatura del estátor L2 del generador 2 (max) | Generator 2 Stojan L2 Temp (max) | Generator stator phase L2 temperature generator g2 | deg_c | °C | Maximum | Double | 10 minute tag
WGEN2.SttTmp2_10m_Min | #N/A | WGEN2. | SttTmp2_10m_Min | Generator 2 Stator L2 Temp (min) | Generator 2 Stator L2 Temperatur (min) | Temperatura del estátor L2 del generador 2 (min) | Generator 2 Stojan L2 Temp (min) | Generator stator phase L2 temperature generator g2 | deg_c | °C | Minimum | Double | 10 minute tag
WGEN2.SttTmp2_10m_Std | #N/A | WGEN2. | SttTmp2_10m_Std | Generator 2 Stator L2 Temp (std) | Generator 2 Stator L2 Temperatur (std) | Temperatura del estátor L2 del generador 2 (std) | Generator 2 Stojan L2 Temp (std) | Generator stator phase L2 temperature generator g2 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN2.SttTmp3 | #N/A | WGEN2. | SttTmp3 | Generator 2 Stator L3 Temp | Generator 2 Stator L3 Temperatur | Temperatura del estátor L3 del generador 2 | Generator 2 Stojan L3 Temp | Generator stator phase L3 temperature generator g2 | deg_c | °C | Live Value | Double | Live Value
WGEN2.SttTmp3_10m_Avg | #N/A | WGEN2. | SttTmp3_10m_Avg | Generator 2 Stator L3 Temp (avg) | Generator 2 Stator L3 Temperatur (avg) | Temperatura del estátor L3 del generador 2 (avg) | Generator 2 Stojan L3 Temp (avg) | Generator stator phase L3 temperature generator g2 | deg_c | °C | Average | Double | 10 minute tag
WGEN2.SttTmp3_10m_Max | #N/A | WGEN2. | SttTmp3_10m_Max | Generator 2 Stator L3 Temp (max) | Generator 2 Stator L3 Temperatur (max) | Temperatura del estátor L3 del generador 2 (max) | Generator 2 Stojan L3 Temp (max) | Generator stator phase L3 temperature generator g2 | deg_c | °C | Maximum | Double | 10 minute tag
WGEN2.SttTmp3_10m_Min | #N/A | WGEN2. | SttTmp3_10m_Min | Generator 2 Stator L3 Temp (min) | Generator 2 Stator L3 Temperatur (min) | Temperatura del estátor L3 del generador 2 (min) | Generator 2 Stojan L3 Temp (min) | Generator stator phase L3 temperature generator g2 | deg_c | °C | Minimum | Double | 10 minute tag
WGEN2.SttTmp3_10m_Std | #N/A | WGEN2. | SttTmp3_10m_Std | Generator 2 Stator L3 Temp (std) | Generator 2 Stator L3 Temperatur (std) | Temperatura del estátor L3 del generador 2 (std) | Generator 2 Stojan L3 Temp (std) | Generator stator phase L3 temperature generator g2 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN2.SupVArh | #N/A | WGEN2. | SupVArh | Reactive energy supplied by generator 2 | Lieferung von Blindenergie durch Generator 2 | Energía reactiva suministrada por el generador 2 | Energia bierna dostar. przez generator 2 | Reactive energy supplied by generator g2 | VArh | VArh | Total Counter | Double | 10 minute tag
WGEN2.SupVArh_10m_End | #N/A | WGEN2. | SupVArh_10m_End | Reactive energy supplied by generator 2 (end) | Lieferung von Blindenergie durch Generator 3 (end) | Energía reactiva suministrada por el generador 2 (end) | Energia bierna dostar. przez generator 2 (end) | Reactive energy supplied by generator g2 | VArh | VArh | Endvalue | Double | 10 minute tag
WGEN2.SupVArh_10m_Sum | #N/A | WGEN2. | SupVArh_10m_Sum | Reactive energy supplied by generator 2 (sum) | Lieferung von Blindenergie durch Generator 4 (sum) | Energía reactiva suministrada por el generador 2 (sum) | Energia bierna dostar. przez generator 2 (sum) | Reactive energy supplied by generator g2 | VArh | VArh | Summation | Double | 10 minute tag
WGEN2.SupVArh_Mly_Sum | #N/A | WGEN2. | SupVArh_Mly_Sum | Reactive energy supplied by generator 2 (sum) | Lieferung von Blindenergie durch Generator 5 (sum) | Energía reactiva suministrada por el generador 2 (sum) | Energia bierna dostar. przez generator 2 (sum) | Reactive energy supplied by generator g2 | VArh | VArh | Summation | Double | Monthly tag
WGEN2.SupWh | #N/A | WGEN2. | SupWh | Active energy supply by generator 2 | Lieferung von Wirkenergie durch Generator 2 | Energía activa suministrada por el generador 2 | Energia czynna dostar. przez generator 2 | Active (real) energy supply by generator g2 | Wh | Wh | Total Counter | Double | Live Value
WGEN2.SupWh_10m_End | #N/A | WGEN2. | SupWh_10m_End | Active energy supply by generator 2 (end) | Lieferung von Wirkenergie durch Generator 3 (end) | Energía activa suministrada por el generador 2 (end) | Energia czynna dostar. przez generator 2 (end) | Active (real) energy supply by generator g2 | Wh | Wh | Endvalue | Double | 10 minute tag
WGEN2.SupWh_10m_Sum | #N/A | WGEN2. | SupWh_10m_Sum | Active energy supply by generator 2 (sum) | Lieferung von Wirkenergie durch Generator 4 (sum) | Energía activa suministrada por el generador 2 (sum) | Energia czynna dostar. przez generator 2 (sum) | Active (real) energy supply by generator g2 | Wh | Wh | Summation | Double | 10 minute tag
WGEN2.SupWh_Mly_Sum | #N/A | WGEN2. | SupWh_Mly_Sum | Active energy supply by generator 2 (sum) | Lieferung von Wirkenergie durch Generator 5 (sum) | Energía activa suministrada por el generador 2 (sum) | Energia czynna dostar. przez generator 2 (sum) | Active (real) energy supply by generator g2 | Wh | Wh | Summation | Double | Monthly tag
WGEN2.TotVArh | #N/A | WGEN2. | TotVArh | Total reactive energy production generator 2 | Gesamte Blindenergieerzeugung Generator 2 | Energía reactiva total producida por el generador 2 | Całk. energia bierna gen. 2 | Total (net) reactive energy production generator g2 | VArh | VArh | Total Counter | Double | Live Value
WGEN2.TotVArh_10m_End | #N/A | WGEN2. | TotVArh_10m_End | Total reactive energy production generator 2 (end) | Gesamte Blindenergieerzeugung Generator 3 (end) | Energía reactiva total producida por el generador 2 (end) | Całk. energia bierna gen. 2 (end) | Total (net) reactive energy production generator g2 | VArh | VArh | Endvalue | Double | 10 minute tag
WGEN2.TotVArh_10m_Sum | #N/A | WGEN2. | TotVArh_10m_Sum | Total reactive energy production generator 2 (sum) | Gesamte Blindenergieerzeugung Generator 4 (sum) | Energía reactiva total producida por el generador 2 (sum) | Całk. energia bierna gen. 2 (sum) | Total (net) reactive energy production generator g2 | VArh | VArh | Summation | Double | 10 minute tag
WGEN2.TotVArh_Mly_Sum | #N/A | WGEN2. | TotVArh_Mly_Sum | Total reactive energy production generator 2 (sum) | Gesamte Blindenergieerzeugung Generator 5 (sum) | Energía reactiva total producida por el generador 2 (sum) | Całk. energia bierna gen. 2 (sum) | Total (net) reactive energy production generator g2 | VArh | VArh | Summation | Double | Monthly tag
WGEN2.TotWh | #N/A | WGEN2. | TotWh | Total active energy production generator 2 | Gesamte Wirkenergieerzeugung Generator 2 | Energía activa total producida por el generador 2 | Całk. energia czynna gen. 2 | Total (net) active energy production i.e. produced-consumed energy g2 | Wh | Wh | Total Counter | Double | Live Value
WGEN2.TotWh_10m_End | #N/A | WGEN2. | TotWh_10m_End | Total active energy production generator 2 (end) | Gesamte Wirkenergieerzeugung Generator 3 (end) | Energía activa total producida por el generador 2 (end) | Całk. energia czynna gen. 2 (end) | Total (net) active energy production i.e. produced-consumed energy g2 | Wh | Wh | Endvalue | Double | 10 minute tag
WGEN2.TotWh_10m_Sum | #N/A | WGEN2. | TotWh_10m_Sum | Total active energy production generator 2 (sum) | Gesamte Wirkenergieerzeugung Generator 4 (sum) | Energía activa total producida por el generador 2 (sum) | Całk. energia czynna gen. 2 (sum) | Total (net) active energy production i.e. produced-consumed energy g2 | Wh | Wh | Summation | Double | 10 minute tag
WGEN2.TotWh_Mly_Sum | #N/A | WGEN2. | TotWh_Mly_Sum | Total active energy production generator 2 (sum) | Gesamte Wirkenergieerzeugung Generator 5 (sum) | Energía activa total producida por el generador 2 (sum) | Całk. energia czynna gen. 2 (sum) | Total (net) active energy production i.e. produced-consumed energy g2 | Wh | Wh | Summation | Double | Monthly tag
WGEN3.SttTmp | #N/A | WGEN3. | SttTmp | Generator 3 Temp | Generator 3 Temperatur | Temperatura del generador 3 | Generator 3 Temp | Generator temperature generator 3 | deg_c | °C | Live Value | Double | Live Value
WGEN3.SttTmp_10m_Avg | #N/A | WGEN3. | SttTmp_10m_Avg | Generator 3 Temp (avg) | Generator 3 Temperatur (avg) | Temperatura del generador 3 (avg) | Generator 3 Temp (avg) | Generator temperature generator 3 | deg_c | °C | Average | Double | 10 minute tag
WGEN3.SttTmp_10m_Max | #N/A | WGEN3. | SttTmp_10m_Max | Generator 3 Temp (max) | Generator 3 Temperatur (max) | Temperatura del generador 3 (max) | Generator 3 Temp (max) | Generator temperature generator 3 | deg_c | °C | Maximum | Double | 10 minute tag
WGEN3.SttTmp_10m_Min | #N/A | WGEN3. | SttTmp_10m_Min | Generator 3 Temp (min) | Generator 3 Temperatur (min) | Temperatura del generador 3 (min) | Generator 3 Temp (min) | Generator temperature generator 3 | deg_c | °C | Minimum | Double | 10 minute tag
WGEN3.SttTmp_10m_Std | #N/A | WGEN3. | SttTmp_10m_Std | Generator 3 Temp (std) | Generator 3 Temperatur (std) | Temperatura del generador 3 (std) | Generator 3 Temp (std) | Generator temperature generator 3 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WGEN4.SttTmp | #N/A | WGEN4. | SttTmp | Generator 4 Temp | Generator 4 Temperatur | Temperatura del generador 4 | Generator 4 Temp | Generator temperature generator 4 | deg_c | °C | Live Value | Double | Live Value
WGEN4.SttTmp_10m_Avg | #N/A | WGEN4. | SttTmp_10m_Avg | Generator 4 Temp (avg) | Generator 4 Temperatur (avg) | Temperatura del generador 4 (avg) | Generator 4 Temp (avg) | Generator temperature generator 4 | deg_c | °C | Average | Double | 10 minute tag
WGEN4.SttTmp_10m_Max | #N/A | WGEN4. | SttTmp_10m_Max | Generator 4 Temp (max) | Generator 4 Temperatur (max) | Temperatura del generador 4 (max) | Generator 4 Temp (max) | Generator temperature generator 4 | deg_c | °C | Maximum | Double | 10 minute tag
WGEN4.SttTmp_10m_Min | #N/A | WGEN4. | SttTmp_10m_Min | Generator 4 Temp (min) | Generator 4 Temperatur (min) | Temperatura del generador 4 (min) | Generator 4 Temp (min) | Generator temperature generator 4 | deg_c | °C | Minimum | Double | 10 minute tag
WGEN4.SttTmp_10m_Std | #N/A | WGEN4. | SttTmp_10m_Std | Generator 4 Temp (std) | Generator 4 Temperatur (std) | Temperatura del generador 4 (std) | Generator 4 Temp (std) | Generator temperature generator 4 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WMET.AirDen | WMET.AirDen | WMET. | AirDen | Air Density | Dichte der Luft | Densidad del aire | Gęstość powietrza | Density of air | Enum | kg/m³ | Live Value | Double | Live Value
WMET.AirDen_10m_Avg | #N/A | WMET. | AirDen_10m_Avg | Air Density (avg) | Dichte der Luft (avg) | Densidad del aire (avg) | Gęstość powietrza (avg) | Density of air | Enum | kg/m³ | Average | Double | 10 minute tag
WMET.AirDen_10m_Max | #N/A | WMET. | AirDen_10m_Max | Air Density (max) | Dichte der Luft (max) | Densidad del aire (max) | Gęstość powietrza (max) | Density of air | Enum | kg/m³ | Maximum | Double | 10 minute tag
WMET.AirDen_10m_Min | #N/A | WMET. | AirDen_10m_Min | Air Density (min) | Dichte der Luft (min) | Densidad del aire (min) | Gęstość powietrza (min) | Density of air | Enum | kg/m³ | Minimum | Double | 10 minute tag
WMET.AirDen_10m_Std | #N/A | WMET. | AirDen_10m_Std | Air Density (std) | Dichte der Luft (std) | Densidad del aire (std) | Gęstość powietrza (std) | Density of air | Enum | kg/m³ | Standard Deviation | Double | 10 minute tag
WMET.Alt | WMET.Alt | WMET. | Alt | Sensor altitude | Sensorhöhe | Sensor de altitud | Wysokość czujnika | Sensor altitude | m | m | Live Value | Double | Live Value
WMET.Ane1Par1_10m_End | #N/A | WMET. | Ane1Par1_10m_End | Parameter m/s/Hz Anemometer 1 (end) | Parameter m/s/Hz Anemometer 1 (end) | Parámetro m/s/Hz del anemómetro 0 (end) | Anemometr parametru m/s/Hz 1 (end) | Parameter m/s/Hz, i.e. factor for calculating m/s from the Hz value from anemometer 1 | Enum | m/s/Hz | Endvalue | Double | 10 minute tag
WMET.Ane1Par2_10m_End | #N/A | WMET. | Ane1Par2_10m_End | Parameter offset in m/s Anemometer 1 (end) | Parameter Offset in m/s Anemometer 1 (end) | Compensación del parámetro en m/s del anemómetro 0 (end) | Przesunięcie parametru w anemometrze m/s 1 (end) | Parameter offset in m/s when calculating m/s from Hz value from anemometer 1 | m_s | m/s | Endvalue | Double | 10 minute tag
WMET.Ane1Par3_10m_End | #N/A | WMET. | Ane1Par3_10m_End | Parameter Corrections factor Anemometer 1 (end) | Parameter Korrekturen Faktor Anemometer 1 (end) | Factor de correcciones del parámetro del anemómetro 0 (end) | Współczynnik korekcji parametrów Anemometr 1 (end) | Parameter Corrections factor (gain) anemometer1 | Enum | Enum | Endvalue | Double | 10 minute tag
WMET.Ane1Par4_10m_End | #N/A | WMET. | Ane1Par4_10m_End | Parameter Corrections offset Anemometer 1 (end) | Parameter Korrekturen Offset Anemometer 1 (end) | Compensación de correcciones del parámetro del anemómetro 0 (end) | Korekty parametrów offset Anemometr 1 (end) | Parameter Corrections offset anemometer1 | Enum | Enum | Endvalue | Double | 10 minute tag
WMET.Ane2Par1_10m_End | #N/A | WMET. | Ane2Par1_10m_End | Parameter m/s/Hz Anemometer 2 (end) | Parameter m/s/Hz Anemometer 2 (end) | Parámetro m/s/Hz del anemómetro 1 (end) | Parametr m/s/Hz Anemometr 2 (end) | Parameter m/s/Hz, i.e. factor for calculating m/s from the Hz value from anemometer 2 | Enum | m/s/Hz | Endvalue | Double | 10 minute tag
WMET.Ane2Par2_10m_End | #N/A | WMET. | Ane2Par2_10m_End | Parameter offset in m/s Anemometer 2 (end) | Parameter Offset in m/s Anemometer 2 (end) | Compensación del parámetro en m/s del anemómetro 1 (end) | Przesunięcie parametru w anemometrze m/s 2 (end) | Parameter offset in m/s when calculating m/s from Hz value from anemometer 2 | m_s | m/s | Endvalue | Double | 10 minute tag
WMET.Ane2Par3_10m_End | #N/A | WMET. | Ane2Par3_10m_End | Parameter Corrections factor Anemometer 2 (end) | Korrekturparameter Faktor Anemometer 2 (end) | Factor de correcciones del parámetro del anemómetro 1 (end) | Współczynnik korekcji parametrów Anemometr 2 (end) | Parameter Corrections factor (gain) anemometer2 | Enum | Enum | Endvalue | Double | 10 minute tag
WMET.Ane2Par4_10m_End | #N/A | WMET. | Ane2Par4_10m_End | Parameter Corrections offset Anemometer 2 (end) | Korrekturparameter Offset Anemometer 2 (end) | Compensación de correcciones del parámetro del anemómetro 1 (end) | Korekty parametrów offset Anemometr 2 (end) | Parameter Corrections offset anemometer2 | Enum | Enum | Endvalue | Double | 10 minute tag
WMET.AneHtCnt | #N/A | WMET. | AneHtCnt | Number of activations of the wind sensor heat | Anzahl der Aktivierungen der Windsensorwärme | Número de activaciones del calentador del sensor de viento | Liczba aktywacji ogrz. czujnika wiatru | Number of activations of the wind sensor heat | count | Count | Total Counter | Long | Live Value
WMET.AneHtCnt_10m_End | #N/A | WMET. | AneHtCnt_10m_End | Number of activations of the wind sensor heat (end) | Anzahl der Aktivierungen der Windsensorwärme (end) | Número de activaciones del calentador del sensor de viento (end) | Liczba aktywacji ogrz. czujnika wiatru (end) | Number of activations of the wind sensor heat | count | Count | Endvalue | Long | 10 minute tag
WMET.AneHtTms | #N/A | WMET. | AneHtTms | Time the wind sensor heat has been activated | Zeit, in der die Windsensorwärme aktiviert wurde | Tiempo que el calentador del sensor de viento ha estado activado | Czas aktywacji ogrz. czujnika wiatru | Time the wind sensor heat has been activated | s | seconds | Total Counter | Long | Live Value
WMET.AneHtTms_10m_End | #N/A | WMET. | AneHtTms_10m_End | Time the wind sensor heat has been activated (end) | Zeit, in der die Windsensorwärme aktiviert wurde (end) | Tiempo que el calentador del sensor de viento ha estado activado (end) | Czas aktywacji ogrz. czujnika wiatru (end) | Time the wind sensor heat has been activated | s | seconds | Endvalue | Long | 10 minute tag
WMET.AneHz1_10m_Avg | #N/A | WMET. | AneHz1_10m_Avg | Anamometer 1 Frequency (avg) | Anamometer 1 Frequenz (avg) | Frecuencia del anemómetro 1 (avg) | Anamometru 1 Częstotliwość (avg) | Frequency from anemometer 1 | Hz | Hz | Average | Double | 10 minute tag
WMET.AneHz2_10m_Avg | #N/A | WMET. | AneHz2_10m_Avg | Anamometer 2 Frequency (avg) | Anamometer 2 Frequenz (avg) | Frecuencia del anemómetro 2 (avg) | Anamometru 2 Częstotliwość (avg) | Frequency from anemometer 2 | Hz | Hz | Average | Double | 10 minute tag
WMET.BatV | #N/A | WMET. | BatV | Logger battery voltage | Batteriespannung des Loggers | Tensión de la batería del registrador | Napięcie akum. rejestratora | Logger battery voltage | V | V | Live Value | Double | Live Value
WMET.BatV_10m_Avg | #N/A | WMET. | BatV_10m_Avg | Logger battery voltage (avg) | Batteriespannung des Loggers (avg) | Tensión de la batería del registrador (avg) | Napięcie akum. rejestratora (avg) | Logger battery voltage | V | V | Average | Double | 10 minute tag
WMET.BatV_10m_Max | #N/A | WMET. | BatV_10m_Max | Logger battery voltage (max) | Batteriespannung des Loggers (max) | Tensión de la batería del registrador (max) | Napięcie akum. rejestratora (max) | Logger battery voltage | V | V | Maximum | Double | 10 minute tag
WMET.BatV_10m_Min | #N/A | WMET. | BatV_10m_Min | Logger battery voltage (min) | Batteriespannung des Loggers (min) | Tensión de la batería del registrador (min) | Napięcie akum. rejestratora (min) | Logger battery voltage | V | V | Minimum | Double | 10 minute tag
WMET.BatV_10m_Std | #N/A | WMET. | BatV_10m_Std | Logger battery voltage (std) | Batteriespannung des Loggers (std) | Tensión de la batería del registrador (std) | Napięcie akum. rejestratora (std) | Logger battery voltage | V | V | Standard Deviation | Double | 10 minute tag
WMET.CloudCvr | WMET.CloudCvr | WMET. | CloudCvr | Cloud Cover level | Bewölkungsgrad | Nivel de nubosidad | Poziom zachmurzenia | Cloud cover level | Enum | Enum | Live Value | Double
WMET.DctInsol | WMET.DctInsol | WMET. | DctInsol | Direct Normal Insolation | Direkte normale Sonneneinstrahlung | Insolación directa normal | Bezpośrednie normalne nasłonecznienie | Direct normal insolation | Enum | Enum | Live Value | Double
WMET.DewPt | WMET.DewPt | WMET. | DewPt | Dew point | Taupunkt | Punto de rocío | Punkt rosy | Dew point |  |  | Live Value | Double
WMET.DffInsol | WMET.DffInsol | WMET. | DffInsol | Diffuse insolation | Diffuse Sonneneinstrahlung | Insolación difusa | Rozproszone nasłonecznienie | Diffuse insolation |  |  | Live Value | Double
WMET.DlDur | WMET.DlDur | WMET. | DlDur | Daylight duration | Tageslichtdauer | Duración de luz diurna | Czas trwania światła dziennego | Daylight duration (time elapsed between sunrise and sunset) | s | seconds | Total Counter | Long | Live Value
WMET.EnvHum | WMET.EnvHum | WMET. | EnvHum | Humidity | Luftfeuchtigkeit | Humedad | Wilgotność | Humidity | percent | percent | Live Value | Double | Live Value
WMET.EnvHum_10m_Avg | #N/A | WMET. | EnvHum_10m_Avg | Humidity (avg) | Luftfeuchtigkeit (avg) | Humedad (avg) | Wilgotność (avg) | Humidity | percent | percent | Average | Double | 10 minute tag
WMET.EnvHum_10m_Max | #N/A | WMET. | EnvHum_10m_Max | Humidity (max) | Luftfeuchtigkeit (max) | Humedad (max) | Wilgotność (max) | Humidity | percent | percent | Maximum | Double | 10 minute tag
WMET.EnvHum_10m_Min | #N/A | WMET. | EnvHum_10m_Min | Humidity (min) | Luftfeuchtigkeit (min) | Humedad (min) | Wilgotność (min) | Humidity | percent | percent | Minimum | Double | 10 minute tag
WMET.EnvHum_10m_Std | #N/A | WMET. | EnvHum_10m_Std | Humidity (std) | Luftfeuchtigkeit (std) | Humedad (std) | Wilgotność (std) | Humidity | percent | percent | Standard Deviation | Double | 10 minute tag
WMET.EnvPres | WMET.EnvPres | WMET. | EnvPres | Barometric Pressure | Barometrischer Druck | Presión barométrica | Ciśnienie barometryczne | Barometric pressure | bar | bar | Live Value | Double | Live Value
WMET.EnvPres_10m_Avg | #N/A | WMET. | EnvPres_10m_Avg | Barometric Pressure (avg) | Barometrischer Druck (avg) | Presión barométrica (avg) | Ciśnienie barometryczne (avg) | Barometric pressure | bar | bar | Average | Double | 10 minute tag
WMET.EnvPres_10m_Max | #N/A | WMET. | EnvPres_10m_Max | Barometric Pressure (max) | Barometrischer Druck (max) | Presión barométrica (max) | Ciśnienie barometryczne (max) | Barometric pressure | bar | bar | Maximum | Double | 10 minute tag
WMET.EnvPres_10m_Min | #N/A | WMET. | EnvPres_10m_Min | Barometric Pressure (min) | Barometrischer Druck (min) | Presión barométrica (min) | Ciśnienie barometryczne (min) | Barometric pressure | bar | bar | Minimum | Double | 10 minute tag
WMET.EnvPres_10m_Std | #N/A | WMET. | EnvPres_10m_Std | Barometric Pressure (std) | Barometrischer Druck (std) | Presión barométrica (std) | Ciśnienie barometryczne (std) | Barometric pressure | bar | bar | Standard Deviation | Double | 10 minute tag
WMET.EnvTmp | WMET.EnvTmp | WMET. | EnvTmp | Ambient Temp | Umgebungstemperatur | Temperatura ambiente | Temp otoczenia | Ambient temperature | deg_c | °C | Live Value | Double | Live Value | Used in standard monitor Presentation
WMET.EnvTmp_10m_Avg | #N/A | WMET. | EnvTmp_10m_Avg | Ambient Temp (avg) | Umgebungstemperatur (avg) | Temperatura ambiente (avg) | Temp otoczenia (avg) | Ambient temperature | deg_c | °C | Average | Double | 10 minute tag | Needed for reports
WMET.EnvTmp_10m_Max | #N/A | WMET. | EnvTmp_10m_Max | Ambient Temp (max) | Umgebungstemperatur (max) | Temperatura ambiente (max) | Temp otoczenia (max) | Ambient temperature | deg_c | °C | Maximum | Double | 10 minute tag | Common tags for analysis
WMET.EnvTmp_10m_Min | #N/A | WMET. | EnvTmp_10m_Min | Ambient Temp (min) | Umgebungstemperatur (min) | Temperatura ambiente (min) | Temp otoczenia (min) | Ambient temperature | deg_c | °C | Minimum | Double | 10 minute tag | Common tags for analysis
WMET.EnvTmp_10m_Std | #N/A | WMET. | EnvTmp_10m_Std | Ambient Temp (std) | Umgebungstemperatur (std) | Temperatura ambiente (std) | Temp otoczenia (std) | Ambient temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WMET.EnvTmp1 | #N/A | WMET. | EnvTmp1 | Ambient Temp1 | Umgebungstemperatur1 | Temperatura ambiente 1 | Temp otoczenia1 | Ambient temperature sensor1 | deg_c | °C | Live Value | Double | Live Value
WMET.EnvTmp1_10m_Avg | #N/A | WMET. | EnvTmp1_10m_Avg | Ambient Temp1 (avg) | Umgebungstemperatur1 (avg) | Temperatura ambiente 1 (avg) | Temp otoczenia1 (avg) | Ambient temperature sensor1 | deg_c | °C | Average | Double | 10 minute tag
WMET.EnvTmp1_10m_Max | #N/A | WMET. | EnvTmp1_10m_Max | Ambient Temp1 (max) | Umgebungstemperatur1 (max) | Temperatura ambiente 1 (max) | Temp otoczenia1 (max) | Ambient temperature sensor1 | deg_c | °C | Maximum | Double | 10 minute tag
WMET.EnvTmp1_10m_Min | #N/A | WMET. | EnvTmp1_10m_Min | Ambient Temp1 (min) | Umgebungstemperatur1 (min) | Temperatura ambiente 1 (min) | Temp otoczenia1 (min) | Ambient temperature sensor1 | deg_c | °C | Minimum | Double | 10 minute tag
WMET.EnvTmp1_10m_Std | #N/A | WMET. | EnvTmp1_10m_Std | Ambient Temp1 (std) | Umgebungstemperatur1 (std) | Temperatura ambiente 1 (std) | Temp otoczenia1 (std) | Ambient temperature sensor1 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WMET.EnvTmp2 | #N/A | WMET. | EnvTmp2 | Ambient Temp2 | Umgebungstemperatur2 | Temperatura ambiente 2 | Temp2 otoczenia | Ambient temperature sensor2 | deg_c | °C | Live Value | Double | Live Value
WMET.EnvTmp2_10m_Avg | #N/A | WMET. | EnvTmp2_10m_Avg | Ambient Temp2 (avg) | Umgebungstemperatur2 (avg) | Temperatura ambiente 2 (avg) | Temp2 otoczenia (avg) | Ambient temperature sensor2 | deg_c | °C | Average | Double | 10 minute tag
WMET.EnvTmp2_10m_Max | #N/A | WMET. | EnvTmp2_10m_Max | Ambient Temp2 (max) | Umgebungstemperatur2 (max) | Temperatura ambiente 2 (max) | Temp2 otoczenia (max) | Ambient temperature sensor2 | deg_c | °C | Maximum | Double | 10 minute tag
WMET.EnvTmp2_10m_Min | #N/A | WMET. | EnvTmp2_10m_Min | Ambient Temp2 (min) | Umgebungstemperatur2 (min) | Temperatura ambiente 2 (min) | Temp2 otoczenia (min) | Ambient temperature sensor2 | deg_c | °C | Minimum | Double | 10 minute tag
WMET.EnvTmp2_10m_Std | #N/A | WMET. | EnvTmp2_10m_Std | Ambient Temp2 (std) | Umgebungstemperatur2 (std) | Temperatura ambiente 2 (std) | Temp2 otoczenia (std) | Ambient temperature sensor2 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WMET.HorInsol | WMET.HorInsol | WMET. | HorInsol | Total horizontal insolation | Gesamte horizontale Sonneneinstrahlung | Insolación horizontal total | Całkowite poziome nasłonecznienie | Total horizontal insolation |  |  | Live Value | Double
WMET.HorWdDir | WMET.HorWdDir | WMET. | HorWdDir | Wind Direction Primary Windvane | Windrichtung Primäre Windfahne | Dirección del viento de la veleta primaria | Kierunek wiatru Główny wiatrowskaz | Wind direction primary windvane 0-360 degrees, 0 is north | deg | Degrees | Live Value | Double | Live Value | Used in some specialised presentations
WMET.HorWdDir_10m_Avg | #N/A | WMET. | HorWdDir_10m_Avg | Wind Direction Primary Windvane (avg) | Windrichtung Primäre Windfahne (avg) | Dirección del viento de la veleta primaria (avg) | Kierunek wiatru Główny wiatrowskaz (avg) | Wind direction primary windvane 0-360 degrees, 0 is north | deg | Degrees | Average | Double | 10 minute tag | Needed for reports
WMET.HorWdDir_10m_Max | #N/A | WMET. | HorWdDir_10m_Max | Wind Direction Primary Windvane (max) | Windrichtung Primäre Windfahne (max) | Dirección del viento de la veleta primaria (max) | Kierunek wiatru Główny wiatrowskaz (max) | Wind direction primary windvane 0-360 degrees, 0 is north | deg | Degrees | Maximum | Double | 10 minute tag | Common tags for analysis
WMET.HorWdDir_10m_Min | #N/A | WMET. | HorWdDir_10m_Min | Wind Direction Primary Windvane (min) | Windrichtung Primäre Windfahne (min) | Dirección del viento de la veleta primaria (min) | Kierunek wiatru Główny wiatrowskaz (min) | Wind direction primary windvane 0-360 degrees, 0 is north | deg | Degrees | Minimum | Double | 10 minute tag | Common tags for analysis
WMET.HorWdDir_10m_Std | #N/A | WMET. | HorWdDir_10m_Std | Wind Direction Primary Windvane (std) | Windrichtung Primäre Windfahne (std) | Dirección del viento de la veleta primaria (std) | Kierunek wiatru Główny wiatrowskaz (std) | Wind direction primary windvane 0-360 degrees, 0 is north | deg | Degrees | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WMET.HorWdDir1 | #N/A | WMET. | HorWdDir1 | Wind Direction Primary Windvane | Windrichtung Primäre Windfahne | Dirección del viento de la veleta primaria | Kierunek wiatru Główny wiatrowskaz | Wind direction primary windvane 0-360 degrees, 0 is north | deg | Degrees | Live Value | Double | Live Value
WMET.HorWdDir1_10m_Avg | #N/A | WMET. | HorWdDir1_10m_Avg | Wind Direction Primary Windvane (avg) | Windrichtung Primäre Windfahne (avg) | Dirección del viento de la veleta primaria (avg) | Kierunek wiatru Główny wiatrowskaz (avg) | Wind direction primary windvane 0-360 degrees, 0 is north | deg | Degrees | Average | Double | 10 minute tag
WMET.HorWdDir1_10m_Max | #N/A | WMET. | HorWdDir1_10m_Max | Wind Direction Primary Windvane (max) | Windrichtung Primäre Windfahne (max) | Dirección del viento de la veleta primaria (max) | Kierunek wiatru Główny wiatrowskaz (max) | Wind direction primary windvane 0-360 degrees, 0 is north | deg | Degrees | Maximum | Double | 10 minute tag
WMET.HorWdDir1_10m_Min | #N/A | WMET. | HorWdDir1_10m_Min | Wind Direction Primary Windvane (min) | Windrichtung Primäre Windfahne (min) | Dirección del viento de la veleta primaria (min) | Kierunek wiatru Główny wiatrowskaz (min) | Wind direction primary windvane 0-360 degrees, 0 is north | deg | Degrees | Minimum | Double | 10 minute tag
WMET.HorWdDir1_10m_Std | #N/A | WMET. | HorWdDir1_10m_Std | Wind Direction Primary Windvane (std) | Windrichtung Primäre Windfahne (std) | Dirección del viento de la veleta primaria (std) | Kierunek wiatru Główny wiatrowskaz (std) | Wind direction primary windvane 0-360 degrees, 0 is north | deg | Degrees | Standard Deviation | Double | 10 minute tag
WMET.HorWdDir2 | #N/A | WMET. | HorWdDir2 | Wind Direction Seconday Windvane | Windrichtung Sekundäre Windfahne | Dirección del viento de la veleta secundaria | Kierunek wiatru Rezerw. wiatrowskaz | Wind direction seconday windvane 0-360 degrees, 0 is north | deg | Degrees | Live Value | Double | Live Value
WMET.HorWdDir2_10m_Avg | #N/A | WMET. | HorWdDir2_10m_Avg | Wind Direction Seconday Windvane (avg) | Windrichtung Sekundäre Windfahne (avg) | Dirección del viento de la veleta secundaria (avg) | Kierunek wiatru Rezerw. wiatrowskaz (avg) | Wind direction seconday windvane 0-360 degrees, 0 is north | deg | Degrees | Average | Double | 10 minute tag
WMET.HorWdDir2_10m_Max | #N/A | WMET. | HorWdDir2_10m_Max | Wind Direction Seconday Windvane (max) | Windrichtung Sekundäre Windfahne (max) | Dirección del viento de la veleta secundaria (max) | Kierunek wiatru Rezerw. wiatrowskaz (max) | Wind direction seconday windvane 0-360 degrees, 0 is north | deg | Degrees | Maximum | Double | 10 minute tag
WMET.HorWdDir2_10m_Min | #N/A | WMET. | HorWdDir2_10m_Min | Wind Direction Seconday Windvane (min) | Windrichtung Sekundäre Windfahne (min) | Dirección del viento de la veleta secundaria (min) | Kierunek wiatru Rezerw. wiatrowskaz (min) | Wind direction seconday windvane 0-360 degrees, 0 is north | deg | Degrees | Minimum | Double | 10 minute tag
WMET.HorWdDir2_10m_Std | #N/A | WMET. | HorWdDir2_10m_Std | Wind Direction Seconday Windvane (std) | Windrichtung Sekundäre Windfahne (std) | Dirección del viento de la veleta secundaria (std) | Kierunek wiatru Rezerw. wiatrowskaz (std) | Wind direction seconday windvane 0-360 degrees, 0 is north | deg | Degrees | Standard Deviation | Double | 10 minute tag
WMET.HorWdDirRel | #N/A | WMET. | HorWdDirRel | Relative Wind Direction Primary Windvane | Relative Windrichtung Primäre Windfahne | Dirección del viento relativa de la veleta primaria | Względny kierunek wiatru Główny wiatrowskaz | Relative Wind direction primary windvane | deg | Degrees | Live Value | Double | Live Value
WMET.HorWdDirRel_10m_Avg | #N/A | WMET. | HorWdDirRel_10m_Avg | Relative Wind Direction Primary Windvane (avg) | Relative Windrichtung Primäre Windfahne (avg) | Dirección del viento relativa de la veleta primaria (avg) | Względny kierunek wiatru Główny wiatrowskaz (avg) | Relative Wind direction primary windvane | deg | Degrees | Average | Double | 10 minute tag
WMET.HorWdDirRel_10m_Max | #N/A | WMET. | HorWdDirRel_10m_Max | Relative Wind Direction Primary Windvane (max) | Relative Windrichtung Primäre Windfahne (max) | Dirección del viento relativa de la veleta primaria (max) | Względny kierunek wiatru Główny wiatrowskaz (max) | Relative Wind direction primary windvane | deg | Degrees | Maximum | Double | 10 minute tag
WMET.HorWdDirRel_10m_Min | #N/A | WMET. | HorWdDirRel_10m_Min | Relative Wind Direction Primary Windvane (min) | Relative Windrichtung Primäre Windfahne (min) | Dirección del viento relativa de la veleta primaria (min) | Względny kierunek wiatru Główny wiatrowskaz (min) | Relative Wind direction primary windvane | deg | Degrees | Minimum | Double | 10 minute tag
WMET.HorWdDirRel_10m_Std | #N/A | WMET. | HorWdDirRel_10m_Std | Relative Wind Direction Primary Windvane (std) | Relative Windrichtung Primäre Windfahne (std) | Dirección del viento relativa de la veleta primaria (std) | Względny kierunek wiatru Główny wiatrowskaz (std) | Relative Wind direction primary windvane | deg | Degrees | Standard Deviation | Double | 10 minute tag
WMET.HorWdDirRel1 | #N/A | WMET. | HorWdDirRel1 | Relative Wind Direction Seconday Windvane | Relative Windrichtung Sekundäre Windfahne | Dirección del viento relativa de la veleta secundaria | Względny kierunek wiatru Rezerw. wiatrowskaz | Relative Wind direction primary windvane | deg | Degrees | Live Value | Double | Live Value
WMET.HorWdDirRel1_10m_Avg | #N/A | WMET. | HorWdDirRel1_10m_Avg | Relative Wind Direction Seconday Windvane (avg) | Relative Windrichtung Sekundäre Windfahne (avg) | Dirección del viento relativa de la veleta secundaria (avg) | Względny kierunek wiatru Rezerw. wiatrowskaz (avg) | Relative Wind direction primary windvane | deg | Degrees | Average | Double | 10 minute tag
WMET.HorWdDirRel1_10m_Max | #N/A | WMET. | HorWdDirRel1_10m_Max | Relative Wind Direction Seconday Windvane (max) | Relative Windrichtung Sekundäre Windfahne (max) | Dirección del viento relativa de la veleta secundaria (max) | Względny kierunek wiatru Rezerw. wiatrowskaz (max) | Relative Wind direction primary windvane | deg | Degrees | Maximum | Double | 10 minute tag
WMET.HorWdDirRel1_10m_Min | #N/A | WMET. | HorWdDirRel1_10m_Min | Relative Wind Direction Seconday Windvane (min) | Relative Windrichtung Sekundäre Windfahne (min) | Dirección del viento relativa de la veleta secundaria (min) | Względny kierunek wiatru Rezerw. wiatrowskaz (min) | Relative Wind direction primary windvane | deg | Degrees | Minimum | Double | 10 minute tag
WMET.HorWdDirRel1_10m_Std | #N/A | WMET. | HorWdDirRel1_10m_Std | Relative Wind Direction Seconday Windvane (std) | Relative Windrichtung Sekundäre Windfahne (std) | Dirección del viento relativa de la veleta secundaria (std) | Względny kierunek wiatru Rezerw. wiatrowskaz (std) | Relative Wind direction primary windvane | deg | Degrees | Standard Deviation | Double | 10 minute tag
WMET.HorWdDirRel2 | #N/A | WMET. | HorWdDirRel2 | Relative Wind Direction Seconday Windvane | Relative Windrichtung Sekundäre Windfahne | Dirección del viento relativa de la veleta secundaria | Względny kierunek wiatru Rezerw. wiatrowskaz | Relative Wind direction seconday windvane | deg | Degrees | Live Value | Double | Live Value
WMET.HorWdDirRel2_10m_Avg | #N/A | WMET. | HorWdDirRel2_10m_Avg | Relative Wind Direction Seconday Windvane (avg) | Relative Windrichtung Sekundäre Windfahne (avg) | Dirección del viento relativa de la veleta secundaria (avg) | Względny kierunek wiatru Rezerw. wiatrowskaz (avg) | Relative Wind direction seconday windvane | deg | Degrees | Average | Double | 10 minute tag
WMET.HorWdDirRel2_10m_Max | #N/A | WMET. | HorWdDirRel2_10m_Max | Relative Wind Direction Seconday Windvane (max) | Relative Windrichtung Sekundäre Windfahne (max) | Dirección del viento relativa de la veleta secundaria (max) | Względny kierunek wiatru Rezerw. wiatrowskaz (max) | Relative Wind direction seconday windvane | deg | Degrees | Maximum | Double | 10 minute tag
WMET.HorWdDirRel2_10m_Min | #N/A | WMET. | HorWdDirRel2_10m_Min | Relative Wind Direction Seconday Windvane (min) | Relative Windrichtung Sekundäre Windfahne (min) | Dirección del viento relativa de la veleta secundaria (min) | Względny kierunek wiatru Rezerw. wiatrowskaz (min) | Relative Wind direction seconday windvane | deg | Degrees | Minimum | Double | 10 minute tag
WMET.HorWdDirRel2_10m_Std | #N/A | WMET. | HorWdDirRel2_10m_Std | Relative Wind Direction Seconday Windvane (std) | Relative Windrichtung Sekundäre Windfahne (std) | Dirección del viento relativa de la veleta secundaria (std) | Względny kierunek wiatru Rezerw. wiatrowskaz (std) | Relative Wind direction seconday windvane | deg | Degrees | Standard Deviation | Double | 10 minute tag
WMET.HorWdSpd | WMET.HorWdSpd | WMET. | HorWdSpd | Wind speed primary anemometer | Windgeschwindigkeit Primäranemometer | Velocidad del viento del anemómetro primario | Prędkość wiatru Główny anemometr | Wind speed primary anemometer | m_s | m/s | Live Value | Double | Live Value | Used in standard monitor Presentation
WMET.HorWdSpd_10m_Avg | #N/A | WMET. | HorWdSpd_10m_Avg | Wind speed primary anemometer (avg) | Windgeschwindigkeit Primäranemometer (avg) | Velocidad del viento del anemómetro primario (avg) | Prędkość wiatru Główny anemometr (avg) | Wind speed primary anemometer | m_s | m/s | Average | Double | 10 minute tag | Needed for reports | Used in standard Park monitor presentation
WMET.HorWdSpd_10m_Max | #N/A | WMET. | HorWdSpd_10m_Max | Wind speed primary anemometer (max) | Windgeschwindigkeit Primäranemometer (max) | Velocidad del viento del anemómetro primario (max) | Prędkość wiatru Główny anemometr (max) | Wind speed primary anemometer | m_s | m/s | Maximum | Double | 10 minute tag | Common tags for analysis
WMET.HorWdSpd_10m_Min | #N/A | WMET. | HorWdSpd_10m_Min | Wind speed primary anemometer (min) | Windgeschwindigkeit Primäranemometer (min) | Velocidad del viento del anemómetro primario (min) | Prędkość wiatru Główny anemometr (min) | Wind speed primary anemometer | m_s | m/s | Minimum | Double | 10 minute tag | Common tags for analysis
WMET.HorWdSpd_10m_Std | #N/A | WMET. | HorWdSpd_10m_Std | Wind speed primary anemometer (std) | Windgeschwindigkeit Primäranemometer (std) | Velocidad del viento del anemómetro primario (std) | Prędkość wiatru Główny anemometr (std) | Wind speed primary anemometer | m_s | m/s | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WMET.HorWdSpd1 | #N/A | WMET. | HorWdSpd1 | Wind speed primary anemometer | Windgeschwindigkeit Primäranemometer | Velocidad del viento del anemómetro primario | Prędkość wiatru Główny anemometr | Wind speed primary anemometer | m_s | m/s | Live Value | Double | Live Value | Used in standard monitor Presentation
WMET.HorWdSpd1_10m_Avg | #N/A | WMET. | HorWdSpd1_10m_Avg | Wind speed primary anemometer (avg) | Windgeschwindigkeit Primäranemometer (avg) | Velocidad del viento del anemómetro primario (avg) | Prędkość wiatru Główny anemometr (avg) | Wind speed primary anemometer | m_s | m/s | Average | Double | 10 minute tag | Needed for reports | Used in standard Park monitor presentation
WMET.HorWdSpd1_10m_Max | #N/A | WMET. | HorWdSpd1_10m_Max | Wind speed primary anemometer (max) | Windgeschwindigkeit Primäranemometer (max) | Velocidad del viento del anemómetro primario (max) | Prędkość wiatru Główny anemometr (max) | Wind speed primary anemometer | m_s | m/s | Maximum | Double | 10 minute tag | Common tags for analysis
WMET.HorWdSpd1_10m_Min | #N/A | WMET. | HorWdSpd1_10m_Min | Wind speed primary anemometer (min) | Windgeschwindigkeit Primäranemometer (min) | Velocidad del viento del anemómetro primario (min) | Prędkość wiatru Główny anemometr (min) | Wind speed primary anemometer | m_s | m/s | Minimum | Double | 10 minute tag | Common tags for analysis
WMET.HorWdSpd1_10m_Std | #N/A | WMET. | HorWdSpd1_10m_Std | Wind speed primary anemometer (std) | Windgeschwindigkeit Primäranemometer (std) | Velocidad del viento del anemómetro primario (std) | Prędkość wiatru Główny anemometr (std) | Wind speed primary anemometer | m_s | m/s | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WMET.HorWdSpd2 | #N/A | WMET. | HorWdSpd2 | Wind speed secondary anemometer | Windgeschwindigkeit Sekundäranemometer | Velocidad del viento del anemómetro secundario | Prędkość wiatru Rezerw. anemometr | Wind speed secondary anemometer | m_s | m/s | Live Value | Double | Live Value
WMET.HorWdSpd2_10m_Avg | #N/A | WMET. | HorWdSpd2_10m_Avg | Wind speed secondary anemometer (avg) | Windgeschwindigkeit Sekundäranemometer (avg) | Velocidad del viento del anemómetro secundario (avg) | Prędkość wiatru Rezerw. anemometr (avg) | Wind speed secondary anemometer | m_s | m/s | Average | Double | 10 minute tag | Rare tags for analysis
WMET.HorWdSpd2_10m_Max | #N/A | WMET. | HorWdSpd2_10m_Max | Wind speed secondary anemometer (max) | Windgeschwindigkeit Sekundäranemometer (max) | Velocidad del viento del anemómetro secundario (max) | Prędkość wiatru Rezerw. anemometr (max) | Wind speed secondary anemometer | m_s | m/s | Maximum | Double | 10 minute tag | Rare tags for analysis
WMET.HorWdSpd2_10m_Min | #N/A | WMET. | HorWdSpd2_10m_Min | Wind speed secondary anemometer (min) | Windgeschwindigkeit Sekundäranemometer (min) | Velocidad del viento del anemómetro secundario (min) | Prędkość wiatru Rezerw. anemometr (min) | Wind speed secondary anemometer | m_s | m/s | Minimum | Double | 10 minute tag | Rare tags for analysis
WMET.HorWdSpd2_10m_Std | #N/A | WMET. | HorWdSpd2_10m_Std | Wind speed secondary anemometer (std) | Windgeschwindigkeit Sekundäranemometer (std) | Velocidad del viento del anemómetro secundario (std) | Prędkość wiatru Rezerw. anemometr (std) | Wind speed secondary anemometer | m_s | m/s | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WMET.HorWdSpdEst | #N/A | WMET. | HorWdSpdEst | Estimated Wind speed | Geschätzte Windgeschwindigkeit | Velocidad del viento estimada | Szacowana prędkość wiatru | Estimated Horisontal Wind Speed | m_s | m/s | Live Value | Double | Live Value
WMET.HorWdSpdEst_10m_Avg | #N/A | WMET. | HorWdSpdEst_10m_Avg | Estimated Wind speed (avg) | Geschätzte Windgeschwindigkeit (avg) | Velocidad del viento estimada (avg) | Szacowana prędkość wiatru (avg) | Estimated Horisontal Wind Speed | m_s | m/s | Average | Double | 10 minute tag
WMET.HorWdSpdEst_10m_Max | #N/A | WMET. | HorWdSpdEst_10m_Max | Estimated Wind speed (max) | Geschätzte Windgeschwindigkeit (max) | Velocidad del viento estimada (max) | Szacowana prędkość wiatru (max) | Estimated Horisontal Wind Speed | m_s | m/s | Maximum | Double | 10 minute tag
WMET.HorWdSpdEst_10m_Min | #N/A | WMET. | HorWdSpdEst_10m_Min | Estimated Wind speed (min) | Geschätzte Windgeschwindigkeit (min) | Velocidad del viento estimada (min) | Szacowana prędkość wiatru (min) | Estimated Horisontal Wind Speed | m_s | m/s | Minimum | Double | 10 minute tag
WMET.HorWdSpdEst_10m_Std | #N/A | WMET. | HorWdSpdEst_10m_Std | Estimated Wind speed (std) | Geschätzte Windgeschwindigkeit (std) | Velocidad del viento estimada (std) | Szacowana prędkość wiatru (std) | Estimated Horisontal Wind Speed | m_s | m/s | Standard Deviation | Double | 10 minute tag
WMET.Ice | WMET.Ice | WMET. | Ice | Thickness of ice | Dicke des Eises | Espesor del hielo | Grubość lodu | Thickness of ice | mm | mm | Live Value | Double | Live Value
WMET.Ice_10m_Avg | #N/A | WMET. | Ice_10m_Avg | Thickness of ice (avg) | Dicke des Eises (avg) | Espesor del hielo (avg) | Grubość lodu (avg) | Thickness of ice | mm | mm | Average | Double | 10 minute tag
WMET.Ice_10m_Max | #N/A | WMET. | Ice_10m_Max | Thickness of ice (max) | Dicke des Eises (max) | Espesor del hielo (max) | Grubość lodu (max) | Thickness of ice | mm | mm | Maximum | Double | 10 minute tag
WMET.Ice_10m_Min | #N/A | WMET. | Ice_10m_Min | Thickness of ice (min) | Dicke des Eises (min) | Espesor del hielo (min) | Grubość lodu (min) | Thickness of ice | mm | mm | Minimum | Double | 10 minute tag
WMET.Ice_10m_Std | #N/A | WMET. | Ice_10m_Std | Thickness of ice (std) | Dicke des Eises (std) | Espesor del hielo (std) | Grubość lodu (std) | Thickness of ice | mm | mm | Standard Deviation | Double | 10 minute tag
WMET.IceSt | WMET.IceSt | WMET. | IceSt | Ice Detection Status | Status der Eisdetektion | Estado de detección de hielo | Stan wykrywania lodu | Status of ice detection | Enum | Enum | Live Value | Long | Live Value
WMET.Ilum | #N/A | WMET. | Ilum | Ambient brightness | Umgebungshelligkeit | Claridad ambiental | Jasność otoczenia | Ambient brightness [Lux] (Illuminance) | Lux | Lux | Live Value | Double | Live Value
WMET.Ilum_10m_Avg | #N/A | WMET. | Ilum_10m_Avg | Ambient brightness (avg) | Umgebungshelligkeit (avg) | Claridad ambiental (avg) | Jasność otoczenia (avg) | Average ambient brightness [Lux] (Illuminance) | Lux | Lux | Average | Double | 10 minute tag
WMET.RnFll | WMET.RnFll | WMET. | RnFll | Rainfall | Niederschlag | Precipitación | Opady | Rainfall | mm | mm | Live Value | Double
WMET.RnFll_10m_Avg | #N/A | WMET. | RnFll_10m_Avg | Rainfall (avg) | Niederschlag (avg) | Precipitación (avg) | Opady (avg) | Average rainfall [mm/min] | mm | mm | Average | Double | 10 minute tag
WMET.RnFll_10m_Max | #N/A | WMET. | RnFll_10m_Max | Rainfall (max) | Niederschlag (max) | Precipitación (max) | Opady (max) | Maximum rainfall [mm/min] | mm | mm | Maximum | Double | 10 minute tag
WMET.RnFll_10m_Min | #N/A | WMET. | RnFll_10m_Min | Rainfall (min) | Niederschlag (min) | Precipitación (min) | Opady (min) | Minimum rainfall [mm/min] | mm | mm | Minimum | Double | 10 minute tag
WMET.RnFll_10m_Std | #N/A | WMET. | RnFll_10m_Std | Rainfall (std) | Niederschlag (std) | Precipitación (std) | Opady (std) | standard deviation rainfall [mm/min] | mm | mm | Standard Deviation | Double | 10 minute tag
WMET.SnwCvr | WMET.SnwCvr | WMET. | SnwCvr | Snow cover | Schneedecke | Cubierta de nieve | Pokrywa śnieżna | Snow cover |  |  | Live Value | Double
WMET.SnwDen | WMET.SnwDen | WMET. | SnwDen | Density of snowfall | Dichte des Schneefalls | Densidad de nevada | Gęstość opadów śniegu | Density of snowfall |  |  | Live Value | Double
WMET.SnwEq | WMET.SnwEq | WMET. | SnwEq | Water equivalent of snowfall | Wasseräquivalent des Schneefalls | Equivalente de agua de la nevada | Ekwiwalent wody opadów śniegu | Water equivalent of snowfall |  |  | Live Value | Double
WMET.SnwFll | WMET.SnwFll | WMET. | SnwFll | Snowfall | Schneefall | nevada | Opad śniegu | Snowfall |  |  | Live Value | Double
WMET.SnwTmp | WMET.SnwTmp | WMET. | SnwTmp | Snowfall temp | Schneefall-Temperatur | Temperatura de la nevada | Temp opadów śniegu | Temperature of snowfall | deg_c | °C | Live Value | Double
WMET.VerWdDir | WMET.VerWdDir | WMET. | VerWdDir | Vertical Wind Direction | Vertikale Windrichtung | Dirección vertical del viento | Pionowy kierunek wiatru | Vertical wind direction | deg | Degrees | Live Value | Double | Live Value
WMET.VerWdSpd | WMET.VerWdSpd | WMET. | VerWdSpd | Vertical wind speed | Vertikale Windgeschwindigkeit | Velocidad del viento vertical | Prędkość wiatru pionowego | Vertical wind speed | m_s | m/s | Live Value | Double | Live Value
WMET.VerWdSpd_10m_Avg | #N/A | WMET. | VerWdSpd_10m_Avg | Vertical wind speed (avg) | Vertikale Windgeschwindigkeit (avg) | Velocidad del viento vertical (avg) | Prędkość wiatru pionowego (avg) | Vertical wind speed | m_s | m/s | Average | Double | 10 minute tag
WMET.VerWdSpd_10m_Max | #N/A | WMET. | VerWdSpd_10m_Max | Vertical wind speed (max) | Vertikale Windgeschwindigkeit (max) | Velocidad del viento vertical (max) | Prędkość wiatru pionowego (max) | Vertical wind speed | m_s | m/s | Maximum | Double | 10 minute tag
WMET.VerWdSpd_10m_Min | #N/A | WMET. | VerWdSpd_10m_Min | Vertical wind speed (min) | Vertikale Windgeschwindigkeit (min) | Velocidad del viento vertical (min) | Prędkość wiatru pionowego (min) | Vertical wind speed | m_s | m/s | Minimum | Double | 10 minute tag
WMET.VerWdSpd_10m_Std | #N/A | WMET. | VerWdSpd_10m_Std | Vertical wind speed (std) | Vertikale Windgeschwindigkeit (std) | Velocidad del viento vertical (std) | Prędkość wiatru pionowego (std) | Vertical wind speed | m_s | m/s | Standard Deviation | Double | 10 minute tag
WMET.WdGustSpd | WMET.WdGustSpd | WMET. | WdGustSpd | Gust Wind speed | Windgeschwindigkeit Böe | Ráfaga de velocidad del viento | Prędkość podmuchów wiatru | Wind gust speed | m_s | m/s | Live Value | Double | Live Value
WMET.WetBlbTmp | WMET.WetBlbTmp | WMET. | WetBlbTmp | Wet Bulb Temp | Feuchtkugeltemperatur | Temperatura del bulbo húmedo | Temp Wilgotnego Termometru | Wet bulb temperature | deg_c | °C | Live Value | Double
WMET.WtrTmp | WMET.WtrTmp | WMET. | WtrTmp | Water Temp | Wassertemperatur | Temperatura del agua | Temp wody | Temperature of water | deg_c | °C | Live Value | Double
WNAC.AneSt | WNAC.AneSt | WNAC. | AneSt | Anemometer Status | Status des Anemometers | Estado del anemómetro | Stan anemometru | Status of primary anemometer /secondary anemometer | Enum | Enum | Live Value | Long | Live Value
WNAC.BecBlbSt | WNAC.BecBlbSt | WNAC. | BecBlbSt | Aviation light Status | Status des Flugscheinwerfers | Estado de la luz para aviación | Stan świateł lotniczych | Aviation light status 0=ok, 1=fault | Enum | Enum | Live Value | Long | Live Value
WNAC.BecLevSpt | WNAC.BecLevSpt | WNAC. | BecLevSpt | Setpoint bulb light level of beacon | Sollwert Glühbirnenleuchtstärke der Bake | Punto de ajuste de nivel de la bombilla de la baliza | Nastawa poziomu światła latarni | Setpoint bulb light level of beacon |  |  | Live Value | Double
WNAC.BecLumLev | WNAC.BecLumLev | WNAC. | BecLumLev | Value of luminosity level of beacon | Wert des Leuchtniveaus der Bake | Valor de nivel de luminosidad de baliza | Wartość poziomu jasności latarni | Value of luminosity level of beacon |  |  | Live Value | Double
WNAC.BecMod | WNAC.BecMod | WNAC. | BecMod | Set Beacon Modus | Sollwert Bake Modus | Establecer modo de la baliza | Ustawianie trybu latarni | Set modus of beacon | Enum | Enum | Live Value | Long
WNAC.ClWtrInTmp | #N/A | WNAC. | ClWtrInTmp | Cooling Water Temp Before Heat Exchanger | Kühlwassertemperatur vor Wärmetauscher | Temperatura del agua de refrigeración delante del intercambiador de calor | Temp wody chłodzącej Temp Przed wymiennikiem ciepła | Temperature of cooling water immediately before entering the heat exchanger | deg_c | °C | Live Value | Double | Live Value
WNAC.ClWtrInTmp_10m_Avg | #N/A | WNAC. | ClWtrInTmp_10m_Avg | Cooling Water Temp Before Heat Exchanger (avg) | Kühlwassertemperatur vor Wärmetauscher (avg) | Temperatura del agua de refrigeración delante del intercambiador de calor (avg) | Temp wody chłodzącej Temp Przed wymiennikiem ciepła (avg) | Temperature of cooling water immediately before entering the heat exchanger | deg_c | °C | Average | Double | 10 minute tag
WNAC.ClWtrInTmp_10m_Max | #N/A | WNAC. | ClWtrInTmp_10m_Max | Cooling Water Temp Before Heat Exchanger (max) | Kühlwassertemperatur vor Wärmetauscher (max) | Temperatura del agua de refrigeración delante del intercambiador de calor (max) | Temp wody chłodzącej Temp Przed wymiennikiem ciepła (max) | Temperature of cooling water immediately before entering the heat exchanger | deg_c | °C | Maximum | Double | 10 minute tag
WNAC.ClWtrInTmp_10m_Min | #N/A | WNAC. | ClWtrInTmp_10m_Min | Cooling Water Temp Before Heat Exchanger (min) | Kühlwassertemperatur vor Wärmetauscher (min) | Temperatura del agua de refrigeración delante del intercambiador de calor (min) | Temp wody chłodzącej Temp Przed wymiennikiem ciepła (min) | Temperature of cooling water immediately before entering the heat exchanger | deg_c | °C | Minimum | Double | 10 minute tag
WNAC.ClWtrInTmp_10m_Std | #N/A | WNAC. | ClWtrInTmp_10m_Std | Cooling Water Temp Before Heat Exchanger (std) | Kühlwassertemperatur vor Wärmetauscher (std) | Temperatura del agua de refrigeración delante del intercambiador de calor (std) | Temp wody chłodzącej Temp Przed wymiennikiem ciepła (std) | Temperature of cooling water immediately before entering the heat exchanger | deg_c | °C | Standard Deviation | Double | 10 minute tag
WNAC.ClWtrOutTmp | #N/A | WNAC. | ClWtrOutTmp | Cooling Water Temp After Heat Exchanger | Kühlwassertemperatur nach dem Wärmetauscher | Temperatura del agua de refrigeración detrás del intercambiador de calor | Temp wody chłodzącej po wymienniku ciepła | Temperature of cooling water immediately after exiting the heat exchanger | deg_c | °C | Live Value | Double | Live Value
WNAC.ClWtrOutTmp_10m_Avg | #N/A | WNAC. | ClWtrOutTmp_10m_Avg | Cooling Water Temp After Heat Exchanger (avg) | Kühlwassertemperatur nach dem Wärmetauscher (avg) | Temperatura del agua de refrigeración detrás del intercambiador de calor (avg) | Temp wody chłodzącej po wymienniku ciepła (avg) | Temperature of cooling water immediately after exiting the heat exchanger | deg_c | °C | Average | Double | 10 minute tag
WNAC.ClWtrOutTmp_10m_Max | #N/A | WNAC. | ClWtrOutTmp_10m_Max | Cooling Water Temp After Heat Exchanger (max) | Kühlwassertemperatur nach dem Wärmetauscher (max) | Temperatura del agua de refrigeración detrás del intercambiador de calor (max) | Temp wody chłodzącej po wymienniku ciepła (max) | Temperature of cooling water immediately after exiting the heat exchanger | deg_c | °C | Maximum | Double | 10 minute tag
WNAC.ClWtrOutTmp_10m_Min | #N/A | WNAC. | ClWtrOutTmp_10m_Min | Cooling Water Temp After Heat Exchanger (min) | Kühlwassertemperatur nach dem Wärmetauscher (min) | Temperatura del agua de refrigeración detrás del intercambiador de calor (min) | Temp wody chłodzącej po wymienniku ciepła (min) | Temperature of cooling water immediately after exiting the heat exchanger | deg_c | °C | Minimum | Double | 10 minute tag
WNAC.ClWtrOutTmp_10m_Std | #N/A | WNAC. | ClWtrOutTmp_10m_Std | Cooling Water Temp After Heat Exchanger (std) | Kühlwassertemperatur nach dem Wärmetauscher (std) | Temperatura del agua de refrigeración detrás del intercambiador de calor (std) | Temp wody chłodzącej po wymienniku ciepła (std) | Temperature of cooling water immediately after exiting the heat exchanger | deg_c | °C | Standard Deviation | Double | 10 minute tag
WNAC.Dir | WNAC.Dir | WNAC. | Dir | Nacelle Direction | Richtung der Gondel | Dirección de góndola | Kierunek Gondoli | Direction of the nacelle, 0-360 degrees 0 is north | deg | Degrees | Live Value | Double | Live Value | Used in some specialised presentations
WNAC.Dir_10m_Avg | #N/A | WNAC. | Dir_10m_Avg | Nacelle Direction (avg) | Richtung der Gondel (avg) | Dirección de góndola (avg) | Kierunek Gondola (avg) | Direction of the nacelle, 0-360 degrees 0 is north | deg | Degrees | Average | Double | 10 minute tag | Rare tags for analysis
WNAC.Dir_10m_Max | #N/A | WNAC. | Dir_10m_Max | Nacelle Direction (max) | Richtung der Gondel (max) | Dirección de góndola (max) | Kierunek Gondola (max) | Direction of the nacelle, 0-360 degrees 0 is north | deg | Degrees | Maximum | Double | 10 minute tag | Rare tags for analysis
WNAC.Dir_10m_Min | #N/A | WNAC. | Dir_10m_Min | Nacelle Direction (min) | Richtung der Gondel (min) | Dirección de góndola (min) | Kierunek Gondola (min) | Direction of the nacelle, 0-360 degrees 0 is north | deg | Degrees | Minimum | Double | 10 minute tag | Rare tags for analysis
WNAC.Dir_10m_Std | #N/A | WNAC. | Dir_10m_Std | Nacelle Direction (std) | Richtung der Gondel (std) | Dirección de góndola (std) | Kierunek Gondola (std) | Direction of the nacelle, 0-360 degrees 0 is north | deg | Degrees | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WNAC.FanCnt | #N/A | WNAC. | FanCnt | Number of activations of the nacelle fan | Anzahl der Aktivierungen des Gondellüfters | Número de activaciones del ventilador de góndola | Liczba aktywacji wentylatora gondoli | Number of activations of the nacelle fan | count | Count | Total Counter | Long | Live Value
WNAC.FanCnt_10m_End | #N/A | WNAC. | FanCnt_10m_End | Number of activations of the nacelle fan (end) | Anzahl der Aktivierungen des Gondellüfters (end) | Número de activaciones del ventilador de góndola (end) | Liczba aktywacji wentylatora gondoli (end) | Number of activations of the nacelle fan | count | Count | Endvalue | Long | 10 minute tag
WNAC.FanTms | #N/A | WNAC. | FanTms | Time the nacelle fan has been activated | Zeit, in der der Gondellüfter aktiviert wurde | Tiempo que el ventilador de góndola ha estado activado | Czas aktywacji wentylatora gondoli | Time the nacelle fan has been activated | s | seconds | Total Counter | Long | Live Value
WNAC.FanTms_10m_End | #N/A | WNAC. | FanTms_10m_End | Time the nacelle fan has been activated (end) | Zeit, in der der Gondellüfter aktiviert wurde (end) | Tiempo que el ventilador de góndola ha estado activado (end) | Czas aktywacji wentylatora gondoli (end) | Time the nacelle fan has been activated | s | seconds | Endvalue | Long | 10 minute tag
WNAC.FlshSpt | WNAC.FlshSpt | WNAC. | FlshSpt | Setpoint value of flash duty cycle of beacon | Sollwert der Blitzeinschaltdauer der Bake | Valor del punto de ajuste de ciclo de trabajo de destello de baliza | Nastawa cyklu błysku latarni | Setpoint value of flash duty cycle of beacon |  |  | Setpoint | Double
WNAC.HtCnt1_10m_End | #N/A | WNAC. | HtCnt1_10m_End | Number of activations of the nacelle heat 1 (end) | Anzahl der Aktivierungen der Gondelheizung 1 (end) | Número de activaciones del calentador 1 de góndola (end) | Liczba aktywacji ogrz.1 gondoli (end) | Number of activations of the nacelle heat 1 | count | Count | Endvalue | Long | 10 minute tag
WNAC.HtCnt2_10m_End | #N/A | WNAC. | HtCnt2_10m_End | Number of activations of the nacelle heat 2 (end) | Anzahl der Aktivierungen der Gondelheizung 2 (end) | Número de activaciones del calentador 2 de góndola (end) | Liczba aktywacji ogrz.2 gondoli (end) | Number of activations of the nacelle heat 2 | count | Count | Endvalue | Long | 10 minute tag
WNAC.HtexTmp1 | #N/A | WNAC. | HtexTmp1 | Lower Heat Exchanger Temp | Untere Wärmetauschertemperatur | Temperatura inferior del intercambiador de calor | Dolna Temp wymiennika ciepła | Temperature of heat exchanger (lower) | deg_c | °C | Live Value | Double | Live Value
WNAC.HtexTmp1_10m_Avg | #N/A | WNAC. | HtexTmp1_10m_Avg | Lower Heat Exchanger Temp (avg) | Untere Wärmetauschertemperatur (avg) | Temperatura inferior del intercambiador de calor (avg) | Dolna Temp wymiennika ciepła (avg) | Temperature of heat exchanger (lower) | deg_c | °C | Average | Double | 10 minute tag
WNAC.HtexTmp1_10m_Max | #N/A | WNAC. | HtexTmp1_10m_Max | Lower Heat Exchanger Temp (max) | Untere Wärmetauschertemperatur (max) | Temperatura inferior del intercambiador de calor (max) | Dolna Temp wymiennika ciepła (max) | Temperature of heat exchanger (lower) | deg_c | °C | Maximum | Double | 10 minute tag
WNAC.HtexTmp1_10m_Min | #N/A | WNAC. | HtexTmp1_10m_Min | Lower Heat Exchanger Temp (min) | Untere Wärmetauschertemperatur (min) | Temperatura inferior del intercambiador de calor (min) | Dolna Temp wymiennika ciepła (min) | Temperature of heat exchanger (lower) | deg_c | °C | Minimum | Double | 10 minute tag
WNAC.HtexTmp1_10m_Std | #N/A | WNAC. | HtexTmp1_10m_Std | Lower Heat Exchanger Temp (std) | Untere Wärmetauschertemperatur (std) | Temperatura inferior del intercambiador de calor (std) | Dolna Temp wymiennika ciepła (std) | Temperature of heat exchanger (lower) | deg_c | °C | Standard Deviation | Double | 10 minute tag
WNAC.HtexTmp2 | #N/A | WNAC. | HtexTmp2 | Upper Heat Exchanger Temp | Obere Wärmetauschertemperatur | Temperatura superior del intercambiador de calor | Górna Temp wymiennika ciepła | Temperature of heat exchanger (Upper) | deg_c | °C | Live Value | Double | Live Value
WNAC.HtexTmp2_10m_Avg | #N/A | WNAC. | HtexTmp2_10m_Avg | Upper Heat Exchanger Temp (avg) | Obere Wärmetauschertemperatur (avg) | Temperatura superior del intercambiador de calor (avg) | Górna Temp wymiennika ciepła (avg) | Temperature of heat exchanger (Upper) | deg_c | °C | Average | Double | 10 minute tag
WNAC.HtexTmp2_10m_Max | #N/A | WNAC. | HtexTmp2_10m_Max | Upper Heat Exchanger Temp (max) | Obere Wärmetauschertemperatur (max) | Temperatura superior del intercambiador de calor (max) | Górna Temp wymiennika ciepła (max) | Temperature of heat exchanger (Upper) | deg_c | °C | Maximum | Double | 10 minute tag
WNAC.HtexTmp2_10m_Min | #N/A | WNAC. | HtexTmp2_10m_Min | Upper Heat Exchanger Temp (min) | Obere Wärmetauschertemperatur (min) | Temperatura superior del intercambiador de calor (min) | Górna Temp wymiennika ciepła (min) | Temperature of heat exchanger (Upper) | deg_c | °C | Minimum | Double | 10 minute tag
WNAC.HtexTmp2_10m_Std | #N/A | WNAC. | HtexTmp2_10m_Std | Upper Heat Exchanger Temp (std) | Obere Wärmetauschertemperatur (std) | Temperatura superior del intercambiador de calor (std) | Górna Temp wymiennika ciepła (std) | Temperature of heat exchanger (Upper) | deg_c | °C | Standard Deviation | Double | 10 minute tag
WNAC.HtFanCnt_10m_End | #N/A | WNAC. | HtFanCnt_10m_End | Number of activations of the nacelle heater fan (end) | Anzahl der Aktivierungen des Gondelheizlüfter (end) | Número de activaciones del ventilador del calentador de góndola (end) | Liczba aktywacji wentylatora nagrzewnicy gondoli (end) | Number of activations of the nacelle heater fan | count | Count | Endvalue | Long | 10 minute tag
WNAC.HtFanTms_10m_End | #N/A | WNAC. | HtFanTms_10m_End | Time nacelle heater fan has been activated (end) | Zeit, in der die Lüftung der Gondelheizung aktiviert wurde (end) | Tiempo que el ventilador del calentador de góndola ha estado activado (end) | Czas aktywacji wentylator nagrzewnicy gondoli (end) | Time nacelle heater fan has been activated | s | seconds | Endvalue | Long | 10 minute tag
WNAC.HtTms1_10m_End | #N/A | WNAC. | HtTms1_10m_End | Time the nacelle heat 1 has been activated (end) | Zeit, in der die Gondelheizung 1 aktiviert wurde (end) | Tiempo que el calentador 1 de góndola ha estado activado (end) | Czas aktywacji ogrz.1 gondoli (end) | Time the nacelle heat 1 has been activated | s | seconds | Endvalue | Long | 10 minute tag
WNAC.HtTms2_10m_End | #N/A | WNAC. | HtTms2_10m_End | Time the nacelle heat 2 has been activated (end) | Zeit, in der die Gondelheizung 2 aktiviert wurde (end) | Tiempo que el calentador 2 de góndola ha estado activado (end) | Czas aktywacji ogrz.2 gondoli (end) | Time the nacelle heat 2 has been activated | s | seconds | Endvalue | Long | 10 minute tag
WNAC.HyOilHtVlvSt | #N/A | WNAC. | HyOilHtVlvSt | Hydraulic station pitch heating valve | Hydraulikstation Pitch-Heizventil | Válvula de calentamiento del paso de la estación hidráulica | Stacja hydr. zaworu ogrzew. Pitch | Hydraulic station pitch heating valve | Enum | Enum | Live Value | Long | Live Value
WNAC.HyOilInlFilDiffPres | #N/A | WNAC. | HyOilInlFilDiffPres | Hydraulic station pitch differential pressure | Differenzdruck der Pitch-Hydraulikstation | Presión diferencial del paso de la estación hidráulica | Stacja hydr.ciśnienie różnicowe Pitch | Hydraulic station pitch differential pressure hi | bar | bar | Live Value | Double | Live Value
WNAC.HyOilLevSt | #N/A | WNAC. | HyOilLevSt | Hydraulic station pitch oil level | Ölstand in der Pitch-Hydraulikstation | Nivel del aceite del paso de la estación hidráulica | Stacja hydr. poziom oleju Pitch | Hydraulic station pitch oil level | Enum | Enum | Live Value | Long | Live Value
WNAC.HyOilLkgSt | #N/A | WNAC. | HyOilLkgSt | Sludge under pitch hydraulic station | Schlamm unter der Pitch-Hydraulikstation | Lodo debajo del paso de la estación hidráulica | Osad pod stacją hydr. Pitch | Sludge under pitch hydraulic station | Enum | Enum | Live Value | Long | Live Value
WNAC.HyOilOfFilDiffPres | #N/A | WNAC. | HyOilOfFilDiffPres | Offline Filter Differential Pressure | Nebenstromfilter-Differenzdruck | Presión diferencial del filtro sin conexión | Różnice ciśnień filtrów offline | Hydraulic Station Offline filter differential pressure | bar | bar | Live Value | Double | Live Value
WNAC.HyOilOfFilDiffPres_10m_Avg | #N/A | WNAC. | HyOilOfFilDiffPres_10m_Avg | Offline Filter Differential Pressure (avg) | Nebenstromfilter-Differenzdruck (avg) | Presión diferencial del filtro sin conexión (avg) | Różnice ciśnień filtrów offline (avg) | Hydraulic Station Offline filter differential pressure | bar | bar | Average | Double | 10 minute tag
WNAC.HyOilOfFilDiffPres_10m_Max | #N/A | WNAC. | HyOilOfFilDiffPres_10m_Max | Offline Filter Differential Pressure (max) | Nebenstromfilter-Differenzdruck (max) | Presión diferencial del filtro sin conexión (max) | Różnice ciśnień filtrów offline (max) | Hydraulic Station Offline filter differential pressure | bar | bar | Maximum | Double | 10 minute tag
WNAC.HyOilOfFilDiffPres_10m_Min | #N/A | WNAC. | HyOilOfFilDiffPres_10m_Min | Offline Filter Differential Pressure (min) | Nebenstromfilter-Differenzdruck (min) | Presión diferencial del filtro sin conexión (min) | Różnice ciśnień filtrów offline (min) | Hydraulic Station Offline filter differential pressure | bar | bar | Minimum | Double | 10 minute tag
WNAC.HyOilOfFilDiffPres_10m_Std | #N/A | WNAC. | HyOilOfFilDiffPres_10m_Std | Offline Filter Differential Pressure (std) | Nebenstromfilter-Differenzdruck (std) | Presión diferencial del filtro sin conexión (std) | Różnice ciśnień filtrów offline (std) | Hydraulic Station Offline filter differential pressure | bar | bar | Standard Deviation | Double | 10 minute tag
WNAC.HyOilOfFilPmpSt | #N/A | WNAC. | HyOilOfFilPmpSt | Hydraulic station Pitch Offline pump | Hydraulikstation Pitch Offline Pumpe | Bomba sin conexión del paso de la estación hidráulica | Stacja hydr. Pitch Pompa offline | Feedback Hydraulic station Pitch Offline pump | Enum | Enum | Live Value | Long | Live Value
WNAC.HyOilPmpCnt | #N/A | WNAC. | HyOilPmpCnt | Number of activations of the hydraulic oil pump | Anzahl der Aktivierungen der Hydraulikölpumpe | Número de activaciones de la bomba de aceite hidráulico | Liczba aktywacji hydraulicznej pompy oleju | Number of activations of the hydraulic oil pump | count | Count | Total Counter | Long | Live Value
WNAC.HyOilPmpCnt_10m_End | #N/A | WNAC. | HyOilPmpCnt_10m_End | Number of activations of the hydraulic oil pump, in nacelle (end) | Anzahl der Aktivierungen der Hydraulikölpumpe, in der Gondel (end) | Número de activaciones de la bomba de aceite hidráulico, en góndola (end) | Liczba aktywacji hydraulicznej pompy oleju, w gondoli (end) | Number of activations of the hydraulic oil pump, in nacelle | count | Count | Endvalue | Long | 10 minute tag
WNAC.HyOilPmpSt | #N/A | WNAC. | HyOilPmpSt | Hydraulic station Pitch High pressure | Hydraulikstation Pitch Hoher Druck | Presión alta del paso de la estación hidráulica | Stacja hydrauliczna Pitch Wysokie ciśnienie | Feedback Hydraulic station Pitch High pressure | Enum | Enum | Live Value | Long | Live Value
WNAC.HyOilPmpTms | #N/A | WNAC. | HyOilPmpTms | Time the hydraulic oil pump has been activated | Zeit, in der die Hydraulikölpumpe aktiviert wurde | Tiempo que la bomba de freno de aceite hidráulico ha estado activada | Czas aktywacji hydraulicznej pompy oleju | Time the hydraulic oil pump has been activated | s | seconds | Total Counter | Long | Live Value
WNAC.HyOilPmpTms_10m_End | #N/A | WNAC. | HyOilPmpTms_10m_End | Time the hydraulic oil pump has been activated (end) | Zeit, in der die Hydraulikölpumpe aktiviert wurde (end) | Tiempo que la bomba de freno de aceite hidráulico ha estado activada (end) | Czas aktywacji hydraulicznej pompy oleju (end) | Time the hydraulic oil pump has been activated, in nacelle | s | seconds | Endvalue | Long | 10 minute tag
WNAC.HyOilPres | #N/A | WNAC. | HyOilPres | Nacelle Hydraulic System Pressure | Druck im Hydrauliksystem der Gondel | Presión del sistema hidráulico de góndola | Ciśnienie w układzie hydr. Gondola | Nacelle hydraulic system pressure | bar | bar | Live Value | Double | Live Value
WNAC.HyOilPres_10m_Avg | #N/A | WNAC. | HyOilPres_10m_Avg | Nacelle Hydraulic System Pressure (avg) | Druck im Hydrauliksystem der Gondel (avg) | Presión del sistema hidráulico de góndola (avg) | Ciśnienie w układzie hydr. Gondola (avg) | Nacelle hydraulic system pressure | bar | bar | Average | Double | 10 minute tag | Rare tags for analysis
WNAC.HyOilPres_10m_Max | #N/A | WNAC. | HyOilPres_10m_Max | Nacelle Hydraulic System Pressure (max) | Druck im Hydrauliksystem der Gondel (max) | Presión del sistema hidráulico de góndola (max) | Ciśnienie w układzie hydr. Gondola (max) | Nacelle hydraulic system pressure | bar | bar | Maximum | Double | 10 minute tag | Rare tags for analysis
WNAC.HyOilPres_10m_Min | #N/A | WNAC. | HyOilPres_10m_Min | Nacelle Hydraulic System Pressure (min) | Druck im Hydrauliksystem der Gondel (min) | Presión del sistema hidráulico de góndola (min) | Ciśnienie w układzie hydr. Gondola (min) | Nacelle hydraulic system pressure | bar | bar | Minimum | Double | 10 minute tag | Rare tags for analysis
WNAC.HyOilPres_10m_Std | #N/A | WNAC. | HyOilPres_10m_Std | Nacelle Hydraulic System Pressure (std) | Druck im Hydrauliksystem der Gondel (std) | Presión del sistema hidráulico de góndola (std) | Ciśnienie w układzie hydr. Gondola (std) | Nacelle hydraulic system pressure | bar | bar | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WNAC.HyOilRlfVlvSt | #N/A | WNAC. | HyOilRlfVlvSt | Hydraulic station pitch Pressure reference | Hydraulikstation Pitch Druckreferenz | Referencia de presión del paso de la estación hidráulica | Rozstaw stacji hydr. Odniesienie ciśnienia | Hydraulic station pitch Pressure reference | Enum | Enum | Live Value | Long | Live Value
WNAC.HyOilTmp | #N/A | WNAC. | HyOilTmp | Nacelle Hydraulic Oil Temp | Hydrauliköltemperatur der Gondel | Temperatura de aceite hidráulico de góndola | Gondola olej hydr. Temp | Nacelle Hydraulic oil temperature | deg_c | °C | Live Value | Double | Live Value
WNAC.HyOilTmp_10m_Avg | #N/A | WNAC. | HyOilTmp_10m_Avg | Nacelle Hydraulic Oil Temp (avg) | Hydrauliköltemperatur der Gondel (avg) | Temperatura de aceite hidráulico de góndola (avg) | Gondola olej hydr. Temp (avg) | Nacelle Hydraulic oil temperature | deg_c | °C | Average | Double | 10 minute tag
WNAC.HyOilTmp_10m_Max | #N/A | WNAC. | HyOilTmp_10m_Max | Nacelle Hydraulic Oil Temp (max) | Hydrauliköltemperatur der Gondel (max) | Temperatura de aceite hidráulico de góndola (max) | Gondola olej hydr. Temp (max) | Nacelle Hydraulic oil temperature | deg_c | °C | Maximum | Double | 10 minute tag
WNAC.HyOilTmp_10m_Min | #N/A | WNAC. | HyOilTmp_10m_Min | Nacelle Hydraulic Oil Temp (min) | Hydrauliköltemperatur der Gondel (min) | Temperatura de aceite hidráulico de góndola (min) | Gondola olej hydr. Temp (min) | Nacelle Hydraulic oil temperature | deg_c | °C | Minimum | Double | 10 minute tag
WNAC.HyOilTmp_10m_Std | #N/A | WNAC. | HyOilTmp_10m_Std | Nacelle Hydraulic Oil Temp (std) | Hydrauliköltemperatur der Gondel (std) | Temperatura de aceite hidráulico de góndola (std) | Gondola olej hydr. Temp (std) | Nacelle Hydraulic oil temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WNAC.IceTmp | #N/A | WNAC. | IceTmp | Ice Detection Temperature | Eisdetektion Temperatur | Temperatura de detección del hielo | Temp wykrywania lodu | Ice Detection Temperature | deg_c | °C | Live Value | Double | Live Value
WNAC.IceTmp_10m_Avg | #N/A | WNAC. | IceTmp_10m_Avg | Ice Detection Temperature (avg) | Eisdetektion Temperatur (avg) | Temperatura de detección del hielo (avg) | Temp wykrywania lodu (avg) | Ice Detection Temperature | deg_c | °C | Average | Double | 10 minute tag
WNAC.IceTmp_10m_Max | #N/A | WNAC. | IceTmp_10m_Max | Ice Detection Temperature (max) | Eisdetektion Temperatur (max) | Temperatura de detección del hielo (max) | Temp wykrywania lodu (max) | Ice Detection Temperature | deg_c | °C | Maximum | Double | 10 minute tag
WNAC.IceTmp_10m_Min | #N/A | WNAC. | IceTmp_10m_Min | Ice Detection Temperature (min) | Eisdetektion Temperatur (min) | Temperatura de detección del hielo (min) | Temp wykrywania lodu (min) | Ice Detection Temperature | deg_c | °C | Minimum | Double | 10 minute tag
WNAC.IceTmp_10m_Std | #N/A | WNAC. | IceTmp_10m_Std | Ice Detection Temperature (std) | Eisdetektion Temperatur (std) | Temperatura de detección del hielo (std) | Temp wykrywania lodu (std) | Ice Detection Temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WNAC.IntnHum | WNAC.IntnHum | WNAC. | IntnHum | Internal humidity nacelle | Interne Feuchtigkeit der Gondel | Humedad interna góndola | Gondola wewn. wilgotność | Internal humidity nacelle, 10 minute average value | percent | percent | Live Value | Double | Live Value
WNAC.IntnHum_10m_Avg | #N/A | WNAC. | IntnHum_10m_Avg | Internal humidity nacelle (avg) | Interne Feuchtigkeit der Gondel (avg) | Humedad interna góndola (avg) | Gondola wewn. wilgotność (avg) | Internal humidity nacelle, 10 minute average value | percent | percent | Average | Double | 10 minute tag
WNAC.IntnHum_10m_Max | #N/A | WNAC. | IntnHum_10m_Max | Internal humidity nacelle (max) | Interne Feuchtigkeit der Gondel (max) | Humedad interna góndola (max) | Gondola wewn. wilgotność (max) | Internal humidity nacelle, 10 minute maximum value | percent | percent | Maximum | Double | 10 minute tag
WNAC.IntnHum_10m_Min | #N/A | WNAC. | IntnHum_10m_Min | Internal humidity nacelle (min) | Interne Feuchtigkeit der Gondel (min) | Humedad interna góndola (min) | Gondola wewn. wilgotność (min) | Internal humidity nacelle, 10 minute minimum value | percent | percent | Minimum | Double | 10 minute tag
WNAC.IntnHum_10m_Std | #N/A | WNAC. | IntnHum_10m_Std | Internal humidity nacelle (std) | Interne Feuchtigkeit der Gondel (std) | Humedad interna góndola (std) | Gondola wewn. wilgotność (std) | Internal humidity nacelle, 10 minute standard deviation value | percent | percent | Standard Deviation | Double | 10 minute tag
WNAC.IntnTmp | WNAC.IntnTmp | WNAC. | IntnTmp | Nacelle Internal Temp | Innentemperatur der Gondel | Temperatura interna de góndola | Gondola wewn. temp | Nacelle internal temperature | deg_c | °C | Live Value | Double | Live Value | Used in some specialised presentations
WNAC.IntnTmp_10m_Avg | #N/A | WNAC. | IntnTmp_10m_Avg | Nacelle Internal Temp (avg) | Innentemperatur der Gondel (avg) | Temperatura interna de góndola (avg) | Gondola wewn. temp (avg) | Nacelle internal temperature | deg_c | °C | Average | Double | 10 minute tag | Rare tags for analysis
WNAC.IntnTmp_10m_Max | #N/A | WNAC. | IntnTmp_10m_Max | Nacelle Internal Temp (max) | Innentemperatur der Gondel (max) | Temperatura interna de góndola (max) | Gondola wewn. temp (max) | Nacelle internal temperature | deg_c | °C | Maximum | Double | 10 minute tag | Rare tags for analysis
WNAC.IntnTmp_10m_Min | #N/A | WNAC. | IntnTmp_10m_Min | Nacelle Internal Temp (min) | Innentemperatur der Gondel (min) | Temperatura interna de góndola (min) | Gondola wewn. temp (min) | Nacelle internal temperature | deg_c | °C | Minimum | Double | 10 minute tag | Rare tags for analysis
WNAC.IntnTmp_10m_Std | #N/A | WNAC. | IntnTmp_10m_Std | Nacelle Internal Temp (std) | Innentemperatur der Gondel (std) | Temperatura interna de góndola (std) | Gondola wewn. temp (std) | Nacelle internal temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WNAC.IntnTmp2 | #N/A | WNAC. | IntnTmp2 | Nacelle Internal Temp2 | Innentemperatur der Gondel 2 | Temperatura 2 interna de góndola | Gondola wewn. Temp2 | Nacelle internal temperature sensor 2 | deg_c | °C | Live Value | Double | Live Value | Used in some specialised presentations
WNAC.IntnTmp3 | #N/A | WNAC. | IntnTmp3 | Nacelle Internal Temp3 | Innentemperatur der Gondel 3 | Temperatura 3 interna de góndola | Gondola wewn. Temp3 | Nacelle internal temperature sensor 3 | deg_c | °C | Live Value | Double | Live Value | Used in some specialised presentations
WNAC.IntnTmp4 | #N/A | WNAC. | IntnTmp4 | Nacelle Internal Temp4 | Innentemperatur der Gondel 4 | Temperatura 4 interna de góndola | Gondola wewn. Temp4 | Nacelle internal temperature sensor 4 | deg_c | °C | Live Value | Double | Live Value | Used in some specialised presentations
WNAC.LuPmpCnt | #N/A | WNAC. | LuPmpCnt | Number of activations of the lubrication pump | Anzahl der Aktivierungen der Schmiermittelpumpe | Número de activaciones de la bomba de lubricación | Liczba aktywacji pompy smarnej | Number of activations of the lubrication pump | count | Count | Total Counter | Long | Live Value
WNAC.LuPmpCnt_10m_End | #N/A | WNAC. | LuPmpCnt_10m_End | Number of activations of the lubrication pump (end) | Anzahl der Aktivierungen der Schmiermittelpumpe (end) | Número de activaciones de la bomba de lubricación (end) | Liczba aktywacji pompy smarnej (end) | Number of activations of the lubrication pump | count | Count | Endvalue | Long | 10 minute tag
WNAC.LuPmpTms | #N/A | WNAC. | LuPmpTms | Time lubrication pump has been activated | Zeit, in der die Schmiermittelpumpe aktiviert wurde | Tiempo que la bomba de lubricación ha estado activada | Czas aktywacji pompy smar. | Time lubrication pump has been activated | s | seconds | Total Counter | Long | Live Value
WNAC.LuPmpTms_10m_End | #N/A | WNAC. | LuPmpTms_10m_End | Time lubrication pump has been activated (end) | Zeit, in der die Schmiermittelpumpe aktiviert wurde (end) | Tiempo que la bomba de lubricación ha estado activada (end) | Czas aktywacji pompy smar. (end) | Time lubrication pump has been activated | s | seconds | Endvalue | Long | 10 minute tag
WNAC.OpTmsRs | WNAC.OpTmsRs | WNAC. | OpTmsRs | Operation time of beacon | Betriebszeit der Bake | Tiempo de funcionamiento de baliza | Czas pracy latarni | Operation time of beacon in seconds (vendor specific) | s | seconds | Total Counter | Long | Live Value
WNAC.PnlFanCnt_10m_End | #N/A | WNAC. | PnlFanCnt_10m_End | Number of activations of the panel/Topbox fan (end) | Anzahl der Aktivierungen des Panels/Topbox-Lüfters (end) | Número de activaciones del ventilador del panel/caja de herramientas (end) | Liczba aktywacji wentylatora panelu/Topbox (end) | Number of activations of the panel/Topbox fan | count | Count | Endvalue | Long | 10 minute tag
WNAC.PnlFanTms_10m_End | #N/A | WNAC. | PnlFanTms_10m_End | Time panel/Topbox fan has been activated (end) | Zeit, in der das Panel/Topboxgebläse aktiviert wurde (end) | Tiempo que el ventilador del panel/caja de herramientas ha estado activado (end) | Czas aktywacji wentylatora panelu/Topbox (end) | Time panel/Topbox fan has been activated | s | seconds | Endvalue | Long | 10 minute tag
WNAC.PnlTmp | #N/A | WNAC. | PnlTmp | Nacelle Panel Temp | Gondel-Panel-Temperatur | Temperatura del panel de góndola | Gondola Temp panelu | Nacelle panel/Topbox temperature | deg_c | °C | Live Value | Double | Live Value
WNAC.PnlTmp_10m_Avg | #N/A | WNAC. | PnlTmp_10m_Avg | Nacelle Panel Temp (avg) | Gondel-Panel-Temperatur (avg) | Temperatura del panel de góndola (avg) | Gondola Temp panelu (avg) | Nacelle panel/Topbox temperature | deg_c | °C | Average | Double | 10 minute tag
WNAC.PnlTmp_10m_Max | #N/A | WNAC. | PnlTmp_10m_Max | Nacelle Panel Temp (max) | Gondel-Panel-Temperatur (max) | Temperatura del panel de góndola (max) | Gondola Temp panelu (max) | Nacelle panel/Topbox temperature | deg_c | °C | Maximum | Double | 10 minute tag
WNAC.PnlTmp_10m_Min | #N/A | WNAC. | PnlTmp_10m_Min | Nacelle Panel Temp (min) | Gondel-Panel-Temperatur (min) | Temperatura del panel de góndola (min) | Gondola Temp panelu (min) | Nacelle panel/Topbox temperature | deg_c | °C | Minimum | Double | 10 minute tag
WNAC.PnlTmp_10m_Std | #N/A | WNAC. | PnlTmp_10m_Std | Nacelle Panel Temp (std) | Gondel-Panel-Temperatur (std) | Temperatura del panel de góndola (std) | Gondola Temp panelu (std) | Nacelle panel/Topbox temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WNAC.Pos | #N/A | WNAC. | Pos | Nacelle Position |  |  |  | Position of the nacelle from center (0 is north) | deg | Degrees | Live Value | Double | Live Value
WNAC.Pos_10m_Avg | #N/A | WNAC. | Pos_10m_Avg | Nacelle Position (avg) |  |  |  | Position of the nacelle from center (0 is north) | deg | Degrees | Average | Double | 10 minute tag
WNAC.Pos_10m_Max | #N/A | WNAC. | Pos_10m_Max | Nacelle Position (max) |  |  |  | Position of the nacelle from center (0 is north) | deg | Degrees | Maximum | Double | 10 minute tag
WNAC.Pos_10m_Min | #N/A | WNAC. | Pos_10m_Min | Nacelle Position (min) |  |  |  | Position of the nacelle from center (0 is north) | deg | Degrees | Minimum | Double | 10 minute tag
WNAC.Pos_10m_Std | #N/A | WNAC. | Pos_10m_Std | Nacelle Position (std) |  |  |  | Position of the nacelle from center (0 is north) | deg | Degrees | Standard Deviation | Double | 10 minute tag
WNAC.TopCtlTmp | #N/A | WNAC. | TopCtlTmp | Top Controller Temp | Temperatur des oberen Reglers | Temperatura del controlador superior | Top kontroler temp | Temperature in the top controller | deg_c | °C | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WNAC.Vis | WNAC.Vis | WNAC. | Vis | Visibility outside nacelle | Sichtbarkeit außerhalb der Gondel | Visibilidad exterior góndola | Widoczność poza gondolą | Visibility outside nacelle | m | m | Live Value | Double | Live Value
WNAC.Vis_10m_Avg | #N/A | WNAC. | Vis_10m_Avg | Visibility outside nacelle (avg) | Sichtbarkeit außerhalb der Gondel (avg) | Visibilidad exterior góndola (avg) | Widoczność poza gondolą (avg) | Visibility outside nacelle | m | m | Average | Double | 10 minute tag
WNAC.Vis_10m_Max | #N/A | WNAC. | Vis_10m_Max | Visibility outside nacelle (max) | Sichtbarkeit außerhalb der Gondel (max) | Visibilidad exterior góndola (max) | Widoczność poza gondolą (max) | Visibility outside nacelle | m | m | Maximum | Double | 10 minute tag
WNAC.Vis_10m_Min | #N/A | WNAC. | Vis_10m_Min | Visibility outside nacelle (min) | Sichtbarkeit außerhalb der Gondel (min) | Visibilidad exterior góndola (min) | Widoczność poza gondolą (min) | Visibility outside nacelle | m | m | Minimum | Double | 10 minute tag
WNAC.Vis_10m_Std | #N/A | WNAC. | Vis_10m_Std | Visibility outside nacelle (std) | Sichtbarkeit außerhalb der Gondel (std) | Visibilidad exterior góndola (std) | Widoczność poza gondolą (std) | Visibility outside nacelle | m | m | Standard Deviation | Double | 10 minute tag
WNAC.VOGSt | #N/A | WNAC. | VOGSt | Vestas Overspeed guard | Vestas Überdrehzahlschutz | Protección contra exceso de velocidad Vestas | Zabezp. max prędk. Vestas | VOG Ok | Enum | Enum | Live Value | Long | Live Value
WNAC.WdHtSt | WNAC.WdHtSt | WNAC. | WdHtSt | Wind sensor Heater Status | Windsensor Heizungsstatus | Estado del calentador del sensor de viento | Stan nagrzewnicy czujnika wiatru | Status of heater for wind sensor | Enum | Enum | Live Value | Long | Live Value
WNAC.XdirDsp | WNAC.XdirDsp | WNAC. | XdirDsp | Nacelle displacement shaft direction | Gondelverschiebung Wellenrichtung | Dirección del eje de desplazamiento de góndola | Kierunek przemieszczenia gondoli | Nacelle displacement shaft direction (longitudinal direction) | m_s2 | m/s^2 | Live Value | Double | Live Value
WNAC.XdirDsp_10m_Avg | #N/A | WNAC. | XdirDsp_10m_Avg | Nacelle displacement shaft direction (avg) | Gondelverschiebung Wellenrichtung (avg) | Dirección del eje de desplazamiento de góndola (avg) | Kierunek przemieszczenia gondoli (avg) | Nacelle displacement shaft direction (longitudinal direction) | m_s2 | m/s^2 | Average | Double | 10 minute tag
WNAC.XdirDsp_10m_Max | #N/A | WNAC. | XdirDsp_10m_Max | Nacelle displacement shaft direction (max) | Gondelverschiebung Wellenrichtung (max) | Dirección del eje de desplazamiento de góndola (max) | Kierunek przemieszczenia gondoli (max) | Nacelle displacement shaft direction (longitudinal direction) | m_s2 | m/s^2 | Maximum | Double | 10 minute tag
WNAC.XdirDsp_10m_Min | #N/A | WNAC. | XdirDsp_10m_Min | Nacelle displacement shaft direction (min) | Gondelverschiebung Wellenrichtung (min) | Dirección del eje de desplazamiento de góndola (min) | Kierunek przemieszczenia gondoli (min) | Nacelle displacement shaft direction (longitudinal direction) | m_s2 | m/s^2 | Minimum | Double | 10 minute tag
WNAC.XdirDsp_10m_Std | #N/A | WNAC. | XdirDsp_10m_Std | Nacelle displacement shaft direction (std) | Gondelverschiebung Wellenrichtung (std) | Dirección del eje de desplazamiento de góndola (std) | Kierunek przemieszczenia gondoli (std) | Nacelle displacement shaft direction (longitudinal direction) | m_s2 | m/s^2 | Standard Deviation | Double | 10 minute tag
WNAC.XdirVbr_10m_Avg | #N/A | WNAC. | XdirVbr_10m_Avg | Vibration in nacelle in longitudinal direction (avg) | Schwingungen in der Gondel in Längsrichtung (avg) | Vibración de la góndola en dirección longitudinal (avg) | Wibracje w gondoli w kierunku wzdłużnym (avg) | Vibration in the nacelle in longitudinal direction (Along the shaft in the nacelle) |  |  | Average | Double | 10 minute tag
WNAC.XdirVbr_10m_Max | #N/A | WNAC. | XdirVbr_10m_Max | Vibration in nacelle in longitudinal direction (max) | Schwingungen in der Gondel in Längsrichtung (max) | Vibración de la góndola en dirección longitudinal (max) | Wibracje w gondoli w kierunku wzdłużnym (max) | Vibration in the nacelle in longitudinal direction (Along the shaft in the nacelle) |  |  | Maximum | Double | 10 minute tag
WNAC.XdirVbr_10m_Min | #N/A | WNAC. | XdirVbr_10m_Min | Vibration in nacelle in longitudinal direction (min) | Schwingungen in der Gondel in Längsrichtung (min) | Vibración de la góndola en dirección longitudinal (min) | Wibracje w gondoli w kierunku wzdłużnym (min) | Vibration in the nacelle in longitudinal direction (Along the shaft in the nacelle) |  |  | Minimum | Double | 10 minute tag
WNAC.XdirVbr_10m_Std | #N/A | WNAC. | XdirVbr_10m_Std | Vibration in nacelle in longitudinal direction (std) | Schwingungen in der Gondel in Längsrichtung (std) | Vibración de la góndola en dirección longitudinal (std) | Wibracje w gondoli w kierunku wzdłużnym (std) | Vibration in the nacelle in longitudinal direction (Along the shaft in the nacelle) |  |  | Standard Deviation | Double | 10 minute tag
WNAC.YdirDsp | WNAC.YdirDsp | WNAC. | YdirDsp | Nacelle displacement | Gondelverschiebung | Desplazamiento de góndola | Przemieszczenie gondoli | Nacelle displacement (lateral direction) | m_s2 | m/s^2 | Live Value | Double | Live Value
WNAC.YdirDsp_10m_Avg | #N/A | WNAC. | YdirDsp_10m_Avg | Nacelle displacement (avg) | Gondelverschiebung (avg) | Desplazamiento de góndola (avg) | Przemieszczenie gondoli (avg) | Nacelle displacement (lateral direction) | m_s2 | m/s^2 | Average | Double | 10 minute tag
WNAC.YdirDsp_10m_Max | #N/A | WNAC. | YdirDsp_10m_Max | Nacelle displacement (max) | Gondelverschiebung (max) | Desplazamiento de góndola (max) | Przemieszczenie gondoli (max) | Nacelle displacement (lateral direction) | m_s2 | m/s^2 | Maximum | Double | 10 minute tag
WNAC.YdirDsp_10m_Min | #N/A | WNAC. | YdirDsp_10m_Min | Nacelle displacement (min) | Gondelverschiebung (min) | Desplazamiento de góndola (min) | Przemieszczenie gondoli (min) | Nacelle displacement (lateral direction) | m_s2 | m/s^2 | Minimum | Double | 10 minute tag
WNAC.YdirDsp_10m_Std | #N/A | WNAC. | YdirDsp_10m_Std | Nacelle displacement (std) | Gondelverschiebung (std) | Desplazamiento de góndola (std) | Przemieszczenie gondoli (std) | Nacelle displacement (lateral direction) | m_s2 | m/s^2 | Standard Deviation | Double | 10 minute tag
WNAC.YdirVbr_10m_Avg | #N/A | WNAC. | YdirVbr_10m_Avg | Vibration in nacelle in Lateral direction (avg) | Schwingungen in der Gondel in seitlicher Richtung (avg) | Vibración de la góndola en dirección lateral (avg) | Wibracje w gondoli w kierunku bocznym (avg) | Vibration in the nacelle in Lateral direction (traversal to the shaft in the nacelle |  |  | Average | Double | 10 minute tag
WNAC.YdirVbr_10m_Max | #N/A | WNAC. | YdirVbr_10m_Max | Vibration in nacelle in Lateral direction (max) | Schwingungen in der Gondel in seitlicher Richtung (max) | Vibración de la góndola en dirección lateral (max) | Wibracje w gondoli w kierunku bocznym (max) | Vibration in the nacelle in Lateral direction (traversal to the shaft in the nacelle |  |  | Maximum | Double | 10 minute tag
WNAC.YdirVbr_10m_Min | #N/A | WNAC. | YdirVbr_10m_Min | Vibration in nacelle in Lateral direction (min) | Schwingungen in der Gondel in seitlicher Richtung (min) | Vibración de la góndola en dirección lateral (min) | Wibracje w gondoli w kierunku bocznym (min) | Vibration in the nacelle in Lateral direction (traversal to the shaft in the nacelle |  |  | Minimum | Double | 10 minute tag
WNAC.YdirVbr_10m_Std | #N/A | WNAC. | YdirVbr_10m_Std | Vibration in nacelle in Lateral direction (std) | Schwingungen in der Gondel in seitlicher Richtung (std) | Vibración de la góndola en dirección lateral (std) | Wibracje w gondoli w kierunku bocznym (std) | Vibration in the nacelle in Lateral direction (traversal to the shaft in the nacelle |  |  | Standard Deviation | Double | 10 minute tag
WROT.BlLod1_10m_Avg | #N/A | WROT. | BlLod1_10m_Avg | Load Blade 1 (avg) | Belastung Blatt 1 (avg) | Cargo de la pala 1 (avg) | Obciąż. łopaty 1 (avg) | Load Blade 1 |  | Nm | Average | Long | 10 minute tag
WROT.BlLod1_10m_Max | #N/A | WROT. | BlLod1_10m_Max | Load Blade 1 (max) | Belastung Blatt 1 (max) | Cargo de la pala 1 (max) | Obciąż. łopaty 1 (max) | Load Blade 1 |  | Nm | Maximum | Long | 10 minute tag
WROT.BlLod1_10m_Min | #N/A | WROT. | BlLod1_10m_Min | Load Blade 1 (min) | Belastung Blatt 1 (min) | Cargo de la pala 1 (min) | Obciąż. łopaty 1 (min) | Load Blade 1 |  | Nm | Minimum | Long | 10 minute tag
WROT.BlLod1_10m_Std | #N/A | WROT. | BlLod1_10m_Std | Load Blade 1 (std) | Belastung Blatt 1 (std) | Cargo de la pala 1 (std) | Obciąż. łopaty 1 (std) | Load Blade 1 |  | Nm | Standard Deviation | Long | 10 minute tag
WROT.BlLod2_10m_Avg | #N/A | WROT. | BlLod2_10m_Avg | Load Blade 2 (avg) | Belastung Blatt 2 (avg) | Cargo de la pala 2 (avg) | Obciąż. łopaty 2 (avg) | Load Blade 2 |  | Nm | Average | Long | 10 minute tag
WROT.BlLod2_10m_Max | #N/A | WROT. | BlLod2_10m_Max | Load Blade 2 (max) | Belastung Blatt 2 (max) | Cargo de la pala 2 (max) | Obciąż. łopaty 2 (max) | Load Blade 2 |  | Nm | Maximum | Long | 10 minute tag
WROT.BlLod2_10m_Min | #N/A | WROT. | BlLod2_10m_Min | Load Blade 2 (min) | Belastung Blatt 2 (min) | Cargo de la pala 2 (min) | Obciąż. łopaty 2 (min) | Load Blade 2 |  | Nm | Minimum | Long | 10 minute tag
WROT.BlLod2_10m_Std | #N/A | WROT. | BlLod2_10m_Std | Load Blade 2 (std) | Belastung Blatt 2 (std) | Cargo de la pala 2 (std) | Obciąż. łopaty 2 (std) | Load Blade 2 |  | Nm | Standard Deviation | Long | 10 minute tag
WROT.BlLod3_10m_Avg | #N/A | WROT. | BlLod3_10m_Avg | Load Blade 3 (avg) | Belastung Blatt 3 (avg) | Cargo de la pala 3 (avg) | Obciąż. łopaty 3 (avg) | Load Blade 3 |  | Nm | Average | Long | 10 minute tag
WROT.BlLod3_10m_Max | #N/A | WROT. | BlLod3_10m_Max | Load Blade 3 (max) | Belastung Blatt 3 (max) | Cargo de la pala 3 (max) | Obciąż. łopaty 3 (max) | Load Blade 3 |  | Nm | Maximum | Long | 10 minute tag
WROT.BlLod3_10m_Min | #N/A | WROT. | BlLod3_10m_Min | Load Blade 3 (min) | Belastung Blatt 3 (min) | Cargo de la pala 3 (min) | Obciąż. łopaty 3 (min) | Load Blade 3 |  | Nm | Minimum | Long | 10 minute tag
WROT.BlLod3_10m_Std | #N/A | WROT. | BlLod3_10m_Std | Load Blade 3 (std) | Belastung Blatt 3 (std) | Cargo de la pala 3 (std) | Obciąż. łopaty 3 (std) | Load Blade 3 |  | Nm | Standard Deviation | Long | 10 minute tag
WROT.BlPthA1 | #N/A | WROT. | BlPthA1 | Pitch Motor 1 Current | Pitchmotor 1 Strom | Corriente del motor de tono 1 | Pitch Motor 1 Prąd | Electrical pitch motor current blade 1 | A | A | Live Value | Double | Live Value
WROT.BlPthA1_10m_Avg | #N/A | WROT. | BlPthA1_10m_Avg | Pitch Motor 1 Current (avg) | Pitchmotor 1 Strom (avg) | Corriente del motor de tono 1 (avg) | Pitch Motor 1 Prąd (avg) | Electrical pitch motor current blade 1 | A | A | Average | Double | 10 minute tag
WROT.BlPthA1_10m_Max | #N/A | WROT. | BlPthA1_10m_Max | Pitch Motor 1 Current (max) | Pitchmotor 1 Strom (max) | Corriente del motor de tono 1 (max) | Pitch Motor 1 Prąd (max) | Electrical pitch motor current blade 1 | A | A | Maximum | Double | 10 minute tag
WROT.BlPthA1_10m_Min | #N/A | WROT. | BlPthA1_10m_Min | Pitch Motor 1 Current (min) | Pitchmotor 1 Strom (min) | Corriente del motor de tono 1 (min) | Pitch Motor 1 Prąd (min) | Electrical pitch motor current blade 1 | A | A | Minimum | Double | 10 minute tag
WROT.BlPthA1_10m_Std | #N/A | WROT. | BlPthA1_10m_Std | Pitch Motor 1 Current (std) | Pitchmotor 1 Strom (std) | Corriente del motor de tono 1 (std) | Pitch Motor 1 Prąd (std) | Electrical pitch motor current blade 1 | A | A | Standard Deviation | Double | 10 minute tag
WROT.BlPthA2 | #N/A | WROT. | BlPthA2 | Pitch Motor 2 Current | Pitchmotor 2 Strom | Corriente del motor de tono 2 | Pitch Motor 2 Prąd | Electrical pitch motor current blade 2 | A | A | Live Value | Double | Live Value
WROT.BlPthA2_10m_Avg | #N/A | WROT. | BlPthA2_10m_Avg | Pitch Motor 2 Current (avg) | Pitchmotor 2 Strom (avg) | Corriente del motor de tono 2 (avg) | Pitch Motor 2 Prąd (avg) | Electrical pitch motor current blade 2 | A | A | Average | Double | 10 minute tag
WROT.BlPthA2_10m_Max | #N/A | WROT. | BlPthA2_10m_Max | Pitch Motor 2 Current (max) | Pitchmotor 2 Strom (max) | Corriente del motor de tono 2 (max) | Pitch Motor 2 Prąd (max) | Electrical pitch motor current blade 2 | A | A | Maximum | Double | 10 minute tag
WROT.BlPthA2_10m_Min | #N/A | WROT. | BlPthA2_10m_Min | Pitch Motor 2 Current (min) | Pitchmotor 2 Strom (min) | Corriente del motor de tono 2 (min) | Pitch Motor 2 Prąd (min) | Electrical pitch motor current blade 2 | A | A | Minimum | Double | 10 minute tag
WROT.BlPthA2_10m_Std | #N/A | WROT. | BlPthA2_10m_Std | Pitch Motor 2 Current (std) | Pitchmotor 2 Strom (std) | Corriente del motor de tono 2 (std) | Pitch Motor 2 Prąd (std) | Electrical pitch motor current blade 2 | A | A | Standard Deviation | Double | 10 minute tag
WROT.BlPthA3 | #N/A | WROT. | BlPthA3 | Pitch Motor 3 Current | Pitchmotor 3 Strom | Corriente del motor de tono 3 | Pitch Motor 3 Prąd | Electrical pitch motor current blade 3 | A | A | Live Value | Double | Live Value
WROT.BlPthA3_10m_Avg | #N/A | WROT. | BlPthA3_10m_Avg | Pitch Motor 3 Current (avg) | Pitchmotor 3 Strom (avg) | Corriente del motor de tono 3 (avg) | Pitch Motor 3 Prąd (avg) | Electrical pitch motor current blade 3 | A | A | Average | Double | 10 minute tag
WROT.BlPthA3_10m_Max | #N/A | WROT. | BlPthA3_10m_Max | Pitch Motor 3 Current (max) | Pitchmotor 3 Strom (max) | Corriente del motor de tono 3 (max) | Pitch Motor 3 Prąd (max) | Electrical pitch motor current blade 3 | A | A | Maximum | Double | 10 minute tag
WROT.BlPthA3_10m_Min | #N/A | WROT. | BlPthA3_10m_Min | Pitch Motor 3 Current (min) | Pitchmotor 3 Strom (min) | Corriente del motor de tono 3 (min) | Pitch Motor 3 Prąd (min) | Electrical pitch motor current blade 3 | A | A | Minimum | Double | 10 minute tag
WROT.BlPthA3_10m_Std | #N/A | WROT. | BlPthA3_10m_Std | Pitch Motor 3 Current (std) | Pitchmotor 3 Strom (std) | Corriente del motor de tono 3 (std) | Pitch Motor 3 Prąd (std) | Electrical pitch motor current blade 3 | A | A | Standard Deviation | Double | 10 minute tag
WROT.BlPthAng2Val1 | #N/A | WROT. | BlPthAng2Val1 | Secondary Pitch angle of blade 1 | Sekundärer Pitch-Winkel von Blatt 1 | Ángulo de paso secundario de la pala 1 | Kąt Pitch wtór. łopata 1 | Pitch angle seconof blade 1 | deg | Degrees | Live Value | Double | Live Value
WROT.BlPthAng2Val1_10m_Avg | #N/A | WROT. | BlPthAng2Val1_10m_Avg | Secondary Pitch angle of blade 1 (avg) | Sekundärer Pitch-Winkel von Blatt 1 (avg) | Ángulo de paso secundario de la pala 1 (avg) | Kąt Pitch wtór. łopata 1 (avg) | Pitch angle blade 1 secondary sensor | deg | Degrees | Average | Double | 10 minute tag
WROT.BlPthAng2Val1_10m_Max | #N/A | WROT. | BlPthAng2Val1_10m_Max | Secondary Pitch angle of blade 1 (max) | Sekundärer Pitch-Winkel von Blatt 1 (max) | Ángulo de paso secundario de la pala 1 (max) | Kąt Pitch wtór. łopata 1 (max) | Pitch angle blade 1 secondary sensor | deg | Degrees | Maximum | Double | 10 minute tag
WROT.BlPthAng2Val1_10m_Min | #N/A | WROT. | BlPthAng2Val1_10m_Min | Secondary Pitch angle of blade 1 (min) | Sekundärer Pitch-Winkel von Blatt 1 (min) | Ángulo de paso secundario de la pala 1 (min) | Kąt Pitch wtór. łopata 1 (min) | Pitch angle blade 1 secondary sensor | deg | Degrees | Minimum | Double | 10 minute tag
WROT.BlPthAng2Val1_10m_Std | #N/A | WROT. | BlPthAng2Val1_10m_Std | Secondary Pitch angle of blade 1 (std) | Sekundärer Pitch-Winkel von Blatt 1 (std) | Ángulo de paso secundario de la pala 1 (std) | Kąt Pitch wtór. łopata 1 (std) | Pitch angle blade 1 secondary sensor | deg | Degrees | Standard Deviation | Double | 10 minute tag
WROT.BlPthAng2Val2 | #N/A | WROT. | BlPthAng2Val2 | Secondary Pitch angle of blade 2 | Sekundärer Pitch-Winkel von Blatt 2 | Ángulo de paso secundario de la pala 2 | Kąt Pitch wtór. łopata 2 | Pitch angle blade 2 secondary sensor | deg | Degrees | Live Value | Double | Live Value
WROT.BlPthAng2Val2_10m_Avg | #N/A | WROT. | BlPthAng2Val2_10m_Avg | Secondary Pitch angle of blade 2 (avg) | Sekundärer Pitch-Winkel von Blatt 2 (avg) | Ángulo de paso secundario de la pala 2 (avg) | Kąt Pitch wtór. łopata 2 (avg) | Pitch angle blade 2 secondary sensor | deg | Degrees | Average | Double | 10 minute tag
WROT.BlPthAng2Val2_10m_Max | #N/A | WROT. | BlPthAng2Val2_10m_Max | Secondary Pitch angle of blade 2 (max) | Sekundärer Pitch-Winkel von Blatt 2 (max) | Ángulo de paso secundario de la pala 2 (max) | Kąt Pitch wtór. łopata 2 (max) | Pitch angle blade 2 secondary sensor | deg | Degrees | Maximum | Double | 10 minute tag
WROT.BlPthAng2Val2_10m_Min | #N/A | WROT. | BlPthAng2Val2_10m_Min | Secondary Pitch angle of blade 2 (min) | Sekundärer Pitch-Winkel von Blatt 2 (min) | Ángulo de paso secundario de la pala 2 (min) | Kąt Pitch wtór. łopata 2 (min) | Pitch angle blade 2 secondary sensor | deg | Degrees | Minimum | Double | 10 minute tag
WROT.BlPthAng2Val2_10m_Std | #N/A | WROT. | BlPthAng2Val2_10m_Std | Secondary Pitch angle of blade 2 (std) | Sekundärer Pitch-Winkel von Blatt 2 (std) | Ángulo de paso secundario de la pala 2 (std) | Kąt Pitch wtór. łopata 2 (std) | Pitch angle blade 2 secondary sensor | deg | Degrees | Standard Deviation | Double | 10 minute tag
WROT.BlPthAng2Val3 | #N/A | WROT. | BlPthAng2Val3 | Secondary Pitch angle of blade 3 | Sekundärer Pitch-Winkel von Blatt 3 | Ángulo de paso secundario de la pala 3 | Kąt Pitch wtór. łopata 3 | Pitch angle blade 3 secondary sensor | deg | Degrees | Live Value | Double | Live Value
WROT.BlPthAng2Val3_10m_Avg | #N/A | WROT. | BlPthAng2Val3_10m_Avg | Secondary Pitch angle of blade 3 (avg) | Sekundärer Pitch-Winkel von Blatt 3 (avg) | Ángulo de paso secundario de la pala 3 (avg) | Kąt Pitch wtór. łopata 3 (avg) | Pitch angle blade 3 secondary sensor | deg | Degrees | Average | Double | 10 minute tag
WROT.BlPthAng2Val3_10m_Max | #N/A | WROT. | BlPthAng2Val3_10m_Max | Secondary Pitch angle of blade 3 (max) | Sekundärer Pitch-Winkel von Blatt 3 (max) | Ángulo de paso secundario de la pala 3 (max) | Kąt Pitch wtór. łopata 3 (max) | Pitch angle blade 3 secondary sensor | deg | Degrees | Maximum | Double | 10 minute tag
WROT.BlPthAng2Val3_10m_Min | #N/A | WROT. | BlPthAng2Val3_10m_Min | Secondary Pitch angle of blade 3 (min) | Sekundärer Pitch-Winkel von Blatt 3 (min) | Ángulo de paso secundario de la pala 3 (min) | Kąt Pitch wtór. łopata 3 (min) | Pitch angle blade 3 secondary sensor | deg | Degrees | Minimum | Double | 10 minute tag
WROT.BlPthAng2Val3_10m_Std | #N/A | WROT. | BlPthAng2Val3_10m_Std | Secondary Pitch angle of blade 3 (std) | Sekundärer Pitch-Winkel von Blatt 3 (std) | Ángulo de paso secundario de la pala 3 (std) | Kąt Pitch wtór. łopata 3 (std) | Pitch angle blade 3 secondary sensor | deg | Degrees | Standard Deviation | Double | 10 minute tag
WROT.BlPthAngRmpTgt1 | #N/A | WROT. | BlPthAngRmpTgt1 | Pitch angle ramped setpoint blade 1 | Pitchwinkel-Rampen-Sollwert Blatt 1 | Punto de ajuste aumentado del ángulo de paso de la pala 1 | Kąt Pitch ramped nastawa łopata 1 | Pitch angle ramped setpoint blade 1 | deg | Degrees | Live Value | Double | Live Value
WROT.BlPthAngRmpTgt1_10m_Avg | #N/A | WROT. | BlPthAngRmpTgt1_10m_Avg | Pitch angle ramped setpoint blade 1 (avg) | Pitchwinkel-Rampen-Sollwert Blatt 1 (avg) | Punto de ajuste aumentado del ángulo de paso de la pala 1 (avg) | Kąt Pitch ramped nastawa łopata 1 (avg) | Pitch angle ramped setpoint blade 1 | deg | Degrees | Average | Double | 10 minute tag
WROT.BlPthAngRmpTgt1_10m_Max | #N/A | WROT. | BlPthAngRmpTgt1_10m_Max | Pitch angle ramped setpoint blade 1 (max) | Pitchwinkel-Rampen-Sollwert Blatt 1 (max) | Punto de ajuste aumentado del ángulo de paso de la pala 1 (max) | Kąt Pitch ramped nastawa łopata 1 (max) | Pitch angle ramped setpoint blade 1 | deg | Degrees | Maximum | Double | 10 minute tag
WROT.BlPthAngRmpTgt1_10m_Min | #N/A | WROT. | BlPthAngRmpTgt1_10m_Min | Pitch angle ramped setpoint blade 1 (min) | Pitchwinkel-Rampen-Sollwert Blatt 1 (min) | Punto de ajuste aumentado del ángulo de paso de la pala 1 (min) | Kąt Pitch ramped nastawa łopata 1 (min) | Pitch angle ramped setpoint blade 1 | deg | Degrees | Minimum | Double | 10 minute tag
WROT.BlPthAngRmpTgt1_10m_Std | #N/A | WROT. | BlPthAngRmpTgt1_10m_Std | Pitch angle ramped setpoint blade 1 (std) | Pitchwinkel-Rampen-Sollwert Blatt 1 (std) | Punto de ajuste aumentado del ángulo de paso de la pala 1 (std) | Kąt Pitch ramped nastawa łopata 1 (std) | Pitch angle ramped setpoint blade 1 | deg | Degrees | Standard Deviation | Double | 10 minute tag
WROT.BlPthAngRmpTgt2 | #N/A | WROT. | BlPthAngRmpTgt2 | Pitch angle ramped setpoint blade 2 | Pitchwinkel-Rampen-Sollwert Blatt 2 | Punto de ajuste aumentado del ángulo de paso de la pala 2 | Kąt Pitch ramped nastawa łopata 2 | Pitch angle ramped setpoint blade 2 | deg | Degrees | Live Value | Double | Live Value
WROT.BlPthAngRmpTgt2_10m_Avg | #N/A | WROT. | BlPthAngRmpTgt2_10m_Avg | Pitch angle ramped setpoint blade 2 (avg) | Pitchwinkel-Rampen-Sollwert Blatt 2 (avg) | Punto de ajuste aumentado del ángulo de paso de la pala 2 (avg) | Kąt Pitch ramped nastawa łopata 2 (avg) | Pitch angle ramped setpoint blade 2 | deg | Degrees | Average | Double | 10 minute tag
WROT.BlPthAngRmpTgt2_10m_Max | #N/A | WROT. | BlPthAngRmpTgt2_10m_Max | Pitch angle ramped setpoint blade 2 (max) | Pitchwinkel-Rampen-Sollwert Blatt 2 (max) | Punto de ajuste aumentado del ángulo de paso de la pala 2 (max) | Kąt Pitch ramped nastawa łopata 2 (max) | Pitch angle ramped setpoint blade 2 | deg | Degrees | Maximum | Double | 10 minute tag
WROT.BlPthAngRmpTgt2_10m_Min | #N/A | WROT. | BlPthAngRmpTgt2_10m_Min | Pitch angle ramped setpoint blade 2 (min) | Pitchwinkel-Rampen-Sollwert Blatt 2 (min) | Punto de ajuste aumentado del ángulo de paso de la pala 2 (min) | Kąt Pitch ramped nastawa łopata 2 (min) | Pitch angle ramped setpoint blade 2 | deg | Degrees | Minimum | Double | 10 minute tag
WROT.BlPthAngRmpTgt2_10m_Std | #N/A | WROT. | BlPthAngRmpTgt2_10m_Std | Pitch angle ramped setpoint blade 2 (std) | Pitchwinkel-Rampen-Sollwert Blatt 2 (std) | Punto de ajuste aumentado del ángulo de paso de la pala 2 (std) | Kąt Pitch ramped nastawa łopata 2 (std) | Pitch angle ramped setpoint blade 2 | deg | Degrees | Standard Deviation | Double | 10 minute tag
WROT.BlPthAngRmpTgt3 | #N/A | WROT. | BlPthAngRmpTgt3 | Pitch angle ramped setpoint blade 3 | Pitchwinkel-Rampen-Sollwert Blatt 3 | Punto de ajuste aumentado del ángulo de paso de la pala 3 | Kąt Pitch ramped nastawa łopata 3 | Pitch angle ramped setpoint blade 3 | deg | Degrees | Live Value | Double | Live Value
WROT.BlPthAngRmpTgt3_10m_Avg | #N/A | WROT. | BlPthAngRmpTgt3_10m_Avg | Pitch angle ramped setpoint blade 3 (avg) | Pitchwinkel-Rampen-Sollwert Blatt 3 (avg) | Punto de ajuste aumentado del ángulo de paso de la pala 3 (avg) | Kąt Pitch ramped nastawa łopata 4 (avg) | Pitch angle ramped setpoint blade 3 | deg | Degrees | Average | Double | 10 minute tag
WROT.BlPthAngRmpTgt3_10m_Max | #N/A | WROT. | BlPthAngRmpTgt3_10m_Max | Pitch angle ramped setpoint blade 3 (max) | Pitchwinkel-Rampen-Sollwert Blatt 3 (max) | Punto de ajuste aumentado del ángulo de paso de la pala 3 (max) | Kąt Pitch ramped nastawa łopata 5 (max) | Pitch angle ramped setpoint blade 3 | deg | Degrees | Maximum | Double | 10 minute tag
WROT.BlPthAngRmpTgt3_10m_Min | #N/A | WROT. | BlPthAngRmpTgt3_10m_Min | Pitch angle ramped setpoint blade 3 (min) | Pitchwinkel-Rampen-Sollwert Blatt 3 (min) | Punto de ajuste aumentado del ángulo de paso de la pala 3 (min) | Kąt Pitch ramped nastawa łopata 6 (min) | Pitch angle ramped setpoint blade 3 | deg | Degrees | Minimum | Double | 10 minute tag
WROT.BlPthAngRmpTgt3_10m_Std | #N/A | WROT. | BlPthAngRmpTgt3_10m_Std | Pitch angle ramped setpoint blade 3 (std) | Pitchwinkel-Rampen-Sollwert Blatt 3 (std) | Punto de ajuste aumentado del ángulo de paso de la pala 3 (std) | Kąt Pitch ramped nastawa łopata 7 (std) | Pitch angle ramped setpoint blade 3 | deg | Degrees | Standard Deviation | Double | 10 minute tag
WROT.BlPthAngTgt | WROT.BlPthAngTgt | WROT. | BlPthAngTgt | Pitch angle setpoint | Pitchwinkel-Sollwert | Punto de ajuste del ángulo de paso | Nastawa kąta Pitch | Pitch angle target value | deg | Degrees | Live Value | Double | Live Value
WROT.BlPthAngTgt_10m_Avg | #N/A | WROT. | BlPthAngTgt_10m_Avg | Pitch angle setpoint (avg) | Pitchwinkel-Sollwert (avg) | Punto de ajuste del ángulo de paso (avg) | Nastawa kąta Pitch (avg) | Pitch angle setpoint | deg | Degrees | Average | Double | 10 minute tag
WROT.BlPthAngTgt_10m_Max | #N/A | WROT. | BlPthAngTgt_10m_Max | Pitch angle setpoint (max) | Pitchwinkel-Sollwert (max) | Punto de ajuste del ángulo de paso (max) | Nastawa kąta Pitch (max) | Pitch angle setpoint | deg | Degrees | Maximum | Double | 10 minute tag
WROT.BlPthAngTgt_10m_Min | #N/A | WROT. | BlPthAngTgt_10m_Min | Pitch angle setpoint (min) | Pitchwinkel-Sollwert (min) | Punto de ajuste del ángulo de paso (min) | Nastawa kąta Pitch (min) | Pitch angle setpoint | deg | Degrees | Minimum | Double | 10 minute tag
WROT.BlPthAngTgt_10m_Std | #N/A | WROT. | BlPthAngTgt_10m_Std | Pitch angle setpoint (std) | Pitchwinkel-Sollwert (std) | Punto de ajuste del ángulo de paso (std) | Nastawa kąta Pitch (std) | Pitch angle setpoint | deg | Degrees | Standard Deviation | Double | 10 minute tag
WROT.BlPthAngTgt1 | #N/A | WROT. | BlPthAngTgt1 | Pitch angle setpoint blade 1 | Pitchwinkel-Sollwert Blatt 1 | Punto de ajuste del ángulo de paso pala 1 | Kąt Pitch nastawa łopata 1 | Pitch angle setpoint blade 1 | deg | Degrees | Live Value | Double | Live Value
WROT.BlPthAngTgt1_10m_Avg | #N/A | WROT. | BlPthAngTgt1_10m_Avg | Pitch angle setpoint blade 1 (avg) | Pitchwinkel-Sollwert Blatt 1 (avg) | Punto de ajuste del ángulo de paso pala 1 (avg) | Kąt Pitch nastawa łopata 1 (avg) | Pitch angle setpoint blade 1 | deg | Degrees | Average | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthAngTgt1_10m_Max | #N/A | WROT. | BlPthAngTgt1_10m_Max | Pitch angle setpoint blade 1 (max) | Pitchwinkel-Sollwert Blatt 1 (max) | Punto de ajuste del ángulo de paso pala 1 (max) | Kąt Pitch nastawa łopata 1 (max) | Pitch angle setpoint blade 1 | deg | Degrees | Maximum | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthAngTgt1_10m_Min | #N/A | WROT. | BlPthAngTgt1_10m_Min | Pitch angle setpoint blade 1 (min) | Pitchwinkel-Sollwert Blatt 1 (min) | Punto de ajuste del ángulo de paso pala 1 (min) | Kąt Pitch nastawa łopata 1 (min) | Pitch angle setpoint blade 1 | deg | Degrees | Minimum | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthAngTgt1_10m_Std | #N/A | WROT. | BlPthAngTgt1_10m_Std | Pitch angle setpoint blade 1 (std) | Pitchwinkel-Sollwert Blatt 1 (std) | Punto de ajuste del ángulo de paso pala 1 (std) | Kąt Pitch nastawa łopata 1 (std) | Pitch angle setpoint blade 1 | deg | Degrees | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthAngTgt2 | #N/A | WROT. | BlPthAngTgt2 | Pitch angle setpoint blade 2 | Pitchwinkel-Sollwert Blatt 2 | Punto de ajuste del ángulo de paso pala 2 | Kąt Pitch nastawa łopata 2 | Pitch angle setpoint blade 2 | deg | Degrees | Live Value | Double | Live Value
WROT.BlPthAngTgt2_10m_Avg | #N/A | WROT. | BlPthAngTgt2_10m_Avg | Pitch angle setpoint blade 2 (avg) | Pitchwinkel-Sollwert Blatt 2 (avg) | Punto de ajuste del ángulo de paso pala 2 (avg) | Kąt Pitch nastawa łopata 2 (avg) | Pitch angle setpoint blade 2 | deg | Degrees | Average | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthAngTgt2_10m_Max | #N/A | WROT. | BlPthAngTgt2_10m_Max | Pitch angle setpoint blade 2 (max) | Pitchwinkel-Sollwert Blatt 2 (max) | Punto de ajuste del ángulo de paso pala 2 (max) | Kąt Pitch nastawa łopata 2 (max) | Pitch angle setpoint blade 2 | deg | Degrees | Maximum | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthAngTgt2_10m_Min | #N/A | WROT. | BlPthAngTgt2_10m_Min | Pitch angle setpoint blade 2 (min) | Pitchwinkel-Sollwert Blatt 2 (min) | Punto de ajuste del ángulo de paso pala 2 (min) | Kąt Pitch nastawa łopata 2 (min) | Pitch angle setpoint blade 2 | deg | Degrees | Minimum | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthAngTgt2_10m_Std | #N/A | WROT. | BlPthAngTgt2_10m_Std | Pitch angle setpoint blade 2 (std) | Pitchwinkel-Sollwert Blatt 2 (std) | Punto de ajuste del ángulo de paso pala 2 (std) | Kąt Pitch nastawa łopata 2 (std) | Pitch angle setpoint blade 2 | deg | Degrees | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthAngTgt3 | #N/A | WROT. | BlPthAngTgt3 | Pitch angle setpoint blade 3 | Pitchwinkel-Sollwert Blatt 3 | Punto de ajuste del ángulo de paso pala 3 | Kąt Pitch nastawa łopata 3 | Pitch angle setpoint blade 3 | deg | Degrees | Live Value | Double | Live Value
WROT.BlPthAngTgt3_10m_Avg | #N/A | WROT. | BlPthAngTgt3_10m_Avg | Pitch angle setpoint blade 3 (avg) | Pitchwinkel-Sollwert Blatt 3 (avg) | Punto de ajuste del ángulo de paso pala 3 (avg) | Kąt Pitch nastawa łopata 3 (avg) | Pitch angle setpoint blade 3 | deg | Degrees | Average | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthAngTgt3_10m_Max | #N/A | WROT. | BlPthAngTgt3_10m_Max | Pitch angle setpoint blade 3 (max) | Pitchwinkel-Sollwert Blatt 3 (max) | Punto de ajuste del ángulo de paso pala 3 (max) | Kąt Pitch nastawa łopata 3 (max) | Pitch angle setpoint blade 3 | deg | Degrees | Maximum | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthAngTgt3_10m_Min | #N/A | WROT. | BlPthAngTgt3_10m_Min | Pitch angle setpoint blade 3 (min) | Pitchwinkel-Sollwert Blatt 3 (min) | Punto de ajuste del ángulo de paso pala 3 (min) | Kąt Pitch nastawa łopata 3 (min) | Pitch angle setpoint blade 3 | deg | Degrees | Minimum | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthAngTgt3_10m_Std | #N/A | WROT. | BlPthAngTgt3_10m_Std | Pitch angle setpoint blade 3 (std) | Pitchwinkel-Sollwert Blatt 3 (std) | Punto de ajuste del ángulo de paso pala 3 (std) | Kąt Pitch nastawa łopata 3 (std) | Pitch angle setpoint blade 3 | deg | Degrees | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthAngTgtErr1 | #N/A | WROT. | BlPthAngTgtErr1 | Pitch angle setpoint error blade 1 | Pitchwinkelsollwertfehler Blatt 1 | Error del punto de ajuste del ángulo de paso de la pala 1 | Kąt Pitch błąd nastawy łopata 1 | Pitch angle setpoint error blade 1 | deg | Degrees | Live Value | Double | Live Value
WROT.BlPthAngTgtErr1_10m_Avg | #N/A | WROT. | BlPthAngTgtErr1_10m_Avg | Pitch angle setpoint error blade 1 (avg) | Pitchwinkelsollwertfehler Blatt 1 (avg) | Error del punto de ajuste del ángulo de paso de la pala 1 (avg) | Kąt Pitch błąd nastawy łopata 1 (avg) | Pitch angle setpoint error blade 1 | deg | Degrees | Average | Double | 10 minute tag
WROT.BlPthAngTgtErr1_10m_Max | #N/A | WROT. | BlPthAngTgtErr1_10m_Max | Pitch angle setpoint error blade 1 (max) | Pitchwinkelsollwertfehler Blatt 1 (max) | Error del punto de ajuste del ángulo de paso de la pala 1 (max) | Kąt Pitch błąd nastawy łopata 1 (max) | Pitch angle setpoint error blade 1 | deg | Degrees | Maximum | Double | 10 minute tag
WROT.BlPthAngTgtErr1_10m_Min | #N/A | WROT. | BlPthAngTgtErr1_10m_Min | Pitch angle setpoint error blade 1 (min) | Pitchwinkelsollwertfehler Blatt 1 (min) | Error del punto de ajuste del ángulo de paso de la pala 1 (min) | Kąt Pitch błąd nastawy łopata 1 (min) | Pitch angle setpoint error blade 1 | deg | Degrees | Minimum | Double | 10 minute tag
WROT.BlPthAngTgtErr1_10m_Std | #N/A | WROT. | BlPthAngTgtErr1_10m_Std | Pitch angle setpoint error blade 1 (std) | Pitchwinkelsollwertfehler Blatt 1 (std) | Error del punto de ajuste del ángulo de paso de la pala 1 (std) | Kąt Pitch błąd nastawy łopata 1 (std) | Pitch angle setpoint error blade 1 | deg | Degrees | Standard Deviation | Double | 10 minute tag
WROT.BlPthAngTgtErr2 | #N/A | WROT. | BlPthAngTgtErr2 | Pitch angle setpoint error blade 2 | Pitchwinkelsollwertfehler Blatt 2 | Error del punto de ajuste del ángulo de paso de la pala 2 | Kąt Pitch błąd nastawy łopata 2 | Pitch angle setpoint error blade 2 | deg | Degrees | Live Value | Double | Live Value
WROT.BlPthAngTgtErr2_10m_Avg | #N/A | WROT. | BlPthAngTgtErr2_10m_Avg | Pitch angle setpoint error blade 2 (avg) | Pitchwinkelsollwertfehler Blatt 2 (avg) | Error del punto de ajuste del ángulo de paso de la pala 2 (avg) | Kąt Pitch błąd nastawy łopata 2 (avg) | Pitch angle setpoint error blade 2 | deg | Degrees | Average | Double | 10 minute tag
WROT.BlPthAngTgtErr2_10m_Max | #N/A | WROT. | BlPthAngTgtErr2_10m_Max | Pitch angle setpoint error blade 2 (max) | Pitchwinkelsollwertfehler Blatt 2 (max) | Error del punto de ajuste del ángulo de paso de la pala 2 (max) | Kąt Pitch błąd nastawy łopata 2 (max) | Pitch angle setpoint error blade 2 | deg | Degrees | Maximum | Double | 10 minute tag
WROT.BlPthAngTgtErr2_10m_Min | #N/A | WROT. | BlPthAngTgtErr2_10m_Min | Pitch angle setpoint error blade 2 (min) | Pitchwinkelsollwertfehler Blatt 2 (min) | Error del punto de ajuste del ángulo de paso de la pala 2 (min) | Kąt Pitch błąd nastawy łopata 2 (min) | Pitch angle setpoint error blade 2 | deg | Degrees | Minimum | Double | 10 minute tag
WROT.BlPthAngTgtErr2_10m_Std | #N/A | WROT. | BlPthAngTgtErr2_10m_Std | Pitch angle setpoint error blade 2 (std) | Pitchwinkelsollwertfehler Blatt 2 (std) | Error del punto de ajuste del ángulo de paso de la pala 2 (std) | Kąt Pitch błąd nastawy łopata 2 (std) | Pitch angle setpoint error blade 2 | deg | Degrees | Standard Deviation | Double | 10 minute tag
WROT.BlPthAngTgtErr3 | #N/A | WROT. | BlPthAngTgtErr3 | Pitch angle setpoint error blade 3 | Pitchwinkelsollwertfehler Blatt 3 | Error del punto de ajuste del ángulo de paso de la pala 3 | Kąt Pitch błąd nastawy łopata 3 | Pitch angle setpoint error blade 3 | deg | Degrees | Live Value | Double | Live Value
WROT.BlPthAngTgtErr3_10m_Avg | #N/A | WROT. | BlPthAngTgtErr3_10m_Avg | Pitch angle setpoint error blade 3 (avg) | Pitchwinkelsollwertfehler Blatt 3 (avg) | Error del punto de ajuste del ángulo de paso de la pala 3 (avg) | Kąt Pitch błąd nastawy łopata 3 (avg) | Pitch angle setpoint error blade 3 | deg | Degrees | Average | Double | 10 minute tag
WROT.BlPthAngTgtErr3_10m_Max | #N/A | WROT. | BlPthAngTgtErr3_10m_Max | Pitch angle setpoint error blade 3 (max) | Pitchwinkelsollwertfehler Blatt 3 (max) | Error del punto de ajuste del ángulo de paso de la pala 3 (max) | Kąt Pitch błąd nastawy łopata 3 (max) | Pitch angle setpoint error blade 3 | deg | Degrees | Maximum | Double | 10 minute tag
WROT.BlPthAngTgtErr3_10m_Min | #N/A | WROT. | BlPthAngTgtErr3_10m_Min | Pitch angle setpoint error blade 3 (min) | Pitchwinkelsollwertfehler Blatt 3 (min) | Error del punto de ajuste del ángulo de paso de la pala 3 (min) | Kąt Pitch błąd nastawy łopata 3 (min) | Pitch angle setpoint error blade 3 | deg | Degrees | Minimum | Double | 10 minute tag
WROT.BlPthAngTgtErr3_10m_Std | #N/A | WROT. | BlPthAngTgtErr3_10m_Std | Pitch angle setpoint error blade 3 (std) | Pitchwinkelsollwertfehler Blatt 3 (std) | Error del punto de ajuste del ángulo de paso de la pala 3 (std) | Kąt Pitch błąd nastawy łopata 3 (std) | Pitch angle setpoint error blade 3 | deg | Degrees | Standard Deviation | Double | 10 minute tag
WROT.BlPthAngVal | WROT.BlPthAngVal | WROT. | BlPthAngVal | Pitch angle | Pitchwinkel | Ángulo de paso | Kąt Pitch | Pitch angle for blade as feedback from the pitch system | deg | Degrees | Live Value | Double | Live Value | Used in standard monitor Presentation
WROT.BlPthAngVal_10m_Avg | #N/A | WROT. | BlPthAngVal_10m_Avg | Pitch angle (avg) | Pitchwinkel (avg) | Ángulo de paso (avg) | Kąt Pitch (avg) | Pitch angle for blade as feedback from the pitch system | deg | Degrees | Average | Double | 10 minute tag | Common tags for analysis
WROT.BlPthAngVal_10m_Max | #N/A | WROT. | BlPthAngVal_10m_Max | Pitch angle (max) | Pitchwinkel (max) | Ángulo de paso (max) | Kąt Pitch (max) | Pitch angle for blade as feedback from the pitch system | deg | Degrees | Maximum | Double | 10 minute tag | Common tags for analysis
WROT.BlPthAngVal_10m_Min | #N/A | WROT. | BlPthAngVal_10m_Min | Pitch angle (min) | Pitchwinkel (min) | Ángulo de paso (min) | Kąt Pitch (min) | Pitch angle for blade as feedback from the pitch system | deg | Degrees | Minimum | Double | 10 minute tag | Common tags for analysis
WROT.BlPthAngVal_10m_Std | #N/A | WROT. | BlPthAngVal_10m_Std | Pitch angle (std) | Pitchwinkel (std) | Ángulo de paso (std) | Kąt Pitch (std) | Pitch angle for blade as feedback from the pitch system | deg | Degrees | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WROT.BlPthAngVal1 | #N/A | WROT. | BlPthAngVal1 | Pitch angle of blade 1 | Pitchwinkel Blatt 1 | Ángulo de paso de la pala 1 | Kąt Pitch łopata 1 | Pitch angle of blade 1 | deg | Degrees | Live Value | Double | Live Value | Used in standard monitor Presentation
WROT.BlPthAngVal1_10m_Avg | #N/A | WROT. | BlPthAngVal1_10m_Avg | Pitch angle of blade 1 (avg) | Pitchwinkel Blatt 1 (avg) | Ángulo de paso de la pala 1 (avg) | Kąt Pitch łopata 1 (avg) | Pitch angle of blade 1 | deg | Degrees | Average | Double | 10 minute tag | Common tags for analysis
WROT.BlPthAngVal1_10m_Max | #N/A | WROT. | BlPthAngVal1_10m_Max | Pitch angle of blade 1 (max) | Pitchwinkel Blatt 1 (max) | Ángulo de paso de la pala 1 (max) | Kąt Pitch łopata 1 (max) | Pitch angle of blade 1 | deg | Degrees | Maximum | Double | 10 minute tag | Common tags for analysis
WROT.BlPthAngVal1_10m_Min | #N/A | WROT. | BlPthAngVal1_10m_Min | Pitch angle of blade 1 (min) | Pitchwinkel Blatt 1 (min) | Ángulo de paso de la pala 1 (min) | Kąt Pitch łopata 1 (min) | Pitch angle of blade 1 | deg | Degrees | Minimum | Double | 10 minute tag | Common tags for analysis
WROT.BlPthAngVal1_10m_Std | #N/A | WROT. | BlPthAngVal1_10m_Std | Pitch angle of blade 1 (std) | Pitchwinkel Blatt 1 (std) | Ángulo de paso de la pala 1 (std) | Kąt Pitch łopata 1 (std) | Pitch angle of blade 1 | deg | Degrees | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WROT.BlPthAngVal2 | #N/A | WROT. | BlPthAngVal2 | Pitch angle of blade 2 | Pitchwinkel Blatt 2 | Ángulo de paso de la pala 2 | Kąt Pitch łopata 2 | Pitch angle of blade 2 | deg | Degrees | Live Value | Double | Live Value
WROT.BlPthAngVal2_10m_Avg | #N/A | WROT. | BlPthAngVal2_10m_Avg | Pitch angle of blade 2 (avg) | Pitchwinkel Blatt 2 (avg) | Ángulo de paso de la pala 2 (avg) | Kąt Pitch łopata 2 (avg) | Pitch angle of blade 2 | deg | Degrees | Average | Double | 10 minute tag | Common tags for analysis
WROT.BlPthAngVal2_10m_Max | #N/A | WROT. | BlPthAngVal2_10m_Max | Pitch angle of blade 2 (max) | Pitchwinkel Blatt 2 (max) | Ángulo de paso de la pala 2 (max) | Kąt Pitch łopata 2 (max) | Pitch angle of blade 2 | deg | Degrees | Maximum | Double | 10 minute tag | Common tags for analysis
WROT.BlPthAngVal2_10m_Min | #N/A | WROT. | BlPthAngVal2_10m_Min | Pitch angle of blade 2 (min) | Pitchwinkel Blatt 2 (min) | Ángulo de paso de la pala 2 (min) | Kąt Pitch łopata 2 (min) | Pitch angle of blade 2 | deg | Degrees | Minimum | Double | 10 minute tag | Common tags for analysis
WROT.BlPthAngVal2_10m_Std | #N/A | WROT. | BlPthAngVal2_10m_Std | Pitch angle of blade 2 (std) | Pitchwinkel Blatt 2 (std) | Ángulo de paso de la pala 2 (std) | Kąt Pitch łopata 2 (std) | Pitch angle of blade 2 | deg | Degrees | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WROT.BlPthAngVal3 | #N/A | WROT. | BlPthAngVal3 | Pitch angle of blade 3 | Pitchwinkel Blatt 3 | Ángulo de paso de la pala 3 | Kąt Pitch łopata 3 | Pitch angle of blade 3 | deg | Degrees | Live Value | Double | Live Value
WROT.BlPthAngVal3_10m_Avg | #N/A | WROT. | BlPthAngVal3_10m_Avg | Pitch angle of blade 3 (avg) | Pitchwinkel Blatt 3 (avg) | Ángulo de paso de la pala 3 (avg) | Kąt Pitch łopata 3 (avg) | Pitch angle of blade 3 | deg | Degrees | Average | Double | 10 minute tag | Common tags for analysis
WROT.BlPthAngVal3_10m_Max | #N/A | WROT. | BlPthAngVal3_10m_Max | Pitch angle of blade 3 (max) | Pitchwinkel Blatt 3 (max) | Ángulo de paso de la pala 3 (max) | Kąt Pitch łopata 3 (max) | Pitch angle of blade 3 | deg | Degrees | Maximum | Double | 10 minute tag | Common tags for analysis
WROT.BlPthAngVal3_10m_Min | #N/A | WROT. | BlPthAngVal3_10m_Min | Pitch angle of blade 3 (min) | Pitchwinkel Blatt 3 (min) | Ángulo de paso de la pala 3 (min) | Kąt Pitch łopata 3 (min) | Pitch angle of blade 3 | deg | Degrees | Minimum | Double | 10 minute tag | Common tags for analysis
WROT.BlPthAngVal3_10m_Std | #N/A | WROT. | BlPthAngVal3_10m_Std | Pitch angle of blade 3 (std) | Pitchwinkel Blatt 3 (std) | Ángulo de paso de la pala 3 (std) | Kąt Pitch łopata 3 (std) | Pitch angle of blade 3 | deg | Degrees | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WROT.BlPthBatChaMaxTmp1 | #N/A | WROT. | BlPthBatChaMaxTmp1 | Pitch Battery Charger 1 Max Temp | Pitch Batterieladegerät 1 Max Temperatur | Temperatura máxima del cargador 1 de batería de paso | Bateria pitch 1 Max Temp | Electrical pitch battery charger maximum temperature blade 1 | deg_c | °C | Live Value | Double | Live Value
WROT.BlPthBatChaMaxTmp1_10m_Avg | #N/A | WROT. | BlPthBatChaMaxTmp1_10m_Avg | Pitch Battery Charger 1 Max Temp (avg) | Pitch Batterieladegerät 1 Max Temperatur (avg) | Temperatura máxima del cargador 1 de batería de paso (avg) | Bateria pitch 1 Max Temp (avg) | Electrical pitch battery charger maximum temperature blade 1 | deg_c | °C | Average | Double | 10 minute tag
WROT.BlPthBatChaMaxTmp1_10m_Max | #N/A | WROT. | BlPthBatChaMaxTmp1_10m_Max | Pitch Battery Charger 1 Max Temp (max) | Pitch Batterieladegerät 1 Max Temperatur (max) | Temperatura máxima del cargador 1 de batería de paso (max) | Bateria pitch 1 Max Temp (max) | Electrical pitch battery charger maximum temperature blade 1 | deg_c | °C | Maximum | Double | 10 minute tag
WROT.BlPthBatChaMaxTmp1_10m_Min | #N/A | WROT. | BlPthBatChaMaxTmp1_10m_Min | Pitch Battery Charger 1 Max Temp (min) | Pitch Batterieladegerät 1 Max Temperatur (min) | Temperatura máxima del cargador 1 de batería de paso (min) | Bateria pitch 1 Max Temp (min) | Electrical pitch battery charger maximum temperature blade 1 | deg_c | °C | Minimum | Double | 10 minute tag
WROT.BlPthBatChaMaxTmp1_10m_Std | #N/A | WROT. | BlPthBatChaMaxTmp1_10m_Std | Pitch Battery Charger 1 Max Temp (std) | Pitch Batterieladegerät 1 Max Temperatur (std) | Temperatura máxima del cargador 1 de batería de paso (std) | Bateria pitch 1 Max Temp (std) | Electrical pitch battery charger maximum temperature blade 1 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.BlPthBatChaMaxTmp2 | #N/A | WROT. | BlPthBatChaMaxTmp2 | Pitch Battery Charger 2 Max Temp | Pitch Batterieladegerät 2 Max Temperatur | Temperatura máxima del cargador 2 de batería de paso | Bateria pitch 2 Max Temp | Electrical pitch battery charger maximum temperature blade 2 | deg_c | °C | Live Value | Double | Live Value
WROT.BlPthBatChaMaxTmp2_10m_Avg | #N/A | WROT. | BlPthBatChaMaxTmp2_10m_Avg | Pitch Battery Charger 2 Max Temp (avg) | Pitch Batterieladegerät 2 Max Temperatur (avg) | Temperatura máxima del cargador 2 de batería de paso (avg) | Bateria pitch 2 Max Temp (avg) | Electrical pitch battery charger maximum temperature blade 2 | deg_c | °C | Average | Double | 10 minute tag
WROT.BlPthBatChaMaxTmp2_10m_Max | #N/A | WROT. | BlPthBatChaMaxTmp2_10m_Max | Pitch Battery Charger 2 Max Temp (max) | Pitch Batterieladegerät 2 Max Temperatur (max) | Temperatura máxima del cargador 2 de batería de paso (max) | Bateria pitch 2 Max Temp (max) | Electrical pitch battery charger maximum temperature blade 2 | deg_c | °C | Maximum | Double | 10 minute tag
WROT.BlPthBatChaMaxTmp2_10m_Min | #N/A | WROT. | BlPthBatChaMaxTmp2_10m_Min | Pitch Battery Charger 2 Max Temp (min) | Pitch Batterieladegerät 2 Max Temperatur (min) | Temperatura máxima del cargador 2 de batería de paso (min) | Bateria pitch 2 Max Temp (min) | Electrical pitch battery charger maximum temperature blade 2 | deg_c | °C | Minimum | Double | 10 minute tag
WROT.BlPthBatChaMaxTmp2_10m_Std | #N/A | WROT. | BlPthBatChaMaxTmp2_10m_Std | Pitch Battery Charger 2 Max Temp (std) | Pitch Batterieladegerät 2 Max Temperatur (std) | Temperatura máxima del cargador 2 de batería de paso (std) | Bateria pitch 2 Max Temp (std) | Electrical pitch battery charger maximum temperature blade 2 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.BlPthBatChaMaxTmp3 | #N/A | WROT. | BlPthBatChaMaxTmp3 | Pitch Battery Charger 3 Max Temp | Pitch Batterieladegerät 3 Max Temperatur | Temperatura máxima del cargador 3 de batería de paso | Bateria pitch 3 Max Temp | Electrical pitch battery charger maximum temperature blade 3 | deg_c | °C | Live Value | Double | Live Value
WROT.BlPthBatChaMaxTmp3_10m_Avg | #N/A | WROT. | BlPthBatChaMaxTmp3_10m_Avg | Pitch Battery Charger 3 Max Temp (avg) | Pitch Batterieladegerät 3 Max Temperatur (avg) | Temperatura máxima del cargador 3 de batería de paso (avg) | Bateria pitch 3 Max Temp (avg) | Electrical pitch battery charger maximum temperature blade 3 | deg_c | °C | Average | Double | 10 minute tag
WROT.BlPthBatChaMaxTmp3_10m_Max | #N/A | WROT. | BlPthBatChaMaxTmp3_10m_Max | Pitch Battery Charger 3 Max Temp (max) | Pitch Batterieladegerät 3 Max Temperatur (max) | Temperatura máxima del cargador 3 de batería de paso (max) | Bateria pitch 3 Max Temp (max) | Electrical pitch battery charger maximum temperature blade 3 | deg_c | °C | Maximum | Double | 10 minute tag
WROT.BlPthBatChaMaxTmp3_10m_Min | #N/A | WROT. | BlPthBatChaMaxTmp3_10m_Min | Pitch Battery Charger 3 Max Temp (min) | Pitch Batterieladegerät 3 Max Temperatur (min) | Temperatura máxima del cargador 3 de batería de paso (min) | Bateria pitch 3 Max Temp (min) | Electrical pitch battery charger maximum temperature blade 3 | deg_c | °C | Minimum | Double | 10 minute tag
WROT.BlPthBatChaMaxTmp3_10m_Std | #N/A | WROT. | BlPthBatChaMaxTmp3_10m_Std | Pitch Battery Charger 3 Max Temp (std) | Pitch Batterieladegerät 3 Max Temperatur (std) | Temperatura máxima del cargador 3 de batería de paso (std) | Bateria pitch 3 Max Temp (std) | Electrical pitch battery charger maximum temperature blade 3 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.BlPthBatPnlTmp1 | #N/A | WROT. | BlPthBatPnlTmp1 | Pitch Battery Panel 1 Temp | Pitch Batteriepanel 1 Temperatur | Temperatura del panel 1 de batería de paso | Panel baterii pitch 1 Temp | Electrical pitch battery panel temperature blade 1 | deg_c | °C | Live Value | Double | Live Value
WROT.BlPthBatPnlTmp1_10m_Avg | #N/A | WROT. | BlPthBatPnlTmp1_10m_Avg | Pitch Battery Panel 1 Temp (avg) | Pitch Batteriepanel 1 Temperatur (avg) | Temperatura del panel 1 de batería de paso (avg) | Panel baterii pitch 1 Temp (avg) | Electrical pitch battery panel temperature blade 1 | deg_c | °C | Average | Double | 10 minute tag
WROT.BlPthBatPnlTmp1_10m_Max | #N/A | WROT. | BlPthBatPnlTmp1_10m_Max | Pitch Battery Panel 1 Temp (max) | Pitch Batteriepanel 1 Temperatur (max) | Temperatura del panel 1 de batería de paso (max) | Panel baterii pitch 1 Temp (max) | Electrical pitch battery panel temperature blade 1 | deg_c | °C | Maximum | Double | 10 minute tag
WROT.BlPthBatPnlTmp1_10m_Min | #N/A | WROT. | BlPthBatPnlTmp1_10m_Min | Pitch Battery Panel 1 Temp (min) | Pitch Batteriepanel 1 Temperatur (min) | Temperatura del panel 1 de batería de paso (min) | Panel baterii pitch 1 Temp (min) | Electrical pitch battery panel temperature blade 1 | deg_c | °C | Minimum | Double | 10 minute tag
WROT.BlPthBatPnlTmp1_10m_Std | #N/A | WROT. | BlPthBatPnlTmp1_10m_Std | Pitch Battery Panel 1 Temp (std) | Pitch Batteriepanel 1 Temperatur (std) | Temperatura del panel 1 de batería de paso (std) | Panel baterii pitch 1 Temp (std) | Electrical pitch battery panel temperature blade 1 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.BlPthBatPnlTmp2 | #N/A | WROT. | BlPthBatPnlTmp2 | Pitch Battery Panel 2 Temp | Pitch Batteriepanel 2 Temperatur | Temperatura del panel 2 de batería de paso | Panel baterii pitch 2 Temp | Electrical pitch battery panel temperature blade 2 | deg_c | °C | Live Value | Double | Live Value
WROT.BlPthBatPnlTmp2_10m_Avg | #N/A | WROT. | BlPthBatPnlTmp2_10m_Avg | Pitch Battery Panel 2 Temp (avg) | Pitch Batteriepanel 2 Temperatur (avg) | Temperatura del panel 2 de batería de paso (avg) | Panel baterii pitch 2 Temp (avg) | Electrical pitch battery panel temperature blade 2 | deg_c | °C | Average | Double | 10 minute tag
WROT.BlPthBatPnlTmp2_10m_Max | #N/A | WROT. | BlPthBatPnlTmp2_10m_Max | Pitch Battery Panel 2 Temp (max) | Pitch Batteriepanel 2 Temperatur (max) | Temperatura del panel 2 de batería de paso (max) | Panel baterii pitch 2 Temp (max) | Electrical pitch battery panel temperature blade 2 | deg_c | °C | Maximum | Double | 10 minute tag
WROT.BlPthBatPnlTmp2_10m_Min | #N/A | WROT. | BlPthBatPnlTmp2_10m_Min | Pitch Battery Panel 2 Temp (min) | Pitch Batteriepanel 2 Temperatur (min) | Temperatura del panel 2 de batería de paso (min) | Panel baterii pitch 2 Temp (min) | Electrical pitch battery panel temperature blade 2 | deg_c | °C | Minimum | Double | 10 minute tag
WROT.BlPthBatPnlTmp2_10m_Std | #N/A | WROT. | BlPthBatPnlTmp2_10m_Std | Pitch Battery Panel 2 Temp (std) | Pitch Batteriepanel 2 Temperatur (std) | Temperatura del panel 2 de batería de paso (std) | Panel baterii pitch 2 Temp (std) | Electrical pitch battery panel temperature blade 2 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.BlPthBatPnlTmp3 | #N/A | WROT. | BlPthBatPnlTmp3 | Pitch Battery Panel 3 Temp | Pitch Batteriepanel 3 Temperatur | Temperatura del panel 3 de batería de paso | Panel baterii pitch 3 Temp | Electrical pitch battery panel temperature blade 3 | deg_c | °C | Live Value | Double | Live Value
WROT.BlPthBatPnlTmp3_10m_Avg | #N/A | WROT. | BlPthBatPnlTmp3_10m_Avg | Pitch Battery Panel 3 Temp (avg) | Pitch Batteriepanel 3 Temperatur (avg) | Temperatura del panel 3 de batería de paso (avg) | Panel baterii pitch 3 Temp (avg) | Electrical pitch battery panel temperature blade 3 | deg_c | °C | Average | Double | 10 minute tag
WROT.BlPthBatPnlTmp3_10m_Max | #N/A | WROT. | BlPthBatPnlTmp3_10m_Max | Pitch Battery Panel 3 Temp (max) | Pitch Batteriepanel 3 Temperatur (max) | Temperatura del panel 3 de batería de paso (max) | Panel baterii pitch 3 Temp (max) | Electrical pitch battery panel temperature blade 3 | deg_c | °C | Maximum | Double | 10 minute tag
WROT.BlPthBatPnlTmp3_10m_Min | #N/A | WROT. | BlPthBatPnlTmp3_10m_Min | Pitch Battery Panel 3 Temp (min) | Pitch Batteriepanel 3 Temperatur (min) | Temperatura del panel 3 de batería de paso (min) | Panel baterii pitch 3 Temp (min) | Electrical pitch battery panel temperature blade 3 | deg_c | °C | Minimum | Double | 10 minute tag
WROT.BlPthBatPnlTmp3_10m_Std | #N/A | WROT. | BlPthBatPnlTmp3_10m_Std | Pitch Battery Panel 3 Temp (std) | Pitch Batteriepanel 3 Temperatur (std) | Temperatura del panel 3 de batería de paso (std) | Panel baterii pitch 3 Temp (std) | Electrical pitch battery panel temperature blade 3 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.BlPthBatSt | #N/A | WROT. | BlPthBatSt | Pitch Battery Status | Pitch Batteriestatus | Estado de batería de paso | Stan baterii pitch | Status of pitch battery 0: Ok 1: Battery test needed | Enum | Enum | Live Value | Long | Live Value
WROT.BlPthCtlV1_10m_Avg | #N/A | WROT. | BlPthCtlV1_10m_Avg | Control voltage pitch valve 1 (avg) | Steuerspannung Pitchventil 1 (avg) | Válvula 1 de control de paso de tensión (avg) | Nap. sterow. pitch zawór 1 (avg) | Control voltage to the pitch propotional valve 1 | V | V | Average | Double | 10 minute tag
WROT.BlPthCtlV1_10m_Max | #N/A | WROT. | BlPthCtlV1_10m_Max | Control voltage pitch valve 1 (max) | Steuerspannung Pitchventil 1 (max) | Válvula 1 de control de paso de tensión (max) | Nap. sterow. pitch zawór 1 (max) | Control voltage to the pitch propotional valve 1 | V | V | Maximum | Double | 10 minute tag
WROT.BlPthCtlV1_10m_Min | #N/A | WROT. | BlPthCtlV1_10m_Min | Control voltage pitch valve 1 (min) | Steuerspannung Pitchventil 1 (min) | Válvula 1 de control de paso de tensión (min) | Nap. sterow. pitch zawór 1 (min) | Control voltage to the pitch propotional valve 1 | V | V | Minimum | Double | 10 minute tag
WROT.BlPthCtlV1_10m_Std | #N/A | WROT. | BlPthCtlV1_10m_Std | Control voltage pitch valve 1 (std) | Steuerspannung Pitchventil 1 (std) | Válvula 1 de control de paso de tensión (std) | Nap. sterow. pitch zawór 1 (std) | Control voltage to the pitch propotional valve 1 | V | V | Standard Deviation | Double | 10 minute tag
WROT.BlPthCtlV2_10m_Avg | #N/A | WROT. | BlPthCtlV2_10m_Avg | Control voltage pitch valve 2 (avg) | Steuerspannung Pitchventil 2 (avg) | Válvula 2 de control de paso de tensión (avg) | Nap. sterow. pitch zawór 2 (avg) | Control voltage to the pitch propotional valve 2 | V | V | Average | Double | 10 minute tag
WROT.BlPthCtlV2_10m_Max | #N/A | WROT. | BlPthCtlV2_10m_Max | Control voltage pitch valve 2 (max) | Steuerspannung Pitchventil 2 (max) | Válvula 2 de control de paso de tensión (max) | Nap. sterow. pitch zawór 2 (max) | Control voltage to the pitch propotional valve 2 | V | V | Maximum | Double | 10 minute tag
WROT.BlPthCtlV2_10m_Min | #N/A | WROT. | BlPthCtlV2_10m_Min | Control voltage pitch valve 2 (min) | Steuerspannung Pitchventil 2 (min) | Válvula 2 de control de paso de tensión (min) | Nap. sterow. pitch zawór 2 (min) | Control voltage to the pitch propotional valve 2 | V | V | Minimum | Double | 10 minute tag
WROT.BlPthCtlV2_10m_Std | #N/A | WROT. | BlPthCtlV2_10m_Std | Control voltage pitch valve 2 (std) | Steuerspannung Pitchventil 2 (std) | Válvula 2 de control de paso de tensión (std) | Nap. sterow. pitch zawór 2 (std) | Control voltage to the pitch propotional valve 2 | V | V | Standard Deviation | Double | 10 minute tag
WROT.BlPthCtlV3_10m_Avg | #N/A | WROT. | BlPthCtlV3_10m_Avg | Control voltage pitch valve 3 (avg) | Steuerspannung Pitchventil 3 (avg) | Válvula 3 de control de paso de tensión (avg) | Nap. sterow. pitch zawór 3 (avg) | Control voltage to the pitch propotional valve 3 | V | V | Average | Double | 10 minute tag
WROT.BlPthCtlV3_10m_Max | #N/A | WROT. | BlPthCtlV3_10m_Max | Control voltage pitch valve 3 (max) | Steuerspannung Pitchventil 3 (max) | Válvula 3 de control de paso de tensión (max) | Nap. sterow. pitch zawór 3 (max) | Control voltage to the pitch propotional valve 3 | V | V | Maximum | Double | 10 minute tag
WROT.BlPthCtlV3_10m_Min | #N/A | WROT. | BlPthCtlV3_10m_Min | Control voltage pitch valve 3 (min) | Steuerspannung Pitchventil 3 (min) | Válvula 3 de control de paso de tensión (min) | Nap. sterow. pitch zawór 3 (min) | Control voltage to the pitch propotional valve 3 | V | V | Minimum | Double | 10 minute tag
WROT.BlPthCtlV3_10m_Std | #N/A | WROT. | BlPthCtlV3_10m_Std | Control voltage pitch valve 3 (std) | Steuerspannung Pitchventil 3 (std) | Válvula 3 de control de paso de tensión (std) | Nap. sterow. pitch zawór 3 (std) | Control voltage to the pitch propotional valve 3 | V | V | Standard Deviation | Double | 10 minute tag
WROT.BlPthDCV1 | #N/A | WROT. | BlPthDCV1 | DC voltage blade 1 | Gleichspannung Blatt 1 | Tensión CC de la pala 1 | Nap. DC łopata 1 | Electrical pitch dc voltage blade 1 | V | V | Live Value | Double | Live Value
WROT.BlPthDCV1_10m_Avg | #N/A | WROT. | BlPthDCV1_10m_Avg | DC voltage blade 1 (avg) | Gleichspannung Blatt 1 (avg) | Tensión CC de la pala 1 (avg) | Nap. DC łopata 1 (avg) | Electrical pitch dc voltage blade 1 | V | V | Average | Double | 10 minute tag
WROT.BlPthDCV1_10m_Max | #N/A | WROT. | BlPthDCV1_10m_Max | DC voltage blade 1 (max) | Gleichspannung Blatt 1 (max) | Tensión CC de la pala 1 (max) | Nap. DC łopata 1 (max) | Electrical pitch dc voltage blade 1 | V | V | Maximum | Double | 10 minute tag
WROT.BlPthDCV1_10m_Min | #N/A | WROT. | BlPthDCV1_10m_Min | DC voltage blade 1 (min) | Gleichspannung Blatt 1 (min) | Tensión CC de la pala 1 (min) | Nap. DC łopata 1 (min) | Electrical pitch dc voltage blade 1 | V | V | Minimum | Double | 10 minute tag
WROT.BlPthDCV1_10m_Std | #N/A | WROT. | BlPthDCV1_10m_Std | DC voltage blade 1 (std) | Gleichspannung Blatt 1 (std) | Tensión CC de la pala 1 (std) | Nap. DC łopata 1 (std) | Electrical pitch dc voltage blade 1 | V | V | Standard Deviation | Double | 10 minute tag
WROT.BlPthDCV2 | #N/A | WROT. | BlPthDCV2 | DC voltage blade 2 | Gleichspannung Blatt 2 | Tensión CC de la pala 2 | Nap. DC łopata 2 | Electrical pitch dc voltage blade 2 | V | V | Live Value | Double | Live Value
WROT.BlPthDCV2_10m_Avg | #N/A | WROT. | BlPthDCV2_10m_Avg | DC voltage blade 2 (avg) | Gleichspannung Blatt 2 (avg) | Tensión CC de la pala 2 (avg) | Nap. DC łopata 2 (avg) | Electrical pitch dc voltage blade 2 | V | V | Average | Double | 10 minute tag
WROT.BlPthDCV2_10m_Max | #N/A | WROT. | BlPthDCV2_10m_Max | DC voltage blade 2 (max) | Gleichspannung Blatt 2 (max) | Tensión CC de la pala 2 (max) | Nap. DC łopata 2 (max) | Electrical pitch dc voltage blade 2 | V | V | Maximum | Double | 10 minute tag
WROT.BlPthDCV2_10m_Min | #N/A | WROT. | BlPthDCV2_10m_Min | DC voltage blade 2 (min) | Gleichspannung Blatt 2 (min) | Tensión CC de la pala 2 (min) | Nap. DC łopata 2 (min) | Electrical pitch dc voltage blade 2 | V | V | Minimum | Double | 10 minute tag
WROT.BlPthDCV2_10m_Std | #N/A | WROT. | BlPthDCV2_10m_Std | DC voltage blade 2 (std) | Gleichspannung Blatt 2 (std) | Tensión CC de la pala 2 (std) | Nap. DC łopata 2 (std) | Electrical pitch dc voltage blade 2 | V | V | Standard Deviation | Double | 10 minute tag
WROT.BlPthDCV3 | #N/A | WROT. | BlPthDCV3 | DC voltage blade 3 | Gleichspannung Blatt 3 | Tensión CC de la pala 3 | Nap. DC łopata 3 | Electrical pitch dc voltage blade 3 | V | V | Live Value | Double | Live Value
WROT.BlPthDCV3_10m_Avg | #N/A | WROT. | BlPthDCV3_10m_Avg | DC voltage blade 3 (avg) | Gleichspannung Blatt 3 (avg) | Tensión CC de la pala 3 (avg) | Nap. DC łopata 3 (avg) | Electrical pitch dc voltage blade 3 | V | V | Average | Double | 10 minute tag
WROT.BlPthDCV3_10m_Max | #N/A | WROT. | BlPthDCV3_10m_Max | DC voltage blade 3 (max) | Gleichspannung Blatt 3 (max) | Tensión CC de la pala 3 (max) | Nap. DC łopata 3 (max) | Electrical pitch dc voltage blade 3 | V | V | Maximum | Double | 10 minute tag
WROT.BlPthDCV3_10m_Min | #N/A | WROT. | BlPthDCV3_10m_Min | DC voltage blade 3 (min) | Gleichspannung Blatt 3 (min) | Tensión CC de la pala 3 (min) | Nap. DC łopata 3 (min) | Electrical pitch dc voltage blade 3 | V | V | Minimum | Double | 10 minute tag
WROT.BlPthDCV3_10m_Std | #N/A | WROT. | BlPthDCV3_10m_Std | DC voltage blade 3 (std) | Gleichspannung Blatt 3 (std) | Tensión CC de la pala 3 (std) | Nap. DC łopata 3 (std) | Electrical pitch dc voltage blade 3 | V | V | Standard Deviation | Double | 10 minute tag
WROT.BlPthHtSnkTmp1 | #N/A | WROT. | BlPthHtSnkTmp1 | Electrical pitch Heatsink 1 Temp | Elektrischer Pitch Kühlkörper 1 Temperatur | Temperatura del disipador térmico 1 del paso eléctrico | Elektryczny radiator pitch 1 Temp | Electrical pitch control Panel heatsink temperature blade 1 | deg_c | °C | Live Value | Double | Live Value
WROT.BlPthHtSnkTmp1_10m_Avg | #N/A | WROT. | BlPthHtSnkTmp1_10m_Avg | Electrical pitch Heatsink 1 Temp (avg) | Elektrischer Pitch Kühlkörper 1 Temperatur (avg) | Temperatura del disipador térmico 1 del paso eléctrico (avg) | Elektryczny radiator pitch 1 Temp (avg) | Electrical pitch control Panel heatsink temperature blade 1 | deg_c | °C | Average | Double | 10 minute tag
WROT.BlPthHtSnkTmp1_10m_Max | #N/A | WROT. | BlPthHtSnkTmp1_10m_Max | Electrical pitch Heatsink 1 Temp (max) | Elektrischer Pitch Kühlkörper 1 Temperatur (max) | Temperatura del disipador térmico 1 del paso eléctrico (max) | Elektryczny radiator pitch 1 Temp (max) | Electrical pitch control Panel heatsink temperature blade 1 | deg_c | °C | Maximum | Double | 10 minute tag
WROT.BlPthHtSnkTmp1_10m_Min | #N/A | WROT. | BlPthHtSnkTmp1_10m_Min | Electrical pitch Heatsink 1 Temp (min) | Elektrischer Pitch Kühlkörper 1 Temperatur (min) | Temperatura del disipador térmico 1 del paso eléctrico (min) | Elektryczny radiator pitch 1 Temp (min) | Electrical pitch control Panel heatsink temperature blade 1 | deg_c | °C | Minimum | Double | 10 minute tag
WROT.BlPthHtSnkTmp1_10m_Std | #N/A | WROT. | BlPthHtSnkTmp1_10m_Std | Electrical pitch Heatsink 1 Temp (std) | Elektrischer Pitch Kühlkörper 1 Temperatur (std) | Temperatura del disipador térmico 1 del paso eléctrico (std) | Elektryczny radiator pitch 1 Temp (std) | Electrical pitch control Panel heatsink temperature blade 1 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.BlPthHtSnkTmp2 | #N/A | WROT. | BlPthHtSnkTmp2 | Electrical pitch Heatsink 2 Temp | Elektrischer Pitch Kühlkörper 2 Temperatur | Temperatura del disipador térmico 2 del paso eléctrico | Elektryczny radiator 2 Temp | Electrical pitch control Panel heatsink temperature blade 2 | deg_c | °C | Live Value | Double | Live Value
WROT.BlPthHtSnkTmp2_10m_Avg | #N/A | WROT. | BlPthHtSnkTmp2_10m_Avg | Electrical pitch Heatsink 2 Temp (avg) | Elektrischer Pitch Kühlkörper 2 Temperatur (avg) | Temperatura del disipador térmico 2 del paso eléctrico (avg) | Elektryczny radiator 2 Temp (avg) | Electrical pitch control Panel heatsink temperature blade 2 | deg_c | °C | Average | Double | 10 minute tag
WROT.BlPthHtSnkTmp2_10m_Max | #N/A | WROT. | BlPthHtSnkTmp2_10m_Max | Electrical pitch Heatsink 2 Temp (max) | Elektrischer Pitch Kühlkörper 2 Temperatur (max) | Temperatura del disipador térmico 2 del paso eléctrico (max) | Elektryczny radiator 2 Temp (max) | Electrical pitch control Panel heatsink temperature blade 2 | deg_c | °C | Maximum | Double | 10 minute tag
WROT.BlPthHtSnkTmp2_10m_Min | #N/A | WROT. | BlPthHtSnkTmp2_10m_Min | Electrical pitch Heatsink 2 Temp (min) | Elektrischer Pitch Kühlkörper 2 Temperatur (min) | Temperatura del disipador térmico 2 del paso eléctrico (min) | Elektryczny radiator 2 Temp (min) | Electrical pitch control Panel heatsink temperature blade 2 | deg_c | °C | Minimum | Double | 10 minute tag
WROT.BlPthHtSnkTmp2_10m_Std | #N/A | WROT. | BlPthHtSnkTmp2_10m_Std | Electrical pitch Heatsink 2 Temp (std) | Elektrischer Pitch Kühlkörper 2 Temperatur (std) | Temperatura del disipador térmico 2 del paso eléctrico (std) | Elektryczny radiator 2 Temp (std) | Electrical pitch control Panel heatsink temperature blade 2 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.BlPthHtSnkTmp3 | #N/A | WROT. | BlPthHtSnkTmp3 | Electrical pitch Heatsink 3 Temp | Elektrischer Pitch Kühlkörper 3 Temperatur | Temperatura del disipador térmico 3 del paso eléctrico | Elektryczny radiator 3 Temp | Electrical pitch control Panel heatsink temperature blade 3 | deg_c | °C | Live Value | Double | Live Value
WROT.BlPthHtSnkTmp3_10m_Avg | #N/A | WROT. | BlPthHtSnkTmp3_10m_Avg | Electrical pitch Heatsink 3 Temp (avg) | Elektrischer Pitch Kühlkörper 3 Temperatur (avg) | Temperatura del disipador térmico 3 del paso eléctrico (avg) | Elektryczny radiator 3 Temp (avg) | Electrical pitch control Panel heatsink temperature blade 3 | deg_c | °C | Average | Double | 10 minute tag
WROT.BlPthHtSnkTmp3_10m_Max | #N/A | WROT. | BlPthHtSnkTmp3_10m_Max | Electrical pitch Heatsink 3 Temp (max) | Elektrischer Pitch Kühlkörper 3 Temperatur (max) | Temperatura del disipador térmico 3 del paso eléctrico (max) | Elektryczny radiator 3 Temp (max) | Electrical pitch control Panel heatsink temperature blade 3 | deg_c | °C | Maximum | Double | 10 minute tag
WROT.BlPthHtSnkTmp3_10m_Min | #N/A | WROT. | BlPthHtSnkTmp3_10m_Min | Electrical pitch Heatsink 3 Temp (min) | Elektrischer Pitch Kühlkörper 3 Temperatur (min) | Temperatura del disipador térmico 3 del paso eléctrico (min) | Elektryczny radiator 3 Temp (min) | Electrical pitch control Panel heatsink temperature blade 3 | deg_c | °C | Minimum | Double | 10 minute tag
WROT.BlPthHtSnkTmp3_10m_Std | #N/A | WROT. | BlPthHtSnkTmp3_10m_Std | Electrical pitch Heatsink 3 Temp (std) | Elektrischer Pitch Kühlkörper 3 Temperatur (std) | Temperatura del disipador térmico 3 del paso eléctrico (std) | Elektryczny radiator 3 Temp (std) | Electrical pitch control Panel heatsink temperature blade 3 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.BlPthHyPres | WROT.BlPthHyPres | WROT. | BlPthHyPres | Hydraulic Oil Pitch Pressure | Hydrauliköl Pitch Druck | Presión de paso de aceite hidráulico | Ciśnienie skoku oleju hydr. | Hydraulic pressure pitch, not specific for any blade | bar | bar | Live Value | Double | Live Value
WROT.BlPthHyPres_10m_Avg | #N/A | WROT. | BlPthHyPres_10m_Avg | Hydraulic Oil Pitch Pressure (avg) | Hydrauliköl Pitch Druck (avg) | Presión de paso de aceite hidráulico (avg) | Ciśnienie skoku oleju hydr. (avg) | Hydraulic pressure pitch, not specific for any blade | bar | bar | Average | Double | 10 minute tag
WROT.BlPthHyPres_10m_Max | #N/A | WROT. | BlPthHyPres_10m_Max | Hydraulic Oil Pitch Pressure (max) | Hydrauliköl Pitch Druck (max) | Presión de paso de aceite hidráulico (max) | Ciśnienie skoku oleju hydr. (max) | Hydraulic pressure pitch, not specific for any blade | bar | bar | Maximum | Double | 10 minute tag
WROT.BlPthHyPres_10m_Min | #N/A | WROT. | BlPthHyPres_10m_Min | Hydraulic Oil Pitch Pressure (min) | Hydrauliköl Pitch Druck (min) | Presión de paso de aceite hidráulico (min) | Ciśnienie skoku oleju hydr. (min) | Hydraulic pressure pitch, not specific for any blade | bar | bar | Minimum | Double | 10 minute tag
WROT.BlPthHyPres_10m_Std | #N/A | WROT. | BlPthHyPres_10m_Std | Hydraulic Oil Pitch Pressure (std) | Hydrauliköl Pitch Druck (std) | Presión de paso de aceite hidráulico (std) | Ciśnienie skoku oleju hydr. (std) | Hydraulic pressure pitch, not specific for any blade | bar | bar | Standard Deviation | Double | 10 minute tag
WROT.BlPthHyPres1 | #N/A | WROT. | BlPthHyPres1 | Hydraulic Oil Pitch Blade 1 Pressure | Hydrauliköl Pitch Blatt 1 Druck | Presión de paso de aceite hidráulico de la pala 1 | Olej hydr. łopata 1 Ciśnienie | Hydraulic oil pressure for blade 1 pitch system | bar | bar | Live Value | Double | Live Value
WROT.BlPthHyPres1_10m_Avg | #N/A | WROT. | BlPthHyPres1_10m_Avg | Hydraulic Oil Pitch Blade 1 Pressure (avg) | Hydrauliköl Pitch Blatt 1 Druck (avg) | Presión de paso de aceite hidráulico de la pala 1 (avg) | Olej hydr. łopata 1 Ciśnienie (avg) | Hydraulic oil pressure for blade 1 pitch system | bar | bar | Average | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthHyPres1_10m_Max | #N/A | WROT. | BlPthHyPres1_10m_Max | Hydraulic Oil Pitch Blade 1 Pressure (max) | Hydrauliköl Pitch Blatt 1 Druck (max) | Presión de paso de aceite hidráulico de la pala 1 (max) | Olej hydr. łopata 1 Ciśnienie (max) | Hydraulic oil pressure for blade 1 pitch system | bar | bar | Maximum | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthHyPres1_10m_Min | #N/A | WROT. | BlPthHyPres1_10m_Min | Hydraulic Oil Pitch Blade 1 Pressure (min) | Hydrauliköl Pitch Blatt 1 Druck (min) | Presión de paso de aceite hidráulico de la pala 1 (min) | Olej hydr. łopata 1 Ciśnienie (min) | Hydraulic oil pressure for blade 1 pitch system | bar | bar | Minimum | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthHyPres1_10m_Std | #N/A | WROT. | BlPthHyPres1_10m_Std | Hydraulic Oil Pitch Blade 1 Pressure (std) | Hydrauliköl Pitch Blatt 1 Druck (std) | Presión de paso de aceite hidráulico de la pala 1 (std) | Olej hydr. łopata 1 Ciśnienie (std) | Hydraulic oil pressure for blade 1 pitch system | bar | bar | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthHyPres2 | #N/A | WROT. | BlPthHyPres2 | Hydraulic Oil Pitch Blade 2 Pressure | Hydrauliköl Pitch Blatt 2 Druck | Presión de paso de aceite hidráulico de la pala 2 | Olej hydr. łopata 2 Ciśnienie | Hydraulic oil pressure for blade 2 pitch system | bar | bar | Live Value | Double | Live Value
WROT.BlPthHyPres2_10m_Avg | #N/A | WROT. | BlPthHyPres2_10m_Avg | Hydraulic Oil Pitch Blade 2 Pressure (avg) | Hydrauliköl Pitch Blatt 2 Druck (avg) | Presión de paso de aceite hidráulico de la pala 2 (avg) | Olej hydr. łopata 2 Ciśnienie (avg) | Hydraulic oil pressure for blade 2 pitch system | bar | bar | Average | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthHyPres2_10m_Max | #N/A | WROT. | BlPthHyPres2_10m_Max | Hydraulic Oil Pitch Blade 2 Pressure (max) | Hydrauliköl Pitch Blatt 2 Druck (max) | Presión de paso de aceite hidráulico de la pala 2 (max) | Olej hydr. łopata 2 Ciśnienie (max) | Hydraulic oil pressure for blade 2 pitch system | bar | bar | Maximum | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthHyPres2_10m_Min | #N/A | WROT. | BlPthHyPres2_10m_Min | Hydraulic Oil Pitch Blade 2 Pressure (min) | Hydrauliköl Pitch Blatt 2 Druck (min) | Presión de paso de aceite hidráulico de la pala 2 (min) | Olej hydr. łopata 2 Ciśnienie (min) | Hydraulic oil pressure for blade 2 pitch system | bar | bar | Minimum | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthHyPres2_10m_Std | #N/A | WROT. | BlPthHyPres2_10m_Std | Hydraulic Oil Pitch Blade 2 Pressure (std) | Hydrauliköl Pitch Blatt 2 Druck (std) | Presión de paso de aceite hidráulico de la pala 2 (std) | Olej hydr. łopata 2 Ciśnienie (std) | Hydraulic oil pressure for blade 2 pitch system | bar | bar | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthHyPres3 | #N/A | WROT. | BlPthHyPres3 | Hydraulic Oil Pitch Blade 3 Pressure | Hydrauliköl Pitch Blatt 3 Druck | Presión de paso de aceite hidráulico de la pala 3 | Olej hydr. łopata 3 Ciśnienie | Hydraulic oil pressure for blade 3 pitch system | bar | bar | Live Value | Double | Live Value
WROT.BlPthHyPres3_10m_Avg | #N/A | WROT. | BlPthHyPres3_10m_Avg | Hydraulic Oil Pitch Blade 3 Pressure (avg) | Hydrauliköl Pitch Blatt 3 Druck (avg) | Presión de paso de aceite hidráulico de la pala 3 (avg) | Olej hydr. łopata 3 Ciśnienie (avg) | Hydraulic oil pressure for blade 3 pitch system | bar | bar | Average | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthHyPres3_10m_Max | #N/A | WROT. | BlPthHyPres3_10m_Max | Hydraulic Oil Pitch Blade 3 Pressure (max) | Hydrauliköl Pitch Blatt 3 Druck (max) | Presión de paso de aceite hidráulico de la pala 3 (max) | Olej hydr. łopata 3 Ciśnienie (max) | Hydraulic oil pressure for blade 3 pitch system | bar | bar | Maximum | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthHyPres3_10m_Min | #N/A | WROT. | BlPthHyPres3_10m_Min | Hydraulic Oil Pitch Blade 3 Pressure (min) | Hydrauliköl Pitch Blatt 3 Druck (min) | Presión de paso de aceite hidráulico de la pala 3 (min) | Olej hydr. łopata 3 Ciśnienie (min) | Hydraulic oil pressure for blade 3 pitch system | bar | bar | Minimum | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthHyPres3_10m_Std | #N/A | WROT. | BlPthHyPres3_10m_Std | Hydraulic Oil Pitch Blade 3 Pressure (std) | Hydrauliköl Pitch Blatt 3 Druck (std) | Presión de paso de aceite hidráulico de la pala 3 (std) | Olej hydr. łopata 3 Ciśnienie (std) | Hydraulic oil pressure for blade 3 pitch system | bar | bar | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WROT.BlPthHyTmp | #N/A | WROT. | BlPthHyTmp | Hydraulic Pitch Temp | Hydraulik Pitch Temperatur | Temperatura de paso hidráulico | Pitch hydr. temp | Temperature of hydraulic pitch system | deg_c | °C | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WROT.BlPthMotSpd1 | #N/A | WROT. | BlPthMotSpd1 | Pitch Motor 1 RPM | Pitch Motor 1 Drehzahl | RPM del motor de paso 1 | Pitch Motor 1 obr./min | Electrical pitch motor RPM Blade 1 | rpm | RPM | Live Value | Double | Live Value
WROT.BlPthMotSpd1_10m_Avg | #N/A | WROT. | BlPthMotSpd1_10m_Avg | Pitch Motor 1 RPM (avg) | Pitch Motor 1 Drehzahl (avg) | RPM del motor de paso 1 (avg) | Pitch Motor 1 obr./min (avg) | Electrical pitch motor RPM Blade 1 | rpm | RPM | Average | Double | 10 minute tag
WROT.BlPthMotSpd1_10m_Max | #N/A | WROT. | BlPthMotSpd1_10m_Max | Pitch Motor 1 RPM (max) | Pitch Motor 1 Drehzahl (max) | RPM del motor de paso 1 (max) | Pitch Motor 1 obr./min (max) | Electrical pitch motor RPM Blade 1 | rpm | RPM | Maximum | Double | 10 minute tag
WROT.BlPthMotSpd1_10m_Min | #N/A | WROT. | BlPthMotSpd1_10m_Min | Pitch Motor 1 RPM (min) | Pitch Motor 1 Drehzahl (min) | RPM del motor de paso 1 (min) | Pitch Motor 1 obr./min (min) | Electrical pitch motor RPM Blade 1 | rpm | RPM | Minimum | Double | 10 minute tag
WROT.BlPthMotSpd1_10m_Std | #N/A | WROT. | BlPthMotSpd1_10m_Std | Pitch Motor 1 RPM (std) | Pitch Motor 1 Drehzahl (std) | RPM del motor de paso 1 (std) | Pitch Motor 1 obr./min (std) | Electrical pitch motor RPM Blade 1 | rpm | RPM | Standard Deviation | Double | 10 minute tag
WROT.BlPthMotSpd2 | #N/A | WROT. | BlPthMotSpd2 | Pitch Motor 2 RPM | Pitch Motor 2 Drehzahl | RPM del motor de paso 2 | Pitch Motor 2 obr./min | Electrical pitch motor RPM Blade 2 | rpm | RPM | Live Value | Double | Live Value
WROT.BlPthMotSpd2_10m_Avg | #N/A | WROT. | BlPthMotSpd2_10m_Avg | Pitch Motor 2 RPM (avg) | Pitch Motor 2 Drehzahl (avg) | RPM del motor de paso 2 (avg) | Pitch Motor 2 obr./min (avg) | Electrical pitch motor RPM Blade 2 | rpm | RPM | Average | Double | 10 minute tag
WROT.BlPthMotSpd2_10m_Max | #N/A | WROT. | BlPthMotSpd2_10m_Max | Pitch Motor 2 RPM (max) | Pitch Motor 2 Drehzahl (max) | RPM del motor de paso 2 (max) | Pitch Motor 2 obr./min (max) | Electrical pitch motor RPM Blade 2 | rpm | RPM | Maximum | Double | 10 minute tag
WROT.BlPthMotSpd2_10m_Min | #N/A | WROT. | BlPthMotSpd2_10m_Min | Pitch Motor 2 RPM (min) | Pitch Motor 2 Drehzahl (min) | RPM del motor de paso 2 (min) | Pitch Motor 2 obr./min (min) | Electrical pitch motor RPM Blade 2 | rpm | RPM | Minimum | Double | 10 minute tag
WROT.BlPthMotSpd2_10m_Std | #N/A | WROT. | BlPthMotSpd2_10m_Std | Pitch Motor 2 RPM (std) | Pitch Motor 2 Drehzahl (std) | RPM del motor de paso 2 (std) | Pitch Motor 2 obr./min (std) | Electrical pitch motor RPM Blade 2 | rpm | RPM | Standard Deviation | Double | 10 minute tag
WROT.BlPthMotSpd3 | #N/A | WROT. | BlPthMotSpd3 | Pitch Motor 3 RPM | Pitch Motor 3 Drehzahl | RPM del motor de paso 3 | Pitch Motor 3 obr./min | Electrical pitch motor RPM Blade 3 | rpm | RPM | Live Value | Double | Live Value
WROT.BlPthMotSpd3_10m_Avg | #N/A | WROT. | BlPthMotSpd3_10m_Avg | Pitch Motor 3 RPM (avg) | Pitch Motor 3 Drehzahl (avg) | RPM del motor de paso 3 (avg) | Pitch Motor 3 obr./min (avg) | Electrical pitch motor RPM Blade 3 | rpm | RPM | Average | Double | 10 minute tag
WROT.BlPthMotSpd3_10m_Max | #N/A | WROT. | BlPthMotSpd3_10m_Max | Pitch Motor 3 RPM (max) | Pitch Motor 3 Drehzahl (max) | RPM del motor de paso 3 (max) | Pitch Motor 3 obr./min (max) | Electrical pitch motor RPM Blade 3 | rpm | RPM | Maximum | Double | 10 minute tag
WROT.BlPthMotSpd3_10m_Min | #N/A | WROT. | BlPthMotSpd3_10m_Min | Pitch Motor 3 RPM (min) | Pitch Motor 3 Drehzahl (min) | RPM del motor de paso 3 (min) | Pitch Motor 3 obr./min (min) | Electrical pitch motor RPM Blade 3 | rpm | RPM | Minimum | Double | 10 minute tag
WROT.BlPthMotSpd3_10m_Std | #N/A | WROT. | BlPthMotSpd3_10m_Std | Pitch Motor 3 RPM (std) | Pitch Motor 3 Drehzahl (std) | RPM del motor de paso 3 (std) | Pitch Motor 3 obr./min (std) | Electrical pitch motor RPM Blade 3 | rpm | RPM | Standard Deviation | Double | 10 minute tag
WROT.BlPthMotTmp1 | #N/A | WROT. | BlPthMotTmp1 | Pitch Motor 1 Temp | Pitch Motor 1 Temperatur | Temperatura del motor de paso 1 | Pitch Motor 1 Temp | Electrical pitch motor temperature blade 1 | deg_c | °C | Live Value | Double | Live Value
WROT.BlPthMotTmp1_10m_Avg | #N/A | WROT. | BlPthMotTmp1_10m_Avg | Pitch Motor 1 Temp (avg) | Pitch Motor 1 Temperatur (avg) | Temperatura del motor de paso 1 (avg) | Pitch Motor 1 Temp (avg) | Electrical pitch motor temperature blade 1 | deg_c | °C | Average | Double | 10 minute tag
WROT.BlPthMotTmp1_10m_Max | #N/A | WROT. | BlPthMotTmp1_10m_Max | Pitch Motor 1 Temp (max) | Pitch Motor 1 Temperatur (max) | Temperatura del motor de paso 1 (max) | Pitch Motor 1 Temp (max) | Electrical pitch motor temperature blade 1 | deg_c | °C | Maximum | Double | 10 minute tag
WROT.BlPthMotTmp1_10m_Min | #N/A | WROT. | BlPthMotTmp1_10m_Min | Pitch Motor 1 Temp (min) | Pitch Motor 1 Temperatur (min) | Temperatura del motor de paso 1 (min) | Pitch Motor 1 Temp (min) | Electrical pitch motor temperature blade 1 | deg_c | °C | Minimum | Double | 10 minute tag
WROT.BlPthMotTmp1_10m_Std | #N/A | WROT. | BlPthMotTmp1_10m_Std | Pitch Motor 1 Temp (std) | Pitch Motor 1 Temperatur (std) | Temperatura del motor de paso 1 (std) | Pitch Motor 1 Temp (std) | Electrical pitch motor temperature blade 1 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.BlPthMotTmp2 | #N/A | WROT. | BlPthMotTmp2 | Pitch Motor 2 Temp | Pitch Motor 2 Temperatur | Temperatura del motor de paso 2 | Pitch Motor 2 Temp | Electrical pitch motor temperature blade 2 | deg_c | °C | Live Value | Double | Live Value
WROT.BlPthMotTmp2_10m_Avg | #N/A | WROT. | BlPthMotTmp2_10m_Avg | Pitch Motor 2 Temp (avg) | Pitch Motor 2 Temperatur (avg) | Temperatura del motor de paso 2 (avg) | Pitch Motor 2 Temp (avg) | Electrical pitch motor temperature blade 2 | deg_c | °C | Average | Double | 10 minute tag
WROT.BlPthMotTmp2_10m_Max | #N/A | WROT. | BlPthMotTmp2_10m_Max | Pitch Motor 2 Temp (max) | Pitch Motor 2 Temperatur (max) | Temperatura del motor de paso 2 (max) | Pitch Motor 2 Temp (max) | Electrical pitch motor temperature blade 2 | deg_c | °C | Maximum | Double | 10 minute tag
WROT.BlPthMotTmp2_10m_Min | #N/A | WROT. | BlPthMotTmp2_10m_Min | Pitch Motor 2 Temp (min) | Pitch Motor 2 Temperatur (min) | Temperatura del motor de paso 2 (min) | Pitch Motor 2 Temp (min) | Electrical pitch motor temperature blade 2 | deg_c | °C | Minimum | Double | 10 minute tag
WROT.BlPthMotTmp2_10m_Std | #N/A | WROT. | BlPthMotTmp2_10m_Std | Pitch Motor 2 Temp (std) | Pitch Motor 2 Temperatur (std) | Temperatura del motor de paso 2 (std) | Pitch Motor 2 Temp (std) | Electrical pitch motor temperature blade 2 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.BlPthMotTmp3 | #N/A | WROT. | BlPthMotTmp3 | Pitch Motor 3 Temp | Pitch Motor 3 Temperatur | Temperatura del motor de paso 3 | Pitch Motor 3 Temp | Electrical pitch motor temperature blade 3 | deg_c | °C | Live Value | Double | Live Value
WROT.BlPthMotTmp3_10m_Avg | #N/A | WROT. | BlPthMotTmp3_10m_Avg | Pitch Motor 3 Temp (avg) | Pitch Motor 3 Temperatur (avg) | Temperatura del motor de paso 3 (avg) | Pitch Motor 3 Temp (avg) | Electrical pitch motor temperature blade 3 | deg_c | °C | Average | Double | 10 minute tag
WROT.BlPthMotTmp3_10m_Max | #N/A | WROT. | BlPthMotTmp3_10m_Max | Pitch Motor 3 Temp (max) | Pitch Motor 3 Temperatur (max) | Temperatura del motor de paso 3 (max) | Pitch Motor 3 Temp (max) | Electrical pitch motor temperature blade 3 | deg_c | °C | Maximum | Double | 10 minute tag
WROT.BlPthMotTmp3_10m_Min | #N/A | WROT. | BlPthMotTmp3_10m_Min | Pitch Motor 3 Temp (min) | Pitch Motor 3 Temperatur (min) | Temperatura del motor de paso 3 (min) | Pitch Motor 3 Temp (min) | Electrical pitch motor temperature blade 3 | deg_c | °C | Minimum | Double | 10 minute tag
WROT.BlPthMotTmp3_10m_Std | #N/A | WROT. | BlPthMotTmp3_10m_Std | Pitch Motor 3 Temp (std) | Pitch Motor 3 Temperatur (std) | Temperatura del motor de paso 3 (std) | Pitch Motor 3 Temp (std) | Electrical pitch motor temperature blade 3 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.BlPthPistPos1 | #N/A | WROT. | BlPthPistPos1 | Pitch hydraulic piston position blade 1 | Pitch Hydraulikkolben Position Blatt 1 | Posición de paso del pistón hidráulico de la pala 1 | Pitch hydr. położ. tłoka łopata 1 | Pitch hydraulic piston position blade 1 |  |  | Live Value | Double | Live Value
WROT.BlPthPistPos1_10m_Avg | #N/A | WROT. | BlPthPistPos1_10m_Avg | Pitch hydraulic piston position blade 1 (avg) | Pitch Hydraulikkolben Position Blatt 1 (avg) | Posición de paso del pistón hidráulico de la pala 1 (avg) | Pitch hydr. położ. tłoka łopata 1 (avg) | Pitch hydraulic piston position blade 1 |  |  | Average | Double | 10 minute tag
WROT.BlPthPistPos1_10m_Max | #N/A | WROT. | BlPthPistPos1_10m_Max | Pitch hydraulic piston position blade 1 (max) | Pitch Hydraulikkolben Position Blatt 1 (max) | Posición de paso del pistón hidráulico de la pala 1 (max) | Pitch hydr. położ. tłoka łopata 1 (max) | Pitch hydraulic piston position blade 1 |  |  | Maximum | Double | 10 minute tag
WROT.BlPthPistPos1_10m_Min | #N/A | WROT. | BlPthPistPos1_10m_Min | Pitch hydraulic piston position blade 1 (min) | Pitch Hydraulikkolben Position Blatt 1 (min) | Posición de paso del pistón hidráulico de la pala 1 (min) | Pitch hydr. położ. tłoka łopata 1 (min) | Pitch hydraulic piston position blade 1 |  |  | Minimum | Double | 10 minute tag
WROT.BlPthPistPos1_10m_Std | #N/A | WROT. | BlPthPistPos1_10m_Std | Pitch hydraulic piston position blade 1 (std) | Pitch Hydraulikkolben Position Blatt 1 (std) | Posición de paso del pistón hidráulico de la pala 1 (std) | Pitch hydr. położ. tłoka łopata 1 (std) | Pitch hydraulic piston position blade 1 |  |  | Standard Deviation | Double | 10 minute tag
WROT.BlPthPistPos2 | #N/A | WROT. | BlPthPistPos2 | Pitch hydraulic piston position blade 2 | Pitch Hydraulikkolben Position Blatt 2 | Posición de paso del pistón hidráulico de la pala 2 | Pitch hydr. położ. tłoka łopata 2 | Pitch hydraulic piston position blade 2 |  |  | Live Value | Double | Live Value
WROT.BlPthPistPos2_10m_Avg | #N/A | WROT. | BlPthPistPos2_10m_Avg | Pitch hydraulic piston position blade 2 (avg) | Pitch Hydraulikkolben Position Blatt 2 (avg) | Posición de paso del pistón hidráulico de la pala 2 (avg) | Pitch hydr. położ. tłoka łopata 2 (avg) | Pitch hydraulic piston position blade 2 |  |  | Average | Double | 10 minute tag
WROT.BlPthPistPos2_10m_Max | #N/A | WROT. | BlPthPistPos2_10m_Max | Pitch hydraulic piston position blade 2 (max) | Pitch Hydraulikkolben Position Blatt 2 (max) | Posición de paso del pistón hidráulico de la pala 2 (max) | Pitch hydr. położ. tłoka łopata 2 (max) | Pitch hydraulic piston position blade 2 |  |  | Maximum | Double | 10 minute tag
WROT.BlPthPistPos2_10m_Min | #N/A | WROT. | BlPthPistPos2_10m_Min | Pitch hydraulic piston position blade 2 (min) | Pitch Hydraulikkolben Position Blatt 2 (min) | Posición de paso del pistón hidráulico de la pala 2 (min) | Pitch hydr. położ. tłoka łopata 2 (min) | Pitch hydraulic piston position blade 2 |  |  | Minimum | Double | 10 minute tag
WROT.BlPthPistPos2_10m_Std | #N/A | WROT. | BlPthPistPos2_10m_Std | Pitch hydraulic piston position blade 2 (std) | Pitch Hydraulikkolben Position Blatt 2 (std) | Posición de paso del pistón hidráulico de la pala 2 (std) | Pitch hydr. położ. tłoka łopata 2 (std) | Pitch hydraulic piston position blade 2 |  |  | Standard Deviation | Double | 10 minute tag
WROT.BlPthPistPos3 | #N/A | WROT. | BlPthPistPos3 | Pitch hydraulic piston position blade 3 | Pitch Hydraulikkolben Position Blatt 3 | Posición de paso del pistón hidráulico de la pala 3 | Pitch hydr. położ. tłoka łopata 3 | Pitch hydraulic piston position blade 3 |  |  | Live Value | Double | Live Value
WROT.BlPthPistPos3_10m_Avg | #N/A | WROT. | BlPthPistPos3_10m_Avg | Pitch hydraulic piston position blade 3 (avg) | Pitch Hydraulikkolben Position Blatt 3 (avg) | Posición de paso del pistón hidráulico de la pala 3 (avg) | Pitch hydr. położ. tłoka łopata 3 (avg) | Pitch hydraulic piston position blade 3 |  |  | Average | Double | 10 minute tag
WROT.BlPthPistPos3_10m_Max | #N/A | WROT. | BlPthPistPos3_10m_Max | Pitch hydraulic piston position blade 3 (max) | Pitch Hydraulikkolben Position Blatt 3 (max) | Posición de paso del pistón hidráulico de la pala 3 (max) | Pitch hydr. położ. tłoka łopata 3 (max) | Pitch hydraulic piston position blade 3 |  |  | Maximum | Double | 10 minute tag
WROT.BlPthPistPos3_10m_Min | #N/A | WROT. | BlPthPistPos3_10m_Min | Pitch hydraulic piston position blade 3 (min) | Pitch Hydraulikkolben Position Blatt 3 (min) | Posición de paso del pistón hidráulico de la pala 3 (min) | Pitch hydr. położ. tłoka łopata 3 (min) | Pitch hydraulic piston position blade 3 |  |  | Minimum | Double | 10 minute tag
WROT.BlPthPistPos3_10m_Std | #N/A | WROT. | BlPthPistPos3_10m_Std | Pitch hydraulic piston position blade 3 (std) | Pitch Hydraulikkolben Position Blatt 3 (std) | Posición de paso del pistón hidráulico de la pala 3 (std) | Pitch hydr. położ. tłoka łopata 3 (std) | Pitch hydraulic piston position blade 3 |  |  | Standard Deviation | Double | 10 minute tag
WROT.BlPthPistVlvPos1 | #N/A | WROT. | BlPthPistVlvPos1 | Pitch hydraulic piston valve position blade 1 | Pitch Hydraulikkolben Ventilposition Blatt 1 | Posición de paso de la válvula del pistón hidráulico de la pala 1 | Pitch hydr. położ. zaworu tłoka łopata 1 | Pitch hydraulic piston proportional valve position blade 1 |  |  | Live Value | Double | Live Value
WROT.BlPthPistVlvPos1_10m_Avg | #N/A | WROT. | BlPthPistVlvPos1_10m_Avg | Pitch hydraulic piston valve position blade 1 (avg) | Pitch Hydraulikkolben Ventilposition Blatt 1 (avg) | Posición de paso de la válvula del pistón hidráulico de la pala 1 (avg) | Pitch hydr. położ. zaworu tłoka łopata 1 (avg) | Pitch hydraulic piston proportional valve position blade 1 |  |  | Average | Double | 10 minute tag
WROT.BlPthPistVlvPos1_10m_Max | #N/A | WROT. | BlPthPistVlvPos1_10m_Max | Pitch hydraulic piston valve position blade 1 (max) | Pitch Hydraulikkolben Ventilposition Blatt 1 (max) | Posición de paso de la válvula del pistón hidráulico de la pala 1 (max) | Pitch hydr. położ. zaworu tłoka łopata 1 (max) | Pitch hydraulic piston proportional valve position blade 1 |  |  | Maximum | Double | 10 minute tag
WROT.BlPthPistVlvPos1_10m_Min | #N/A | WROT. | BlPthPistVlvPos1_10m_Min | Pitch hydraulic piston valve position blade 1 (min) | Pitch Hydraulikkolben Ventilposition Blatt 1 (min) | Posición de paso de la válvula del pistón hidráulico de la pala 1 (min) | Pitch hydr. położ. zaworu tłoka łopata 1 (min) | Pitch hydraulic piston proportional valve position blade 1 |  |  | Minimum | Double | 10 minute tag
WROT.BlPthPistVlvPos1_10m_Std | #N/A | WROT. | BlPthPistVlvPos1_10m_Std | Pitch hydraulic piston valve position blade 1 (std) | Pitch Hydraulikkolben Ventilposition Blatt 1 (std) | Posición de paso de la válvula del pistón hidráulico de la pala 1 (std) | Pitch hydr. położ. zaworu tłoka łopata 1 (std) | Pitch hydraulic piston proportional valve position blade 1 |  |  | Standard Deviation | Double | 10 minute tag
WROT.BlPthPistVlvPos2 | #N/A | WROT. | BlPthPistVlvPos2 | Pitch hydraulic piston valve position blade 2 | Pitch Hydraulikkolben Ventilposition Blatt 2 | Posición de paso de la válvula del pistón hidráulico de la pala 2 | Pitch hydr. położ. zaworu tłoka łopata 2 | Pitch hydraulic piston proportional valve position blade 2 |  |  | Live Value | Double | Live Value
WROT.BlPthPistVlvPos2_10m_Avg | #N/A | WROT. | BlPthPistVlvPos2_10m_Avg | Pitch hydraulic piston valve position blade 2 (avg) | Pitch Hydraulikkolben Ventilposition Blatt 2 (avg) | Posición de paso de la válvula del pistón hidráulico de la pala 2 (avg) | Pitch hydr. położ. zaworu tłoka łopata 2 (avg) | Pitch hydraulic piston proportional valve position blade 2 |  |  | Average | Double | 10 minute tag
WROT.BlPthPistVlvPos2_10m_Max | #N/A | WROT. | BlPthPistVlvPos2_10m_Max | Pitch hydraulic piston valve position blade 2 (max) | Pitch Hydraulikkolben Ventilposition Blatt 2 (max) | Posición de paso de la válvula del pistón hidráulico de la pala 2 (max) | Pitch hydr. położ. zaworu tłoka łopata 2 (max) | Pitch hydraulic piston proportional valve position blade 2 |  |  | Maximum | Double | 10 minute tag
WROT.BlPthPistVlvPos2_10m_Min | #N/A | WROT. | BlPthPistVlvPos2_10m_Min | Pitch hydraulic piston valve position blade 2 (min) | Pitch Hydraulikkolben Ventilposition Blatt 2 (min) | Posición de paso de la válvula del pistón hidráulico de la pala 2 (min) | Pitch hydr. położ. zaworu tłoka łopata 2 (min) | Pitch hydraulic piston proportional valve position blade 2 |  |  | Minimum | Double | 10 minute tag
WROT.BlPthPistVlvPos2_10m_Std | #N/A | WROT. | BlPthPistVlvPos2_10m_Std | Pitch hydraulic piston valve position blade 2 (std) | Pitch Hydraulikkolben Ventilposition Blatt 2 (std) | Posición de paso de la válvula del pistón hidráulico de la pala 2 (std) | Pitch hydr. położ. zaworu tłoka łopata 2 (std) | Pitch hydraulic piston proportional valve position blade 2 |  |  | Standard Deviation | Double | 10 minute tag
WROT.BlPthPistVlvPos3 | #N/A | WROT. | BlPthPistVlvPos3 | Pitch hydraulic piston valve position blade 3 | Pitch Hydraulikkolben Ventilposition Blatt 3 | Posición de paso de la válvula del pistón hidráulico de la pala 3 | Pitch hydr. położ. zaworu tłoka łopata 3 | Pitch hydraulic piston proportional valve position blade 3 |  |  | Live Value | Double | Live Value
WROT.BlPthPistVlvPos3_10m_Avg | #N/A | WROT. | BlPthPistVlvPos3_10m_Avg | Pitch hydraulic piston valve position blade 3 (avg) | Pitch Hydraulikkolben Ventilposition Blatt 3 (avg) | Posición de paso de la válvula del pistón hidráulico de la pala 3 (avg) | Pitch hydr. położ. zaworu tłoka łopata 3 (avg) | Pitch hydraulic piston proportional valve position blade 3 |  |  | Average | Double | 10 minute tag
WROT.BlPthPistVlvPos3_10m_Max | #N/A | WROT. | BlPthPistVlvPos3_10m_Max | Pitch hydraulic piston valve position blade 3 (max) | Pitch Hydraulikkolben Ventilposition Blatt 3 (max) | Posición de paso de la válvula del pistón hidráulico de la pala 3 (max) | Pitch hydr. położ. zaworu tłoka łopata 3 (max) | Pitch hydraulic piston proportional valve position blade 3 |  |  | Maximum | Double | 10 minute tag
WROT.BlPthPistVlvPos3_10m_Min | #N/A | WROT. | BlPthPistVlvPos3_10m_Min | Pitch hydraulic piston valve position blade 3 (min) | Pitch Hydraulikkolben Ventilposition Blatt 3 (min) | Posición de paso de la válvula del pistón hidráulico de la pala 3 (min) | Pitch hydr. położ. zaworu tłoka łopata 3 (min) | Pitch hydraulic piston proportional valve position blade 3 |  |  | Minimum | Double | 10 minute tag
WROT.BlPthPistVlvPos3_10m_Std | #N/A | WROT. | BlPthPistVlvPos3_10m_Std | Pitch hydraulic piston valve position blade 3 (std) | Pitch Hydraulikkolben Ventilposition Blatt 3 (std) | Posición de paso de la válvula del pistón hidráulico de la pala 3 (std) | Pitch hydr. położ. zaworu tłoka łopata 3 (std) | Pitch hydraulic piston proportional valve position blade 3 |  |  | Standard Deviation | Double | 10 minute tag
WROT.BlPthPnlTmp1 | #N/A | WROT. | BlPthPnlTmp1 | Pitch Control Panel 1 Temp | Pitchsteuerung Panel 1 Temperatur | Temperatura de paso del panel 1 de control | Pitch Panel sterow. 1 Temp | Electrical pitch control Panel/Box temperature blade 1 | deg_c | °C | Live Value | Double | Live Value
WROT.BlPthPnlTmp1_10m_Avg | #N/A | WROT. | BlPthPnlTmp1_10m_Avg | Pitch Control Panel 1 Temp (avg) | Pitchsteuerung Panel 1 Temperatur (avg) | Temperatura de paso del panel 1 de control (avg) | Pitch Panel sterow. 1 Temp (avg) | Electrical pitch control Panel/Box temperature blade 1 | deg_c | °C | Average | Double | 10 minute tag
WROT.BlPthPnlTmp1_10m_Max | #N/A | WROT. | BlPthPnlTmp1_10m_Max | Pitch Control Panel 1 Temp (max) | Pitchsteuerung Panel 1 Temperatur (max) | Temperatura de paso del panel 1 de control (max) | Pitch Panel sterow. 1 Temp (max) | Electrical pitch control Panel/Box temperature blade 1 | deg_c | °C | Maximum | Double | 10 minute tag
WROT.BlPthPnlTmp1_10m_Min | #N/A | WROT. | BlPthPnlTmp1_10m_Min | Pitch Control Panel 1 Temp (min) | Pitchsteuerung Panel 1 Temperatur (min) | Temperatura de paso del panel 1 de control (min) | Pitch Panel sterow. 1 Temp (min) | Electrical pitch control Panel/Box temperature blade 1 | deg_c | °C | Minimum | Double | 10 minute tag
WROT.BlPthPnlTmp1_10m_Std | #N/A | WROT. | BlPthPnlTmp1_10m_Std | Pitch Control Panel 1 Temp (std) | Pitchsteuerung Panel 1 Temperatur (std) | Temperatura de paso del panel 1 de control (std) | Pitch Panel sterow. 1 Temp (std) | Electrical pitch control Panel/Box temperature blade 1 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.BlPthPnlTmp2 | #N/A | WROT. | BlPthPnlTmp2 | Pitch Control Panel 2 Temp | Pitchsteuerung Panel 2 Temperatur | Temperatura de paso del panel 2 de control | Pitch Panel sterow. 2 Temp | Electrical pitch control Panel/Box temperature blade 2 | deg_c | °C | Live Value | Double | Live Value
WROT.BlPthPnlTmp2_10m_Avg | #N/A | WROT. | BlPthPnlTmp2_10m_Avg | Pitch Control Panel 2 Temp (avg) | Pitchsteuerung Panel 2 Temperatur (avg) | Temperatura de paso del panel 2 de control (avg) | Pitch Panel sterow. 2 Temp (avg) | Electrical pitch control Panel/Box temperature blade 2 | deg_c | °C | Average | Double | 10 minute tag
WROT.BlPthPnlTmp2_10m_Max | #N/A | WROT. | BlPthPnlTmp2_10m_Max | Pitch Control Panel 2 Temp (max) | Pitchsteuerung Panel 2 Temperatur (max) | Temperatura de paso del panel 2 de control (max) | Pitch Panel sterow. 2 Temp (max) | Electrical pitch control Panel/Box temperature blade 2 | deg_c | °C | Maximum | Double | 10 minute tag
WROT.BlPthPnlTmp2_10m_Min | #N/A | WROT. | BlPthPnlTmp2_10m_Min | Pitch Control Panel 2 Temp (min) | Pitchsteuerung Panel 2 Temperatur (min) | Temperatura de paso del panel 2 de control (min) | Pitch Panel sterow. 2 Temp (min) | Electrical pitch control Panel/Box temperature blade 2 | deg_c | °C | Minimum | Double | 10 minute tag
WROT.BlPthPnlTmp2_10m_Std | #N/A | WROT. | BlPthPnlTmp2_10m_Std | Pitch Control Panel 2 Temp (std) | Pitchsteuerung Panel 2 Temperatur (std) | Temperatura de paso del panel 2 de control (std) | Pitch Panel sterow. 2 Temp (std) | Electrical pitch control Panel/Box temperature blade 2 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.BlPthPnlTmp3 | #N/A | WROT. | BlPthPnlTmp3 | Pitch Control Panel 3 Temp | Pitchsteuerung Panel 3 Temperatur | Temperatura de paso del panel 3 de control | Pitch Panel sterow. 3 Temp | Electrical pitch control Panel/Box temperature blade 3 | deg_c | °C | Live Value | Double | Live Value
WROT.BlPthPnlTmp3_10m_Avg | #N/A | WROT. | BlPthPnlTmp3_10m_Avg | Pitch Control Panel 3 Temp (avg) | Pitchsteuerung Panel 3 Temperatur (avg) | Temperatura de paso del panel 3 de control (avg) | Pitch Panel sterow. 3 Temp (avg) | Electrical pitch control Panel/Box temperature blade 3 | deg_c | °C | Average | Double | 10 minute tag
WROT.BlPthPnlTmp3_10m_Max | #N/A | WROT. | BlPthPnlTmp3_10m_Max | Pitch Control Panel 3 Temp (max) | Pitchsteuerung Panel 3 Temperatur (max) | Temperatura de paso del panel 3 de control (max) | Pitch Panel sterow. 3 Temp (max) | Electrical pitch control Panel/Box temperature blade 3 | deg_c | °C | Maximum | Double | 10 minute tag
WROT.BlPthPnlTmp3_10m_Min | #N/A | WROT. | BlPthPnlTmp3_10m_Min | Pitch Control Panel 3 Temp (min) | Pitchsteuerung Panel 3 Temperatur (min) | Temperatura de paso del panel 3 de control (min) | Pitch Panel sterow. 3 Temp (min) | Electrical pitch control Panel/Box temperature blade 3 | deg_c | °C | Minimum | Double | 10 minute tag
WROT.BlPthPnlTmp3_10m_Std | #N/A | WROT. | BlPthPnlTmp3_10m_Std | Pitch Control Panel 3 Temp (std) | Pitchsteuerung Panel 3 Temperatur (std) | Temperatura de paso del panel 3 de control (std) | Pitch Panel sterow. 3 Temp (std) | Electrical pitch control Panel/Box temperature blade 3 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.BlPthSpd1 | #N/A | WROT. | BlPthSpd1 | Pitch Speed blade 1 | Steigungsgeschwindigkeit Blatt 1 | Velocidad de paso de la pala 1 | Pitch prędk. łopata 1 | Pitch Speed blade 1 | rpm | RPM | Live Value | Double | Live Value
WROT.BlPthSpd1_10m_Avg | #N/A | WROT. | BlPthSpd1_10m_Avg | Pitch Speed blade 1 (avg) | Steigungsgeschwindigkeit Blatt 1 (avg) | Velocidad de paso de la pala 1 (avg) | Pitch prędk. łopata 1 (avg) | Pitch Speed blade 1 | rpm | RPM | Average | Double | 10 minute tag
WROT.BlPthSpd1_10m_Max | #N/A | WROT. | BlPthSpd1_10m_Max | Pitch Speed blade 1 (max) | Steigungsgeschwindigkeit Blatt 1 (max) | Velocidad de paso de la pala 1 (max) | Pitch prędk. łopata 1 (max) | Pitch Speed blade 1 | rpm | RPM | Maximum | Double | 10 minute tag
WROT.BlPthSpd1_10m_Min | #N/A | WROT. | BlPthSpd1_10m_Min | Pitch Speed blade 1 (min) | Steigungsgeschwindigkeit Blatt 1 (min) | Velocidad de paso de la pala 1 (min) | Pitch prędk. łopata 1 (min) | Pitch Speed blade 1 | rpm | RPM | Minimum | Double | 10 minute tag
WROT.BlPthSpd1_10m_Std | #N/A | WROT. | BlPthSpd1_10m_Std | Pitch Speed blade 1 (std) | Steigungsgeschwindigkeit Blatt 1 (std) | Velocidad de paso de la pala 1 (std) | Pitch prędk. łopata 1 (std) | Pitch Speed blade 1 | rpm | RPM | Standard Deviation | Double | 10 minute tag
WROT.BlPthSpd2 | #N/A | WROT. | BlPthSpd2 | Pitch Speed blade 2 | Steigungsgeschwindigkeit Blatt 2 | Velocidad de paso de la pala 2 | Pitch prędk. łopata 2 | Pitch Speed blade 2 | rpm | RPM | Live Value | Double | Live Value
WROT.BlPthSpd2_10m_Avg | #N/A | WROT. | BlPthSpd2_10m_Avg | Pitch Speed blade 2 (avg) | Steigungsgeschwindigkeit Blatt 2 (avg) | Velocidad de paso de la pala 2 (avg) | Pitch prędk. łopata 2 (avg) | Pitch Speed blade 2 | rpm | RPM | Average | Double | 10 minute tag
WROT.BlPthSpd2_10m_Max | #N/A | WROT. | BlPthSpd2_10m_Max | Pitch Speed blade 2 (max) | Steigungsgeschwindigkeit Blatt 2 (max) | Velocidad de paso de la pala 2 (max) | Pitch prędk. łopata 2 (max) | Pitch Speed blade 2 | rpm | RPM | Maximum | Double | 10 minute tag
WROT.BlPthSpd2_10m_Min | #N/A | WROT. | BlPthSpd2_10m_Min | Pitch Speed blade 2 (min) | Steigungsgeschwindigkeit Blatt 2 (min) | Velocidad de paso de la pala 2 (min) | Pitch prędk. łopata 2 (min) | Pitch Speed blade 2 | rpm | RPM | Minimum | Double | 10 minute tag
WROT.BlPthSpd2_10m_Std | #N/A | WROT. | BlPthSpd2_10m_Std | Pitch Speed blade 2 (std) | Steigungsgeschwindigkeit Blatt 2 (std) | Velocidad de paso de la pala 2 (std) | Pitch prędk. łopata 2 (std) | Pitch Speed blade 2 | rpm | RPM | Standard Deviation | Double | 10 minute tag
WROT.BlPthSpd3 | #N/A | WROT. | BlPthSpd3 | Pitch Speed blade 3 | Steigungsgeschwindigkeit Blatt 3 | Velocidad de paso de la pala 3 | Pitch prędk. łopata 3 | Pitch Speed blade 3 | rpm | RPM | Live Value | Double | Live Value
WROT.BlPthSpd3_10m_Avg | #N/A | WROT. | BlPthSpd3_10m_Avg | Pitch Speed blade 3 (avg) | Steigungsgeschwindigkeit Blatt 3 (avg) | Velocidad de paso de la pala 3 (avg) | Pitch prędk. łopata 3 (avg) | Pitch Speed blade 3 | rpm | RPM | Average | Double | 10 minute tag
WROT.BlPthSpd3_10m_Max | #N/A | WROT. | BlPthSpd3_10m_Max | Pitch Speed blade 3 (max) | Steigungsgeschwindigkeit Blatt 3 (max) | Velocidad de paso de la pala 3 (max) | Pitch prędk. łopata 3 (max) | Pitch Speed blade 3 | rpm | RPM | Maximum | Double | 10 minute tag
WROT.BlPthSpd3_10m_Min | #N/A | WROT. | BlPthSpd3_10m_Min | Pitch Speed blade 3 (min) | Steigungsgeschwindigkeit Blatt 3 (min) | Velocidad de paso de la pala 3 (min) | Pitch prędk. łopata 3 (min) | Pitch Speed blade 3 | rpm | RPM | Minimum | Double | 10 minute tag
WROT.BlPthSpd3_10m_Std | #N/A | WROT. | BlPthSpd3_10m_Std | Pitch Speed blade 3 (std) | Steigungsgeschwindigkeit Blatt 3 (std) | Velocidad de paso de la pala 3 (std) | Pitch prędk. łopata 3 (std) | Pitch Speed blade 3 | rpm | RPM | Standard Deviation | Double | 10 minute tag
WROT.BlPthTmp1 | #N/A | WROT. | BlPthTmp1 | Pitch Output Stage 1 Temp | Pitch Ausgang Stufe 1 Temperatur | Temperatura de paso de salida del fase 1 | Pitch Wyjście 1 Temp | Pitch 1 output stage temperature | deg_c | °C | Live Value | Double | Live Value
WROT.BlPthTmp1_10m_Avg | #N/A | WROT. | BlPthTmp1_10m_Avg | Pitch Output Stage 1 Temp (avg) | Pitch Ausgang Stufe 1 Temperatur (avg) | Temperatura de paso de salida del fase 1 (avg) | Pitch Wyjście 1 Temp (avg) | Pitch 1 output stage temperature | deg_c | °C | Average | Double | 10 minute tag
WROT.BlPthTmp1_10m_Max | #N/A | WROT. | BlPthTmp1_10m_Max | Pitch Output Stage 1 Temp (max) | Pitch Ausgang Stufe 1 Temperatur (max) | Temperatura de paso de salida del fase 1 (max) | Pitch Wyjście 1 Temp (max) | Pitch 1 output stage temperature | deg_c | °C | Maximum | Double | 10 minute tag
WROT.BlPthTmp1_10m_Min | #N/A | WROT. | BlPthTmp1_10m_Min | Pitch Output Stage 1 Temp (min) | Pitch Ausgang Stufe 1 Temperatur (min) | Temperatura de paso de salida del fase 1 (min) | Pitch Wyjście 1 Temp (min) | Pitch 1 output stage temperature | deg_c | °C | Minimum | Double | 10 minute tag
WROT.BlPthTmp1_10m_Std | #N/A | WROT. | BlPthTmp1_10m_Std | Pitch Output Stage 1 Temp (std) | Pitch Ausgang Stufe 1 Temperatur (std) | Temperatura de paso de salida del fase 1 (std) | Pitch Wyjście 1 Temp (std) | Pitch 1 output stage temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.BlPthTmp2 | #N/A | WROT. | BlPthTmp2 | Pitch Output Stage 2 Temp | Pitch Ausgang Stufe 2 Temperatur | Temperatura de paso de salida del fase 2 | Pitch Wyjście 2 Temp | Pitch 2 output stage temperature | deg_c | °C | Live Value | Double | Live Value
WROT.BlPthTmp2_10m_Avg | #N/A | WROT. | BlPthTmp2_10m_Avg | Pitch Output Stage 2 Temp (avg) | Pitch Ausgang Stufe 2 Temperatur (avg) | Temperatura de paso de salida del fase 2 (avg) | Pitch Wyjście 2 Temp (avg) | Pitch 2 output stage temperature | deg_c | °C | Average | Double | 10 minute tag
WROT.BlPthTmp2_10m_Max | #N/A | WROT. | BlPthTmp2_10m_Max | Pitch Output Stage 2 Temp (max) | Pitch Ausgang Stufe 2 Temperatur (max) | Temperatura de paso de salida del fase 2 (max) | Pitch Wyjście 2 Temp (max) | Pitch 2 output stage temperature | deg_c | °C | Maximum | Double | 10 minute tag
WROT.BlPthTmp2_10m_Min | #N/A | WROT. | BlPthTmp2_10m_Min | Pitch Output Stage 2 Temp (min) | Pitch Ausgang Stufe 2 Temperatur (min) | Temperatura de paso de salida del fase 2 (min) | Pitch Wyjście 2 Temp (min) | Pitch 2 output stage temperature | deg_c | °C | Minimum | Double | 10 minute tag
WROT.BlPthTmp2_10m_Std | #N/A | WROT. | BlPthTmp2_10m_Std | Pitch Output Stage 2 Temp (std) | Pitch Ausgang Stufe 2 Temperatur (std) | Temperatura de paso de salida del fase 2 (std) | Pitch Wyjście 2 Temp (std) | Pitch 2 output stage temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.BlPthTmp3 | #N/A | WROT. | BlPthTmp3 | Pitch Output Stage 3 Temp | Pitch Ausgang Stufe 3 Temperatur | Temperatura de paso de salida del fase 3 | Pitch Wyjście 3 Temp | Pitch 3 output stage temperature | deg_c | °C | Live Value | Double | Live Value
WROT.BlPthTmp3_10m_Avg | #N/A | WROT. | BlPthTmp3_10m_Avg | Pitch Output Stage 3 Temp (avg) | Pitch Ausgang Stufe 3 Temperatur (avg) | Temperatura de paso de salida del fase 3 (avg) | Pitch Wyjście 3 Temp (avg) | Pitch 3 output stage temperature | deg_c | °C | Average | Double | 10 minute tag
WROT.BlPthTmp3_10m_Max | #N/A | WROT. | BlPthTmp3_10m_Max | Pitch Output Stage 3 Temp (max) | Pitch Ausgang Stufe 3 Temperatur (max) | Temperatura de paso de salida del fase 3 (max) | Pitch Wyjście 3 Temp (max) | Pitch 3 output stage temperature | deg_c | °C | Maximum | Double | 10 minute tag
WROT.BlPthTmp3_10m_Min | #N/A | WROT. | BlPthTmp3_10m_Min | Pitch Output Stage 3 Temp (min) | Pitch Ausgang Stufe 3 Temperatur (min) | Temperatura de paso de salida del fase 3 (min) | Pitch Wyjście 3 Temp (min) | Pitch 3 output stage temperature | deg_c | °C | Minimum | Double | 10 minute tag
WROT.BlPthTmp3_10m_Std | #N/A | WROT. | BlPthTmp3_10m_Std | Pitch Output Stage 3 Temp (std) | Pitch Ausgang Stufe 3 Temperatur (std) | Temperatura de paso de salida del fase 3 (std) | Pitch Wyjście 3 Temp (std) | Pitch 3 output stage temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.BlSt | WROT.BlSt | WROT. | BlSt | Pitch System Status | Pitch System Status | Estado del sistema de paso | Stan systemu pitch | Status of blade as feedback from the pitch system | Enum | Enum | Live Value | Long | Live Value
WROT.BlTorqFil1PAct1_10m_Max | #N/A | WROT. | BlTorqFil1PAct1_10m_Max | 1P filtered moment in blade 1 while TYC active (max) | 1P gefiltertes Moment in Blatt 1 bei aktivem TYC (max) | Momento filtrado 1P en la pala 1 mientras TYC está activo (max) | 1P filtrowany moment w łopacie 1, gdy TYC aktywny (max) | 1P filtered moment in blade 1 while TYC active |  | Nm | Maximum | Double | 10 minute tag
WROT.BlTorqFil1PAct2_10m_Max | #N/A | WROT. | BlTorqFil1PAct2_10m_Max | 1P filtered moment in blade 2 while TYC active (max) | 1P gefiltertes Moment in Blatt 2 bei aktivem TYC (max) | Momento filtrado 1P en la pala 2 mientras TYC está activo (max) | 1P filtrowany moment w łopacie 2, gdy TYC aktywny (max) | 1P filtered moment in blade 2 while TYC active |  | Nm | Maximum | Double | 10 minute tag
WROT.BlTorqFil1PAct3_10m_Max | #N/A | WROT. | BlTorqFil1PAct3_10m_Max | 1P filtered moment in blade 3 while TYC active (max) | 1P gefiltertes Moment in Blatt 3 bei aktivem TYC (max) | Momento filtrado 1P en la pala 3 mientras TYC está activo (max) | 1P filtrowany moment w łopacie 3, gdy TYC aktywny (max) | 1P filtered moment in blade 3 while TYC active |  | Nm | Maximum | Double | 10 minute tag
WROT.BlTorqFil1PInAct1_10m_Max | #N/A | WROT. | BlTorqFil1PInAct1_10m_Max | 1P filtered moment in blade 1 while TYC inactive (max) | 1P gefiltertes Moment in Blatt 1 bei inaktivem TYC (max) | Momento filtrado 1P en la pala 1 mientras TYC está inactivo (max) | 1P filtrowany moment w łopacie 1, gdy TYC nieaktywny (max) | 1P filtered moment in blade 1 while TYC inactive |  | Nm | Maximum | Double | 10 minute tag
WROT.BlTorqFil1PInAct2_10m_Max | #N/A | WROT. | BlTorqFil1PInAct2_10m_Max | 1P filtered moment in blade 2 while TYC inactive (max) | 1P gefiltertes Moment in Blatt 2 bei inaktivem TYC (max) | Momento filtrado 1P en la pala 2 mientras TYC está inactivo (max) | 1P filtrowany moment w łopacie 2, gdy TYC nieaktywny (max) | 1P filtered moment in blade 2 while TYC inactive |  | Nm | Maximum | Double | 10 minute tag
WROT.BlTorqFil1PInAct3_10m_Max | #N/A | WROT. | BlTorqFil1PInAct3_10m_Max | 1P filtered moment in blade 3 while TYC inactive (max) | 1P gefiltertes Moment in Blatt 3 bei inaktivem TYC (max) | Momento filtrado 1P en la pala 3 mientras TYC está inactivo (max) | 1P filtrowany moment w łopacie 3, gdy TYC nieaktywny (max) | 1P filtered moment in blade 3 while TYC inactive |  | Nm | Maximum | Double | 10 minute tag
WROT.BlTorqFil2PAct1_10m_Max | #N/A | WROT. | BlTorqFil2PAct1_10m_Max | 2P filtered moment in blade 1 while TYC active (max) | 2P gefiltertes Moment in Blatt 1 bei aktivem TYC (max) | Momento filtrado 2P en la pala 1 mientras TYC está activo (max) | Moment filtrowany 2P w łopacie 1, gdy TYC aktywny (max) | 2P filtered moment in blade 1 while TYC active |  | Nm | Maximum | Double | 10 minute tag
WROT.BlTorqFil2PAct2_10m_Max | #N/A | WROT. | BlTorqFil2PAct2_10m_Max | 2P filtered moment in blade 2 while TYC active (max) | 2P gefiltertes Moment in Blatt 2 bei aktivem TYC (max) | Momento filtrado 2P en la pala 2 mientras TYC está activo (max) | Przefiltrowany moment 2P w łopacie 2, gdy TYC aktywny (max) | 2P filtered moment in blade 2 while TYC active |  | Nm | Maximum | Double | 10 minute tag
WROT.BlTorqFil2PAct3_10m_Max | #N/A | WROT. | BlTorqFil2PAct3_10m_Max | 2P filtered moment in blade 3 while TYC active (max) | 2P gefiltertes Moment in Blatt 3 bei aktivem TYC (max) | Momento filtrado 2P en la pala 3 mientras TYC está activo (max) | Przefiltrowany moment 2P w łopacie 3, gdy TYC aktywny (max) | 2P filtered moment in blade 3 while TYC active |  | Nm | Maximum | Double | 10 minute tag
WROT.BlTorqFil2PInAct1_10m_Max | #N/A | WROT. | BlTorqFil2PInAct1_10m_Max | 2P filtered moment in blade 1 while TYC inactive (max) | 2P gefiltertes Moment in Blatt 1 bei inaktivem TYC (max) | Momento filtrado 2P en la pala 1 mientras TYC está inactivo (max) | 2P filtrowany moment w łopacie 1, gdy TYC nieaktywny (max) | 2P filtered moment in blade 1 while TYC inactive |  | Nm | Maximum | Double | 10 minute tag
WROT.BlTorqFil2PInAct2_10m_Max | #N/A | WROT. | BlTorqFil2PInAct2_10m_Max | 2P filtered moment in blade 2 while TYC inactive (max) | 2P gefiltertes Moment in Blatt 2 bei inaktivem TYC (max) | Momento filtrado 2P en la pala 2 mientras TYC está inactivo (max) | 2P filtrowany moment w łopacie 2, gdy TYC nieaktywny (max) | 2P filtered moment in blade 2 while TYC inactive |  | Nm | Maximum | Double | 10 minute tag
WROT.BlTorqFil2PInAct3_10m_Max | #N/A | WROT. | BlTorqFil2PInAct3_10m_Max | 2P filtered moment in blade 3 while TYC inactive (max) | 2P gefiltertes Moment in Blatt 3 bei inaktivem TYC (max) | Momento filtrado 2P en la pala 3 mientras TYC está inactivo (max) | 2P filtrowany moment w łopacie 3, gdy TYC nieaktywny (max) | 2P filtered moment in blade 3 while TYC inactive |  | Nm | Maximum | Double | 10 minute tag
WROT.EmgVlvSt | #N/A | WROT. | EmgVlvSt | Emergency Stop valve | Not-Aus-Ventil | Válvula de parada de emergencia | Awaryjny zawór odcinający | Emergency. Stop valve distributing valve | Enum | Enum | Live Value | Long | Live Value
WROT.GsLev | #N/A | WROT. | GsLev | Grease level in the blade bearing lubrication tank | Fettstand im Schmierstofftank des Blattlagers | Nivel de grasa del depósito de lubricación del cojinete de la pala | Poziom smaru w zbiorniku smarowym łożyska łopat | Grease level in the blade bearing lubrication tank | percent | percent | Live Value | Double | Live Value
WROT.GsLev_10m_Avg | #N/A | WROT. | GsLev_10m_Avg | Grease level in the blade bearing lubrication tank (avg) | Fettstand im Schmierstofftank des Blattlagers (avg) | Nivel de grasa del depósito de lubricación del cojinete de la pala (avg) | Poziom smaru w zbiorniku smarowym łożyska łopat (avg) | Grease level in the blade bearing lubrication tank | percent | percent | Average | Double | 10 minute tag
WROT.GsLev_10m_Max | #N/A | WROT. | GsLev_10m_Max | Grease level in the blade bearing lubrication tank (max) | Fettstand im Schmierstofftank des Blattlagers (max) | Nivel de grasa del depósito de lubricación del cojinete de la pala (max) | Poziom smaru w zbiorniku smarowym łożyska łopat (max) | Grease level in the blade bearing lubrication tank | percent | percent | Maximum | Double | 10 minute tag
WROT.GsLev_10m_Min | #N/A | WROT. | GsLev_10m_Min | Grease level in the blade bearing lubrication tank (min) | Fettstand im Schmierstofftank des Blattlagers (min) | Nivel de grasa del depósito de lubricación del cojinete de la pala (min) | Poziom smaru w zbiorniku smarowym łożyska łopat (min) | Grease level in the blade bearing lubrication tank | percent | percent | Minimum | Double | 10 minute tag
WROT.GsLev_10m_Std | #N/A | WROT. | GsLev_10m_Std | Grease level in the blade bearing lubrication tank (std) | Fettstand im Schmierstofftank des Blattlagers (std) | Nivel de grasa del depósito de lubricación del cojinete de la pala (std) | Poziom smaru w zbiorniku smarowym łożyska łopat (std) | Grease level in the blade bearing lubrication tank | percent | percent | Standard Deviation | Double | 10 minute tag
WROT.HubCtlTmp | #N/A | WROT. | HubCtlTmp | Rotor Hub Controller Temp | Reglertemperatur der Rotornabe | Temperatura del controlador del buje del rotor | Temp kontrolera Hub rotora | Temperature in the rotor hub controller | deg_c | °C | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WROT.HubCtlTmp_10m_Avg | #N/A | WROT. | HubCtlTmp_10m_Avg | Rotor Hub Controller Temp (avg) | Reglertemperatur der Rotornabe (avg) | Temperatura del controlador del buje del rotor (avg) | Temp kontrolera Hub rotora (avg) | Temperature in the rotor hub controller | deg_c | °C | Average | Double | 10 minute tag
WROT.HubHyInPres | #N/A | WROT. | HubHyInPres | Hydraulic Hub Inlet Pressure | Hydrauliknaben-Eingangsdruck | Presión de entrada del buje hidráulico | Ciśnienie wlotowe hydr. Hub | Hydraulic pressure at hub inlet | bar | bar | Live Value | Double | Live Value
WROT.HubHyInPres_10m_Avg | #N/A | WROT. | HubHyInPres_10m_Avg | Hydraulic Hub Inlet Pressure (avg) | Hydrauliknaben-Eingangsdruck (avg) | Presión de entrada del buje hidráulico (avg) | Ciśnienie wlotowe hydr. Hub (avg) | Hydraulic pressure at hub inlet | bar | bar | Average | Double | 10 minute tag
WROT.HubHyInPres_10m_Max | #N/A | WROT. | HubHyInPres_10m_Max | Hydraulic Hub Inlet Pressure (max) | Hydrauliknaben-Eingangsdruck (max) | Presión de entrada del buje hidráulico (max) | Ciśnienie wlotowe hydr. Hub (max) | Hydraulic pressure at hub inlet | bar | bar | Maximum | Double | 10 minute tag
WROT.HubHyInPres_10m_Min | #N/A | WROT. | HubHyInPres_10m_Min | Hydraulic Hub Inlet Pressure (min) | Hydrauliknaben-Eingangsdruck (min) | Presión de entrada del buje hidráulico (min) | Ciśnienie wlotowe hydr. Hub (min) | Hydraulic pressure at hub inlet | bar | bar | Minimum | Double | 10 minute tag
WROT.HubHyInPres_10m_Std | #N/A | WROT. | HubHyInPres_10m_Std | Hydraulic Hub Inlet Pressure (std) | Hydrauliknaben-Eingangsdruck (std) | Presión de entrada del buje hidráulico (std) | Ciśnienie wlotowe hydr. Hub (std) | Hydraulic pressure at hub inlet | bar | bar | Standard Deviation | Double | 10 minute tag
WROT.HubPnlTmp | #N/A | WROT. | HubPnlTmp | Hub Panel Temp | Nabenpanel Temperatur | Temperatura del panel del buje | Temp panelu Hub | Hub panel temperature | deg_c | °C | Live Value | Double | Live Value
WROT.HubPnlTmp_10m_Avg | #N/A | WROT. | HubPnlTmp_10m_Avg | Hub Panel Temp (avg) | Nabenpanel Temperatur (avg) | Temperatura del panel del buje (avg) | Temp panelu Hub (avg) | Hub panel temperature | deg_c | °C | Average | Double | 10 minute tag
WROT.HubPnlTmp_10m_Max | #N/A | WROT. | HubPnlTmp_10m_Max | Hub Panel Temp (max) | Nabenpanel Temperatur (max) | Temperatura del panel del buje (max) | Temp panelu Hub (max) | Hub panel temperature | deg_c | °C | Maximum | Double | 10 minute tag
WROT.HubPnlTmp_10m_Min | #N/A | WROT. | HubPnlTmp_10m_Min | Hub Panel Temp (min) | Nabenpanel Temperatur (min) | Temperatura del panel del buje (min) | Temp panelu Hub (min) | Hub panel temperature | deg_c | °C | Minimum | Double | 10 minute tag
WROT.HubPnlTmp_10m_Std | #N/A | WROT. | HubPnlTmp_10m_Std | Hub Panel Temp (std) | Nabenpanel Temperatur (std) | Temperatura del panel del buje (std) | Temp panelu Hub (std) | Hub panel temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.HubTmp | WROT.HubTmp | WROT. | HubTmp | Hub Temp | Nabentemperatur | Temperatura del buje | Temp Hub | Temperature in hub | deg_c | °C | Live Value | Double | Live Value | Used in some specialised presentations
WROT.HubTmp_10m_Avg | #N/A | WROT. | HubTmp_10m_Avg | Hub Temp (avg) | Nabentemperatur (avg) | Temperatura del buje (avg) | Temp Hub (avg) | Temperature in hub | deg_c | °C | Average | Double | 10 minute tag | Rare tags for analysis
WROT.HubTmp_10m_Max | #N/A | WROT. | HubTmp_10m_Max | Hub Temp (max) | Nabentemperatur (max) | Temperatura del buje (max) | Temp Hub (max) | Temperature in hub | deg_c | °C | Maximum | Double | 10 minute tag | Rare tags for analysis
WROT.HubTmp_10m_Min | #N/A | WROT. | HubTmp_10m_Min | Hub Temp (min) | Nabentemperatur (min) | Temperatura del buje (min) | Temp Hub (min) | Temperature in hub | deg_c | °C | Minimum | Double | 10 minute tag | Rare tags for analysis
WROT.HubTmp_10m_Std | #N/A | WROT. | HubTmp_10m_Std | Hub Temp (std) | Nabentemperatur (std) | Temperatura del buje (std) | Temp Hub (std) | Temperature in hub | deg_c | °C | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WROT.HyOilPmpCnt | #N/A | WROT. | HyOilPmpCnt | Number of activations of the hydraulic oil pump | Anzahl der Aktivierungen der Hydraulikölpumpe | Número de activaciones de la bomba de aceite hidráulico | Liczba aktywacji hydraulicznej pompy oleju | Number of activations of the hydraulic oil pump | count | Count | Total Counter | Long | Live Value
WROT.HyOilPmpCnt_10m_End | #N/A | WROT. | HyOilPmpCnt_10m_End | Number of activations of the hydraulic oil pump (end) | Anzahl der Aktivierungen der Hydraulikölpumpe (end) | Número de activaciones de la bomba de aceite hidráulico (end) | Liczba aktywacji hydraulicznej pompy oleju (end) | Number of activations of the hydraulic oil pump | count | Count | Endvalue | Long | 10 minute tag
WROT.HyOilTmp | #N/A | WROT. | HyOilTmp | Hydraulic Oil Temp | Hydrauliköltemperatur | Temperatura de aceite hidráulico | Temp oleju hydr. | Hydraulic oil temperature | deg_c | °C | Live Value | Double | Live Value | Used in some specialised presentations
WROT.HyOilTmp_10m_Avg | #N/A | WROT. | HyOilTmp_10m_Avg | Hydraulic Oil Temp (avg) | Hydrauliköltemperatur (avg) | Temperatura de aceite hidráulico (avg) | Temp oleju hydr. (avg) | Hydraulic oil temperature | deg_c | °C | Average | Double | 10 minute tag
WROT.HyOilTmp_10m_Max | #N/A | WROT. | HyOilTmp_10m_Max | Hydraulic Oil Temp (max) | Hydrauliköltemperatur (max) | Temperatura de aceite hidráulico (max) | Temp oleju hydr. (max) | Hydraulic oil temperature | deg_c | °C | Maximum | Double | 10 minute tag | Rare tags for analysis
WROT.HyOilTmp_10m_Min | #N/A | WROT. | HyOilTmp_10m_Min | Hydraulic Oil Temp (min) | Hydrauliköltemperatur (min) | Temperatura de aceite hidráulico (min) | Temp oleju hydr. (min) | Hydraulic oil temperature | deg_c | °C | Minimum | Double | 10 minute tag | Rare tags for analysis
WROT.HyOilTmp_10m_Std | #N/A | WROT. | HyOilTmp_10m_Std | Hydraulic Oil Temp (std) | Hydrauliköltemperatur (std) | Temperatura de aceite hidráulico (std) | Temp oleju hydr. (std) | Hydraulic oil temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WROT.HyTipBrkPres | #N/A | WROT. | HyTipBrkPres | Hydraulic Oil Tip Brake Pressure | Hydraulikölspitze Bremsdruck | Presión del freno de la boquilla de aceite hidráulico | Ciśnienie hamulca końcówki oleju hydr. | Hydraulic oil pressure tip brake | bar | bar | Live Value | Double | Live Value
WROT.HyTipBrkPres_10m_Avg | #N/A | WROT. | HyTipBrkPres_10m_Avg | Hydraulic Oil Tip Brake Pressure (avg) | Hydraulikölspitze Bremsdruck (avg) | Presión del freno de la boquilla de aceite hidráulico (avg) | Ciśnienie hamulca końcówki oleju hydr. (avg) | Hydraulic oil pressure tip brake | bar | bar | Average | Double | 10 minute tag
WROT.HyTipBrkPres_10m_Max | #N/A | WROT. | HyTipBrkPres_10m_Max | Hydraulic Oil Tip Brake Pressure (max) | Hydraulikölspitze Bremsdruck (max) | Presión del freno de la boquilla de aceite hidráulico (max) | Ciśnienie hamulca końcówki oleju hydr. (max) | Hydraulic oil pressure tip brake | bar | bar | Maximum | Double | 10 minute tag
WROT.HyTipBrkPres_10m_Min | #N/A | WROT. | HyTipBrkPres_10m_Min | Hydraulic Oil Tip Brake Pressure (min) | Hydraulikölspitze Bremsdruck (min) | Presión del freno de la boquilla de aceite hidráulico (min) | Ciśnienie hamulca końcówki oleju hydr. (min) | Hydraulic oil pressure tip brake | bar | bar | Minimum | Double | 10 minute tag
WROT.HyTipBrkPres_10m_Std | #N/A | WROT. | HyTipBrkPres_10m_Std | Hydraulic Oil Tip Brake Pressure (std) | Hydraulikölspitze Bremsdruck (std) | Presión del freno de la boquilla de aceite hidráulico (std) | Ciśnienie hamulca końcówki oleju hydr. (std) | Hydraulic oil pressure tip brake | bar | bar | Standard Deviation | Double | 10 minute tag
WROT.PthCtlSt | WROT.PthCtlSt | WROT. | PthCtlSt | Pitch Control Status | Status der Pitchsteuerung | Estado de control de paso | Pitch status sterow. | Status of pitch control | Enum | Enum | Live Value | Long | Live Value
WROT.PthCylPres1 | #N/A | WROT. | PthCylPres1 | Pitch Block Cylinder A Pressure | Pitch Block Zylinder A Druck | Presión del cilindro A del bloque de paso | Pitch blok cylindrów A ciśnienie | Pitch block cylinder A pressure | bar | bar | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WROT.PthCylPres2 | #N/A | WROT. | PthCylPres2 | Pitch Block Cylinder B Pressure | Pitch Block Zylinder B Druck | Presión del cilindro B del bloque de paso | Pitch blok cylindrów B ciśnienie | Pitch block cylinder B pressure | bar | bar | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WROT.PthCylPres3 | #N/A | WROT. | PthCylPres3 | Pitch Block Cylinder C Pressure | Pitch Block Zylinder C Druck | Presión del cilindro C del bloque de paso | Pitch blok cylindrów C ciśnienie | Pitch block cylinder C pressure | bar | bar | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WROT.PthEmgChk | WROT.PthEmgChk | WROT. | PthEmgChk | Check emergency pitch system | Notpitch-System prüfen | Comprobar el sistema de paso de emergencia | Sprawdź system awaryjny Pitch | Check emergency pitch system | Enum | Enum | Live Value | Long
WROT.PthFdPmpCnt_10m_End | #N/A | WROT. | PthFdPmpCnt_10m_End | Number of activations of the pitch feeder pump (end) | Anzahl der Betätigungen der Pitch Zubringerpumpe (end) | Número de activaciones de la bomba del alimentador de paso (end) | Liczba aktywacji pompy podajnika Pitch (end) | Number of activations of the pitch feeder pump | count | Count | Endvalue | Long | 10 minute tag
WROT.PthFdPmpTms_10m_End | #N/A | WROT. | PthFdPmpTms_10m_End | Time pitch feeder pump has been engaged (end) | Zeit, in der die Pitch-Zubringerpumpe eingeschaltet war (end) | Tiempo que la bomba del alimentador de paso ha estado conectada (end) | Czas aktywacji pompy podajnika Pitch (end) | Time pitch feeder pump has been engaged | s | seconds | Endvalue | Long | 10 minute tag
WROT.PthMainPmpCnt_10m_End | #N/A | WROT. | PthMainPmpCnt_10m_End | Number of activations the pitch main pump (end) | Anzahl der Aktivierungen der Pitch-Hauptpumpe (end) | Número de activaciones de la bomba principal de paso (end) | Liczba aktywacji pompy głównej Pitch (end) | Number of activations the pitch main pump | count | Count | Endvalue | Long | 10 minute tag
WROT.PthMainPmpTms_10m_End | #N/A | WROT. | PthMainPmpTms_10m_End | Time pitch main pump has been engaged (end) | Zeit, in der die Pitch-Hauptpumpe eingeschaltet war (end) | Tiempo que la bomba principal de paso ha estado conectada (end) | Czas aktywacji pompy głównej Pitch (end) | Time pitch main pump has been engaged | s | seconds | Endvalue | Long | 10 minute tag
WROT.PthMnfPres1 | #N/A | WROT. | PthMnfPres1 | Pitch block manifold A pressure | Druck im Pitchblock-Verteiler A | Presión bloque de paso múltiple A | Pitch blok. Kolektor A ciśnienie | Pitch block manifold A pressure | bar | bar | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WROT.PthMnfPres2 | #N/A | WROT. | PthMnfPres2 | Pitch block manifold B pressure | Druck im Pitchblock-Verteiler B | Presión bloque de paso múltiple B | Pitch blok. Kolektor B ciśnienie | Pitch block manifold B pressure | bar | bar | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WROT.PthMnfPres3 | #N/A | WROT. | PthMnfPres3 | Pitch block manifold C pressure | Druck im Pitchblock-Verteiler C | Presión bloque de paso múltiple C | Pitch blok. Kolektor C ciśnienie | Pitch block manifold C pressure | bar | bar | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WROT.RotBlk | WROT.RotBlk | WROT. | RotBlk | Block rotor position command | Rotorpositionsbefehl blockieren | Comando de bloque de la posición del rotor | Polecenie położ blok. rotora | Block rotor position command | Enum | Enum | Live Value | Long
WROT.RotPos | WROT.RotPos | WROT. | RotPos | Rotor position | Position des Rotors | Posición del rotor | Położenie rotora | Angular rotor position | deg | Degrees | Live Value | Double | Live Value
WROT.RotSpd | WROT.RotSpd | WROT. | RotSpd | Rotor RPM | Rotor-Drehzahl | RPM del rotor | Obroty rotora | Rotor rotation speed | rpm | RPM | Live Value | Double | Live Value | Used in standard monitor Presentation
WROT.RotSpd_10m_Avg | #N/A | WROT. | RotSpd_10m_Avg | Rotor RPM (avg) | Rotor-Drehzahl (avg) | RPM del rotor (avg) | Obroty rotora (avg) | Rotor rotation speed | rpm | RPM | Average | Double | 10 minute tag | Common tags for analysis
WROT.RotSpd_10m_Max | #N/A | WROT. | RotSpd_10m_Max | Rotor RPM (max) | Rotor-Drehzahl (max) | RPM del rotor (max) | Obroty rotora (max) | Rotor rotation speed | rpm | RPM | Maximum | Double | 10 minute tag | Common tags for analysis
WROT.RotSpd_10m_Min | #N/A | WROT. | RotSpd_10m_Min | Rotor RPM (min) | Rotor-Drehzahl (min) | RPM del rotor (min) | Obroty rotora (min) | Rotor rotation speed | rpm | RPM | Minimum | Double | 10 minute tag | Common tags for analysis
WROT.RotSpd_10m_Std | #N/A | WROT. | RotSpd_10m_Std | Rotor RPM (std) | Rotor-Drehzahl (std) | RPM del rotor (std) | Obroty rotora (std) | Rotor rotation speed | rpm | RPM | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WROT.RotSpd1 | #N/A | WROT. | RotSpd1 | Rotor RPM | Rotor-Drehzahl | RPM del rotor | Obroty rotora | Rotor rotation speed sensor 1 | rpm | RPM | Live Value | Double | Live Value | Used in standard monitor Presentation
WROT.RotSpd1_10m_Avg | #N/A | WROT. | RotSpd1_10m_Avg | Rotor RPM (avg) | Rotor-Drehzahl (avg) | RPM del rotor (avg) | Obroty rotora (avg) | Rotor rotation speed sensor 1 | rpm | RPM | Average | Double | 10 minute tag | Common tags for analysis
WROT.RotSpd1_10m_Max | #N/A | WROT. | RotSpd1_10m_Max | Rotor RPM (max) | Rotor-Drehzahl (max) | RPM del rotor (max) | Obroty rotora (max) | Rotor rotation speed sensor 1 | rpm | RPM | Maximum | Double | 10 minute tag | Common tags for analysis
WROT.RotSpd1_10m_Min | #N/A | WROT. | RotSpd1_10m_Min | Rotor RPM (min) | Rotor-Drehzahl (min) | RPM del rotor (min) | Obroty rotora (min) | Rotor rotation speed sensor 1 | rpm | RPM | Minimum | Double | 10 minute tag | Common tags for analysis
WROT.RotSpd1_10m_Std | #N/A | WROT. | RotSpd1_10m_Std | Rotor RPM (std) | Rotor-Drehzahl (std) | RPM del rotor (std) | Obroty rotora (std) | Rotor rotation speed sensor 1 | rpm | RPM | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WROT.RotSpd2 | #N/A | WROT. | RotSpd2 | Rotor RPM | Rotor-Drehzahl | RPM del rotor | Obroty rotora | Rotor rotation speed sensor 2 | rpm | RPM | Live Value | Double | Live Value | Used in standard monitor Presentation
WROT.RotSpd2_10m_Avg | #N/A | WROT. | RotSpd2_10m_Avg | Rotor RPM (avg) | Rotor-Drehzahl (avg) | RPM del rotor (avg) | Obroty rotora (avg) | Rotor rotation speed sensor 2 | rpm | RPM | Average | Double | 10 minute tag | Common tags for analysis
WROT.RotSpd2_10m_Max | #N/A | WROT. | RotSpd2_10m_Max | Rotor RPM (max) | Rotor-Drehzahl (max) | RPM del rotor (max) | Obroty rotora (max) | Rotor rotation speed sensor 2 | rpm | RPM | Maximum | Double | 10 minute tag | Common tags for analysis
WROT.RotSpd2_10m_Min | #N/A | WROT. | RotSpd2_10m_Min | Rotor RPM (min) | Rotor-Drehzahl (min) | RPM del rotor (min) | Obroty rotora (min) | Rotor rotation speed sensor 2 | rpm | RPM | Minimum | Double | 10 minute tag | Common tags for analysis
WROT.RotSpd2_10m_Std | #N/A | WROT. | RotSpd2_10m_Std | Rotor RPM (std) | Rotor-Drehzahl (std) | RPM del rotor (std) | Obroty rotora (std) | Rotor rotation speed sensor 2 | rpm | RPM | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WROT.RotSt | WROT.RotSt | WROT. | RotSt | Rotor Status | Status des Rotors | Estado del rotor | Status rotora | Status of rotor | Enum | Enum | Live Value | Long | Live Value
WROT.SlpRngTmp | #N/A | WROT. | SlpRngTmp | Rotor Slip Ring Temp | Rotor-Schleifring Temperatur | Temperatura del anillo colector del rotor | Pierścień ślizgowy rotora Temp | Rotor Slip ring temperature | deg_c | °C | Live Value | Double | Live Value
WROT.SlpRngTmp_10m_Avg | #N/A | WROT. | SlpRngTmp_10m_Avg | Rotor Slip Ring Temp (avg) | Rotor-Schleifring Temperatur (avg) | Temperatura del anillo colector del rotor (avg) | Pierścień ślizgowy rotora Temp (avg) | Rotor Slip ring temperature | deg_c | °C | Average | Double | 10 minute tag
WROT.SlpRngTmp_10m_Max | #N/A | WROT. | SlpRngTmp_10m_Max | Rotor Slip Ring Temp (max) | Rotor-Schleifring Temperatur (max) | Temperatura del anillo colector del rotor (max) | Pierścień ślizgowy rotora Temp (max) | Rotor Slip ring temperature | deg_c | °C | Maximum | Double | 10 minute tag
WROT.SlpRngTmp_10m_Min | #N/A | WROT. | SlpRngTmp_10m_Min | Rotor Slip Ring Temp (min) | Rotor-Schleifring Temperatur (min) | Temperatura del anillo colector del rotor (min) | Pierścień ślizgowy rotora Temp (min) | Rotor Slip ring temperature | deg_c | °C | Minimum | Double | 10 minute tag
WROT.SlpRngTmp_10m_Std | #N/A | WROT. | SlpRngTmp_10m_Std | Rotor Slip Ring Temp (std) | Rotor-Schleifring Temperatur (std) | Temperatura del anillo colector del rotor (std) | Pierścień ślizgowy rotora Temp (std) | Rotor Slip ring temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WROT.SpinTmp | #N/A | WROT. | SpinTmp | Spinner Temp | Spinner-Temperatur | Temperatura del rotámetro | Spinner temp | Actual spinner temperature | deg_c | °C | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WROT.SupV | #N/A | WROT. | SupV | Hub supply voltage | Versorgungsspannung der Nabe | Tensión de suministro del buje | Napięcie zasilania Hub | Hub supply voltage | V | V | Live Value | Double | Live Value
WROT.SupV_10m_Avg | #N/A | WROT. | SupV_10m_Avg | Hub supply voltage (avg) | Versorgungsspannung der Nabe (avg) | Tensión de suministro del buje (avg) | Napięcie zasilania Hub (avg) | Hub supply voltage | V | V | Average | Double | 10 minute tag
WROT.SupV_10m_Max | #N/A | WROT. | SupV_10m_Max | Hub supply voltage (max) | Versorgungsspannung der Nabe (max) | Tensión de suministro del buje (max) | Napięcie zasilania Hub (max) | Hub supply voltage | V | V | Maximum | Double | 10 minute tag
WROT.SupV_10m_Min | #N/A | WROT. | SupV_10m_Min | Hub supply voltage (min) | Versorgungsspannung der Nabe (min) | Tensión de suministro del buje (min) | Napięcie zasilania Hub (min) | Hub supply voltage | V | V | Minimum | Double | 10 minute tag
WROT.SupV_10m_Std | #N/A | WROT. | SupV_10m_Std | Hub supply voltage (std) | Versorgungsspannung der Nabe (std) | Tensión de suministro del buje (std) | Napięcie zasilania Hub (std) | Hub supply voltage | V | V | Standard Deviation | Double | 10 minute tag
WROT.TipBrkPmpCnt | #N/A | WROT. | TipBrkPmpCnt | Number of activations of the hydraulic tip brake pump | Anzahl der Aktivierungen der hydraulischen Spitzenbremspumpe | Número de activaciones de la bomba de freno de la boquilla hidráulica | Liczba aktywacji hydraulicznej pompy hamulcowej końcówki | Number of activations of the hydraulic tip brake pump | count | Count | Total Counter | Long | Live Value
WROT.TipBrkPmpCnt_10m_End | #N/A | WROT. | TipBrkPmpCnt_10m_End | Number of activations of the hydraulic tip brake pump (end) | Anzahl der Aktivierungen der hydraulischen Spitzenbremspumpe (end) | Número de activaciones de la bomba de freno de la boquilla hidráulica (end) | Liczba aktywacji hydraulicznej pompy hamulcowej końcówki (end) | Number of activations of the hydraulic tip brake pump | count | Count | Endvalue | Long | 10 minute tag
WROT.TipBrkPmpTms | #N/A | WROT. | TipBrkPmpTms | Time the hydraulic tip brake pump has been activated | Zeit, in der die hydraulische Spitzenbremspumpe aktiviert wurde | Tiempo que la bomba de freno de la boquilla hidráulica ha estado activada | Czas aktywacji hydraulicznej pompy hamulca końcówki | Time the hydraulic tip brake pump has been activated | s | seconds | Total Counter | Long | Live Value
WROT.TipBrkPmpTms_10m_End | #N/A | WROT. | TipBrkPmpTms_10m_End | Time the hydraulic tip brake pump has been activated (end) | Zeit, in der die hydraulische Spitzenbremspumpe aktiviert wurde (end) | Tiempo que la bomba de freno de la boquilla hidráulica ha estado activada (end) | Czas aktywacji hydraulicznej pompy hamulca końcówki (end) | Time the hydraulic tip brake pump has been activated | s | seconds | Endvalue | Long | 10 minute tag
WRPC.CtlModStr | #N/A | WRPC. | CtlModStr | Reactive control mode text | Blindleistungsregelungsmodus Text | Texto de modo de control reactivo | Tekst trybu sterowania mocą bierną | Reactive control mode | String | String | Live Value | Double | Live Value | Universal Park Controller (UPC)
WRPC.CtlSt | #N/A | WRPC. | CtlSt | UPC Reactive power control state | UPC Status der Blindleistungsregelung | Estado del control de potencia reactiva de UPC | UPC Stan sterowania zasilanie biernym | Reactive power control state 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.CtlStStr | #N/A | WRPC. | CtlStStr | Reactive power control state text | Statustext Blindleistungsregelung | Texto del estado del control de potencia reactiva | Tekst stanu kontroli mocy biernej | Reactive power control state text | String | String | Live Value | Double | Live Value | Universal Park Controller (UPC)
WRPC.DrpSpt | WRPC.DrpSpt | WRPC. | DrpSpt | Setpoint for slope of voltage control droop | Sollwert für die Steigung des Spannungsabfalls | Punto de ajuste para pendiente de caída de control de tensión | Nastawa Pitch spadku w trybie reg. nap. | Set reference value for slope of voltage control droop |  |  | Setpoint | Double
WRPC.IntnPFSpt | #N/A | WRPC. | IntnPFSpt | UPC Internal Power factor setpoint | UPC Interner Leistungsfaktorsollwert | Punto de ajuste del factor de potencia interna de UPC | UPC Wewnętrzna nastawa współcz. mocy | Internal power factor setpoint | pf | PF | Live Value | Double | Live Value | Universal Park Controller (UPC)
WRPC.IntnPFSptSt | #N/A | WRPC. | IntnPFSptSt | UPC Internal power factor setpoint state | UPC Interner Leistungsfaktorsollwert Status | Estado del punto de ajuste del factor de potencia interna de UPC | UPC Wewnętrzny współczynnik mocy stan | Internal power factor setpoint state 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.IntnVArSpt | #N/A | WRPC. | IntnVArSpt | UPC Internal reactive power setpoint | UPC Interner Blindleistungssollwert | Punto de ajuste de potencia reactiva interna UPC | UPC Wewnętrzny nastawa mocy biernej | Internal reactive power setpoint | VAr | VAr | Live Value | Double | Live Value | Universal Park Controller (UPC)
WRPC.IntnVArSptSt | #N/A | WRPC. | IntnVArSptSt | UPC Internal reactive power setpoint state | UPC Interner Blindleistungssollwert Status | Estado del punto de ajuste de potencia reactiva interna UPC | UPC Wewnętrzny stan nastawy mocy biernej | Internal reactive power setpoint state 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.ManPFSpt | #N/A | WRPC. | ManPFSpt | UPC Manual power factor setpoint | UPC Manueller Leistungsfaktorsollwert | Punto de ajuste del factor de potencia manual de UPC | UPC Ręczna nastawa współczynnika mocy | Manual power factor setpoint | pf | PF | Setpoint | Double | Live Value | Universal Park Controller (UPC)
WRPC.ManPFSptSt | #N/A | WRPC. | ManPFSptSt | UPC Manual power factor setpoint state | Status UPC manueller Leistungsfaktorsollwert | Estado del punto de ajuste del factor de potencia manual de UPC | UPC Ręczny współczynnik mocy stan | Manual power factor setpoint state 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.ManVArModFD | #N/A | WRPC. | ManVArModFD | UPC Forced disabled | UPC Zwangsweise deaktiviert | Inhabilitación forzada de UPC | UPC Wymuszone wyłączenie | Forced disabled 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.ManVArModNone | #N/A | WRPC. | ManVArModNone | UPC No manual control | UPC Keine manuelle Regelung | Control no manual de UPC | UPC Brak ręcznego sterowania | No manual control 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.ManVArModPF | #N/A | WRPC. | ManVArModPF | UPC Power factor control | UPC Leistungsfaktor-Regelung | Control del factor de potencia de UPC | Kontrola współczynnika mocy UPC | Power factor control 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.ManVArModPFP | #N/A | WRPC. | ManVArModPFP | UPC Power factor control CosPhi(P) | UPC Leistungsfaktor-Regelung CosPhi(P) | Control del factor de potencia CosPhi(P) de UPC | Kontrola współczynnika mocy UPC CosPhi(P) | Power factor control CosPhi(P) 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.ManVArModQ | #N/A | WRPC. | ManVArModQ | UPC Reactive power control | UPC Blindleistungsregelung | Control de la potencia reactiva de UPC | Kontrola mocy biernej UPC | Reactive power control 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.ManVArModQP | #N/A | WRPC. | ManVArModQP | UPC Reactive power control (Q(P)) | UPC Blindleistungsregelung (Q(P)) | Control de la potencia reactiva (Q(P)) de UPC | Kontrola mocy biernej UPC (Q(P)) | Reactive power control (Q(P)) 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.ManVArModQPVDE | #N/A | WRPC. | ManVArModQPVDE | UPC Reactive power control (Q(P)) VDE2018 | UPC Blindleistungsregelung (Q(P)) VDE2018 | Control de la potencia reactiva (Q(P)) VDE2018 de UPC | Kontrola mocy biernej UPC (Q(P)) VDE2018 | Reactive power control (Q(P)) VDE2018 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.ManVArModQU | #N/A | WRPC. | ManVArModQU | UPC Reactive power control (Q(U)) | UPC Blindleistungsregelung (Q(U)) | Control de la potencia reactiva (Q(U)) de UPC | Regulacja mocy biernej UPC (Q(U)) | Reactive power control (Q(U)) 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.ManVArModQUVDE | #N/A | WRPC. | ManVArModQUVDE | UPC Reactive power control (Q(U)) VDE2018 | UPC Blindleistungsregelung (Q(U)) VDE2018 | Control de la potencia reactiva (Q(U)) VDE2018 de UPC | Kontrola mocy biernej UPC (Q(U)) VDE2018 | Reactive power control (Q(U)) VDE2018 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.ManVArModQVDE | #N/A | WRPC. | ManVArModQVDE | UPC Reactive control VDE2018 | UPC Blindleistungsregelung VDE2018 | Control reactivo VDE2018 de UPC | Sterowanie reaktywne UPC VDE2018 | Reactive control VDE2018 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.ManVArModU | #N/A | WRPC. | ManVArModU | UPC Voltage control | UPC Spannungsregelung | Control de la tensión de UPC | Kontrola napięcia UPC | Voltage control 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.ManVArSpt | #N/A | WRPC. | ManVArSpt | UPC Manual reactive power setpoint | UPC Manueller Blindleistungssollwert | Punto de ajuste de potencia reactiva manual de UPC | UPC Ręczna nastawa mocy biernej | Manual reactive power setpoint | VAr | VAr | Setpoint | Double | Live Value | Universal Park Controller (UPC)
WRPC.ManVArSptSt | #N/A | WRPC. | ManVArSptSt | UPC Manual reactive power setpoint state | UPC Manueller Blindleistungssollwertstatus | Estado del punto de ajuste de potencia reactiva manual de UPC | UPC Ręczny stan nastawy mocy biernej | Manual reactive power setpoint state 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.ManVRef | #N/A | WRPC. | ManVRef | UPC Manual voltage reference | UPC Manuelle Spannungsreferenz | Referencia de tensión manual de UPC | Ręczne odniesienie napięcia UPC | Manual voltage reference | V | V | Live Value | Double | Live Value | Universal Park Controller (UPC)
WRPC.ManVRefSt | #N/A | WRPC. | ManVRefSt | UPC Manual voltage reference state | UPC Manuelle Spannungsreferenz Status | Estado de referencia de tensión manual de UPC | Stan odniesienia napięcia UPC Manual | Manual voltage reference state 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.ManVSpt | #N/A | WRPC. | ManVSpt | UPC Manual voltage setpoint | UPC Manueller Spannungssollwert | Punto de ajuste de tensión manual de UPC | Ręczna nastawa napięcia UPC | Manual voltage setpoint | V | V | Setpoint | Double | Live Value | Universal Park Controller (UPC)
WRPC.ManVSptSt | #N/A | WRPC. | ManVSptSt | UPC Manual voltage setpoint state | UPC Manueller Spannungssollwertstatus | Estado del punto de ajuste de tensión manual de UPC | UPC Ręczny stan zadanej wartości napięcia | Manual voltage setpoint state 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.OpTurNum | WRPC.OpTurNum | WRPC. | OpTurNum | Actual number of wind turbines in operation | Tatsächliche Anzahl der in Betrieb befindlichen Windkraftanlagen | Cantidad real de turbinas eólicas en funcionamiento | Rzeczywista liczba turbin wiatrowych w eksploatacji | Actual number of wind turbines in operation | count | Count | Total Counter | Long | Live Value
WRPC.PF | WRPC.PF | WRPC. | PF | UPC Power factor | UPC Leistungsfaktor | Factor de potencia de UPC | Współczynnik mocy UPC | Wind power plant actual power factor | pf | pf | Live Value | Double | Live Value | Universal Park Controller (UPC)
WRPC.PF_10m_Avg | #N/A | WRPC. | PF_10m_Avg | UPC Power factor (avg) | UPC Leistungsfaktor (avg) | Factor de potencia de UPC (avg) | Współczynnik mocy UPC (avg) | Measured Power factor in PCC Average | pf | pf | Average | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.PF_10m_Max | #N/A | WRPC. | PF_10m_Max | UPC Power factor (max) | UPC Leistungsfaktor (max) | Factor de potencia de UPC (max) | Współczynnik mocy UPC (max) | Measured Power factor in PCC Maximum | pf | pf | Maximum | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.PF_10m_Min | #N/A | WRPC. | PF_10m_Min | UPC Power factor (min) | UPC Leistungsfaktor (min) | Factor de potencia de UPC (min) | Współczynnik mocy UPC (min) | Measured Power factor in PCC Minimum | pf | pf | Minimum | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.PF_1s_End | #N/A | WRPC. | PF_1s_End | UPC Power factor (end) | UPC Leistungsfaktor (end) | Factor de potencia de UPC (end) | Współczynnik mocy UPC (end) | Measured Power factor in PCC | pf | pf | Endvalue | Double | 1 second tag | Universal Park Controller (UPC)
WRPC.PFSign | WRPC.PFSign | WRPC. | PFSign | Power factor sign convention: | Vorzeichenkonvention für den Leistungsfaktor: | Convención del signo de factor de potencia: | Konwencja znaku współczynnika mocy: | Power factor sign convention: IEEE = 2 |  |  | Live Value | Long
WRPC.PFSpt | WRPC.PFSpt | WRPC. | PFSpt | UPC Power factor Setpoint | UPC Leistungsfaktor Sollwert | Punto de ajuste del factor de potencia de UPC | Współczynnik mocy UPC nastawa | Set reference value for wind power plant power factor – negative: lagging (producing reactive power); positive: leading (consuming reactive power) as defined by IEEE | pf | pf | Setpoint | Double | Live Value | Universal Park Controller (UPC)
WRPC.PFSpt_10m_Avg | #N/A | WRPC. | PFSpt_10m_Avg | UPC Power factor Setpoint (avg) | UPC Leistungsfaktor Sollwert (avg) | Punto de ajuste del factor de potencia de UPC (avg) | Współczynnik mocy UPC nastawa (avg) | Power factor setpoint Average | pf | pf | Average | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.PFSpt_10m_Max | #N/A | WRPC. | PFSpt_10m_Max | UPC Power factor Setpoint (max) | UPC Leistungsfaktor Sollwert (max) | Punto de ajuste del factor de potencia de UPC (max) | Współczynnik mocy UPC nastawa (max) | Power factor setpoint Maximum | pf | pf | Maximum | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.PFSpt_10m_Min | #N/A | WRPC. | PFSpt_10m_Min | UPC Power factor Setpoint (min) | UPC Leistungsfaktor Sollwert (min) | Punto de ajuste del factor de potencia de UPC (min) | Współczynnik mocy UPC nastawa (min) | Power factor Setpoint Minimum | pf | pf | Minimum | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.PFSpt_1s_End | #N/A | WRPC. | PFSpt_1s_End | UPC Power factor Setpoint (end) | UPC Leistungsfaktor Sollwert (end) | Punto de ajuste del factor de potencia de UPC (end) | Współczynnik mocy UPC nastawa (end) | Power factor setpoint | pf | pf | Endvalue | Double | 1 second tag | Universal Park Controller (UPC)
WRPC.PFSptSt | #N/A | WRPC. | PFSptSt | UPC Controller power factor setpoint state | UPC Regler Leistungsfaktor-Sollwertstatus | Estado del punto de ajuste del factor de potencia de la controladora de UPC | Stan wartości zadanej współczynnika mocy kontrolera UPC | Controller power factor setpoint state 1: Inactive 2: Active | Enum | Enum | Live Value | Double | Live Value | Universal Park Controller (UPC)
WRPC.PsblVArCap | #N/A | WRPC. | PsblVArCap | UPC Possible Capacitive power | UPC Mögliche kapazitive Leistung | Posible potencia capacitiva de UPC | UPC Możliwa moc pojemnościowa | Possible Capacitive power | VAr | VAr | Live Value | Double | Live Value | Universal Park Controller (UPC)
WRPC.PsblVArCap_10m_Avg | #N/A | WRPC. | PsblVArCap_10m_Avg | UPC Possible Capacitive power (avg) | UPC Mögliche kapazitive Leistung (avg) | Posible potencia capacitiva de UPC (avg) | UPC Możliwa moc pojemnościowa (avg) | Possible capacitive power Average | VAr | VAr | Average | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.PsblVArCap_10m_Max | #N/A | WRPC. | PsblVArCap_10m_Max | UPC Possible Capacitive power (max) | UPC Mögliche kapazitive Leistung (max) | Posible potencia capacitiva de UPC (max) | UPC Możliwa moc pojemnościowa (max) | Possible capacitive power Maximum | VAr | VAr | Maximum | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.PsblVArCap_10m_Min | #N/A | WRPC. | PsblVArCap_10m_Min | UPC Possible Capacitive power (min) | UPC Mögliche kapazitive Leistung (min) | Posible potencia capacitiva de UPC (min) | UPC Możliwa moc pojemnościowa (min) | Possible capacitive power Minimum | VAr | VAr | Minimum | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.PsblVArCap_1s_End | #N/A | WRPC. | PsblVArCap_1s_End | UPC Possible Capacitive power (end) | UPC Mögliche kapazitive Leistung (end) | Posible potencia capacitiva de UPC (end) | UPC Możliwa moc pojemnościowa (end) | Possible capacitive power | VAr | VAr | Endvalue | Double | 1 second tag | Universal Park Controller (UPC)
WRPC.PsblVArInd | #N/A | WRPC. | PsblVArInd | UPC Possible Inductive power | UPC Möglich Induktive Leistung | Posible potencia inductiva de UPC | UPC Możliwa moc indukcyjna | Possible Inductive | VAr | VAr | Live Value | Double | Live Value | Universal Park Controller (UPC)
WRPC.PsblVArInd_10m_Avg | #N/A | WRPC. | PsblVArInd_10m_Avg | UPC Possible Inductive power (avg) | UPC Möglich Induktive Leistung (avg) | Posible potencia inductiva de UPC (avg) | UPC Możliwa moc indukcyjna (avg) | Possible inductive power Average | VAr | VAr | Average | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.PsblVArInd_10m_Max | #N/A | WRPC. | PsblVArInd_10m_Max | UPC Possible Inductive power (max) | UPC Möglich Induktive Leistung (max) | Posible potencia inductiva de UPC (max) | UPC Możliwa moc indukcyjna (max) | Possible inductive power Maximum | VAr | VAr | Maximum | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.PsblVArInd_10m_Min | #N/A | WRPC. | PsblVArInd_10m_Min | UPC Possible Inductive power (min) | UPC Möglich Induktive Leistung (min) | Posible potencia inductiva de UPC (min) | UPC Możliwa moc indukcyjna (min) | Possible inductive power Minimum | VAr | VAr | Minimum | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.PsblVArInd_1s_End | #N/A | WRPC. | PsblVArInd_1s_End | UPC Possible Inductive power (end) | UPC Möglich Induktive Leistung (end) | Posible potencia inductiva de UPC (end) | UPC Możliwa moc indukcyjna (end) | Possible inductive power | VAr | VAr | Endvalue | Double | 1 second tag | Universal Park Controller (UPC)
WRPC.UtlPFSpt | #N/A | WRPC. | UtlPFSpt | UPC Utility Power factor setpoint | UPC Netzbetreiber Leistungsfaktorsollwert | Punto de ajuste del factor de potencia de utilidad de UPC | UPC Utility Współczynnik mocy | Utility power factor setpoint | pf | PF | Live Value | Double | Live Value | Universal Park Controller (UPC)
WRPC.UtlPFSptSt | #N/A | WRPC. | UtlPFSptSt | UPC Utility power factor setpoint state | UPC Netzbetreiber Leistungsfaktorsollwert Status | Estado del punto de ajuste del factor de potencia de utilidad de UPC | Stan wartości zadanej współczynnika mocy UPC Utility | Utility power factor setpoint state 0: No comm 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.UtlVArSpt | #N/A | WRPC. | UtlVArSpt | Utility reactive power setpoint | Blindleistungssollwert des Netzbetreibers | Punto de ajuste de potencia reactiva de utilidad | Zadana moc bierna użyteczności | Utility reactive power setpoint | VAr | VAr | Live Value | Double | Live Value | Universal Park Controller (UPC)
WRPC.UtlVArSptSt | #N/A | WRPC. | UtlVArSptSt | UPC Utility reactive power setpoint state | UPC Blindleistungssollwert Status des Netzbetreibers | Estado el punto de ajuste de potencia reactiva de utilidad de UPC | Stan nastawy mocy biernej UPC Utility | Utility reactive power setpoint state 0: No comm 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.UtlVRef | #N/A | WRPC. | UtlVRef | UPC Utility voltage reference | UPC Spannungsreferenz des Netzbetreibers | Referencia de tensión de utilidad de UPC | Odniesienie napięcia UPC Utility | Utility voltage reference | V | V | Live Value | Double | Live Value | Universal Park Controller (UPC)
WRPC.UtlVRefSt | #N/A | WRPC. | UtlVRefSt | UPC Utility voltage reference state | UPC Spannungsreferenz Status des Netzbetreibers | Estado de referencia de tensión de utilidad de UPC | Stan odniesienia napięcia UPC Utility | Utility voltage reference state 0: No comm 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.UtlVSpt | #N/A | WRPC. | UtlVSpt | UPC Utility voltage setpoint | UPC Spannungssollwert des Netzbetreibers | Punto de ajuste de tensión de utilidad de UPC | Zadana nastawa napięcia UPC Utility | Utility voltage setpoint | V | V | Live Value | Double | Live Value | Universal Park Controller (UPC)
WRPC.UtlVSptSt | #N/A | WRPC. | UtlVSptSt | UPC Utility voltage setpoint state | UPC Spannungssollwert Status des Netzbetreibers | Estado el punto de ajuste de tensión de utilidad de UPC | Stan zadanego napięcia UPC Utility | Utility voltage setpoint state 0: No comm 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.V | WRPC.V | WRPC. | V | Wind power plant output voltage at the external grid connection point | Ausgangsspannung der Windkraftanlage am externen Netzanschlusspunkt | Tensión de salida de la central eólica en el punto de conexión con la red externa | Napięcie wyjściowe elektrowni wiatrowej w punkcie przyłączenia do sieci zewnętrznej | Wind power plant output voltage at the external grid connection point |  |  | Live Value | Double | Live Value | Universal Park Controller (UPC)
WRPC.V_10m_Avg | #N/A | WRPC. | V_10m_Avg | UPC PCC Voltage (avg) | UPC PCC-Spannung (avg) | Tensión PCC UPC (avg) | Napięcie UPC PCC (avg) | Measured voltage in PCC Average | V | V | Average | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.V_10m_Max | #N/A | WRPC. | V_10m_Max | UPC PCC Voltage (max) | UPC PCC-Spannung (max) | Tensión PCC UPC (max) | Napięcie UPC PCC (max) | Measured voltage in PCC Maximum | V | V | Maximum | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.V_10m_Min | #N/A | WRPC. | V_10m_Min | UPC PCC Voltage (min) | UPC PCC-Spannung (min) | Tensión PCC UPC (min) | Napięcie UPC PCC (min) | Measured voltage in PCC Minimum | V | V | Minimum | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.V_1s_End | #N/A | WRPC. | V_1s_End | UPC PCC Voltage (end) | UPC PCC-Spannung (end) | Tensión PCC UPC (end) | Napięcie UPC PCC (end) | Measured voltage in PCC | V | V | Endvalue | Double | 1 second tag | Universal Park Controller (UPC)
WRPC.VAr | WRPC.VAr | WRPC. | VAr | UPC Wind power plant reactive power generation | UPC Windkraftanlage Blindleistungserzeugung | Generación de potencia reactiva de la central eólica UPC | Wytwarzanie energii biernej w elektrowni wiatrowej UPC | Wind power plant reactive power generation | VAr | VAr | Live Value | Double | Live Value | Universal Park Controller (UPC)
WRPC.VAr_10m_Avg | #N/A | WRPC. | VAr_10m_Avg | UPC PCC Reactive power (avg) | UPC PCC Blindleistung (avg) | Potencia reactiva PCC UPC (avg) | Moc bierna UPC PCC (avg) | Measured Reactive power in PCC Average | VAr | VAr | Average | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.VAr_10m_Max | #N/A | WRPC. | VAr_10m_Max | UPC PCC Reactive power (max) | UPC PCC Blindleistung (max) | Potencia reactiva PCC UPC (max) | Moc bierna UPC PCC (max) | Measured Reactive power in PCC Maximum | VAr | VAr | Maximum | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.VAr_10m_Min | #N/A | WRPC. | VAr_10m_Min | UPC PCC Reactive power (min) | UPC PCC Blindleistung (min) | Potencia reactiva PCC UPC (min) | Moc bierna UPC PCC (min) | Measured Reactive power in PCC Minimum | VAr | VAr | Minimum | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.VAr_1s_End | #N/A | WRPC. | VAr_1s_End | UPC PCC Reactive power (end) | UPC PCC Blindleistung (end) | Potencia reactiva PCC UPC (end) | Moc bierna UPC PCC (end) | Measured Reactive power in PCC | VAr | VAr | Endvalue | Double | 1 second tag | Universal Park Controller (UPC)
WRPC.VArAct | WRPC.VArAct | WRPC. | VArAct | Activate reactive power control function | Aktivieren der Blindleistungsregelungsfunktion | Activar función de control de potencia reactiva | Aktywuj funkcję sterowania mocą bierną | Activate reactive power control function | Enum | Enum | Live Value | Long
WRPC.VArCapExpt | WRPC.VArCapExpt | WRPC. | VArCapExpt | Wind power plant reactive power export capability | Blindleistungsexportfähigkeit der Windkraftanlage | Capacidad de exportación de potencia reactiva de la central eólica | Zdolność eksportu energii biernej elektrowni wiatrowej | Wind power plant reactive power export (supply) capability |  |  | Live Value | Double
WRPC.VArCapImpt | WRPC.VArCapImpt | WRPC. | VArCapImpt | Wind power plant reactive power import capability | Blindleistungsimportfähigkeit der Windkraftanlage | Capacidad de importación de potencia reactiva de la central eólica | Zdolność do importu energii biernej elektrowni wiatrowych | Wind power plant reactive power import (demand) capability |  |  | Live Value | Double
WRPC.VArDnGraSpt | WRPC.VArDnGraSpt | WRPC. | VArDnGraSpt | Setpoint for gradient for ramping down the wind power plant reactive power output | Sollwert für Gradient zum Herunterfahren der Windkraftanlagen-Blindleistungsabgabe | Punto de ajuste de gradiente para disminuir la salida de potencia reactiva de la central eólica | Zadana nachylenie dla obniżania mocy biernej elektrowni wiatrowej | Set reference value for gradient for ramping down the wind power plant reactive power output |  |  | Setpoint | Double
WRPC.VArMinCap | WRPC.VArMinCap | WRPC. | VArMinCap | Plant minimum reactive power | Mindestblindleistung der Anlage | Potencia reactiva mínima de la planta | Minimalna moc bierna instalacji | Wind power plant minimum reactive power capability of plant | VAr | VAr | Live Value | Double | Live Value
WRPC.VArMod | WRPC.VArMod | WRPC. | VArMod | Reactive power control mode | Modus der Blindleistungsregelung | Modo de control de la potencia reactiva | Tryb sterowania mocą bierną | Reactive power control mode | Enum | Enum | Live Value | Long
WRPC.VArMod_10m_End | #N/A | WRPC. | VArMod_10m_End | Reactive power control mode (end) | Modus der Blindleistungsregelung (end) | Modo de control de la potencia reactiva (end) | Tryb sterowania mocą bierną (end) | Reactive power control mode at the end of the 10minute period | Enum | Enum | Endvalue | Long | 10 minute tag | Universal Park Controller (UPC)
WRPC.VArMod_1s_End | #N/A | WRPC. | VArMod_1s_End | Reactive power control mode (end) | Modus der Blindleistungsregelung (end) | Modo de control de la potencia reactiva (end) | Tryb sterowania mocą bierną (end) | Reactive power control mode | Enum | Enum | Endvalue | Long | 1 second tag | Universal Park Controller (UPC)
WRPC.VArSpt | WRPC.VArSpt | WRPC. | VArSpt | UPC Reactive power setpoint | UPC Blindleistungssollwert | Punto de ajuste de potencia reactiva de UPC | Nastawa mocy biernej UPC | Set reference value of wind power plant reactive power output | VAr | VAr | Live Value | Double | Live Value | Universal Park Controller (UPC)
WRPC.VArSpt_10m_Avg | #N/A | WRPC. | VArSpt_10m_Avg | UPC Reactive power setpoint (avg) | UPC Blindleistungssollwert (avg) | Punto de ajuste de potencia reactiva de UPC (avg) | Nastawa mocy biernej UPC (avg) | Reactive power setpoint Average | VAr | VAr | Average | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.VArSpt_10m_Max | #N/A | WRPC. | VArSpt_10m_Max | UPC Reactive power setpoint (max) | UPC Blindleistungssollwert (max) | Punto de ajuste de potencia reactiva de UPC (max) | Nastawa mocy biernej UPC (max) | Reactive power setpoint Maximum | VAr | VAr | Maximum | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.VArSpt_10m_Min | #N/A | WRPC. | VArSpt_10m_Min | UPC Reactive power setpoint (min) | UPC Blindleistungssollwert (min) | Punto de ajuste de potencia reactiva de UPC (min) | Nastawa mocy biernej UPC (min) | Reactive power setpoint Minimum | VAr | VAr | Minimum | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.VArSpt_1s_End | #N/A | WRPC. | VArSpt_1s_End | UPC Reactive power setpoint (end) | UPC Blindleistungssollwert (end) | Punto de ajuste de potencia reactiva de UPC (end) | Nastawa mocy biernej UPC (end) | Reactive power setpoint | VAr | VAr | Endvalue | Double | 1 second tag | Universal Park Controller (UPC)
WRPC.VArSptSrc_10m_Avg | #N/A | WRPC. | VArSptSrc_10m_Avg | Turbine reactive power generation setpoint source (avg) | Quelle des Blindleistungssollwerts der Turbine (avg) | Fuente del punto de ajuste de generación de potencia reactiva de la turbina (avg) | Źródło zadanej mocy biernej turbiny (avg) | Turbine reactive power generation setpoint source | Enum | Enum | Average | Long | 10 minute tag
WRPC.VArSptSt | #N/A | WRPC. | VArSptSt | Controller reactive power setpoint state | Blindleistungssollwert Status des Reglers | Estado del punto de ajuste de potencia reactiva del controlador | Stan zadanej mocy biernej kontrolera | Controller reactive power setpoint state 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.VArUpGraSpt | WRPC.VArUpGraSpt | WRPC. | VArUpGraSpt | Setpoint for gradient for ramping up the wind power plant reactive power output | Sollwert für Gradient zum Hochfahren der Windkraftanlagen-Blindleistungsabgabe | Punto de ajuste para gradiente para aumentar la salida de potencia reactiva de la central eólica | Zadana dla gradientu dla zwiększenia mocy biernej elektrowni wiatrowej | Set reference value for gradient for ramping up the wind power plant reactive power output |  |  | Setpoint | Double
WRPC.VDnGraSpt | WRPC.VDnGraSpt | WRPC. | VDnGraSpt | Setpoint for wind power plant voltage ramping down | Sollwert für Spannungsabfall der Windkraftanlage | Punto de ajuste para disminuir la tensión de la central eólica | Wartości zadane dla spadku napięcia w elektrowni wiatrowej | Set reference value for wind power plant voltage ramping down |  |  | Setpoint | Double
WRPC.VSpt | WRPC.VSpt | WRPC. | VSpt | UPC Voltage reference | UPC Spannungsreferenz | Referencia de tensión de UPC | Odniesienie napięcia UPC | Set reference value for wind power plant voltage output | V | V | Live Value | Double | Live Value | Universal Park Controller (UPC)
WRPC.VSpt_10m_Avg | #N/A | WRPC. | VSpt_10m_Avg | UPC Voltage setpoint (avg) | UPC Spannungssollwert (avg) | Punto de ajuste de tensión de UPC (avg) | Zadana nastawa napięcia UPC (avg) | Voltage setpoint Average | V | V | Average | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.VSpt_10m_Max | #N/A | WRPC. | VSpt_10m_Max | UPC Voltage setpoint (max) | UPC Spannungssollwert (max) | Punto de ajuste de tensión de UPC (max) | Zadana nastawa napięcia UPC (max) | Voltage setpoint Maximum | V | V | Maximum | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.VSpt_10m_Min | #N/A | WRPC. | VSpt_10m_Min | UPC Voltage setpoint (min) | UPC Spannungssollwert (min) | Punto de ajuste de tensión de UPC (min) | Zadana nastawa napięcia UPC (min) | Voltage setpoint Minimum | V | V | Minimum | Double | 10 minute tag | Universal Park Controller (UPC)
WRPC.VSpt_1s_End | #N/A | WRPC. | VSpt_1s_End | UPC Voltage setpoint (end) | UPC Spannungssollwert (end) | Punto de ajuste de tensión de UPC (end) | Zadana nastawa napięcia UPC (end) | Voltage setpoint | V | V | Endvalue | Double | 1 second tag | Universal Park Controller (UPC)
WRPC.VSptSt | #N/A | WRPC. | VSptSt | Controller voltage setpoint state | Status des Spannungssollwerts des Reglers | Estado el punto de ajuste de tensión del controlador | Stan zadanego napięcia kontrolera | Controller voltage setpoint state 1: Inactive 2: Active | Enum | Enum | Live Value | Long | Live Value | Universal Park Controller (UPC)
WRPC.VUpGraSpt | WRPC.VUpGraSpt | WRPC. | VUpGraSpt | Setpoint for wind power plant voltage ramping up | Sollwert für das Hochfahren der Windkraftanlagenspannung | Punto de ajuste para aumentar la tensión de la central eólica | Nastawa dla wzrostu napięcia w elektrowni wiatrowej | Set reference value for wind power plant voltage ramping up |  |  | Setpoint | Double
WRPC.WMod_10m_End | #N/A | WRPC. | WMod_10m_End | UPC Active power control mode (end) | UPC Modus der Wirkleistungsregelung (end) | Modo de control de la potencia activa de UPC (end) | Tryb aktywnej regulacji mocy UPC (end) | Active power control mode at the end of the 10 minute period | Enum | Enum | Endvalue | Long | 10 minute tag | Universal Park Controller (UPC)
WRPC.WMod_1s_End | #N/A | WRPC. | WMod_1s_End | UPC Active power control mode (end) | UPC Modus der Wirkleistungsregelung (end) | Modo de control de la potencia activa de UPC (end) | Tryb aktywnej regulacji mocy UPC (end) | Active power control mode | Enum | Enum | Endvalue | Long | 1 second tag | Universal Park Controller (UPC)
WTOW.DehumSt | WTOW.DehumSt | WTOW. | DehumSt | De-humidifier Status | Status der Entfeuchtung | Estado del deshumidificador | Stan odwilżacza | Status of de-humidifier | Enum | Enum | Live Value | Long | Live Value
WTOW.DirDsp | #N/A | WTOW. | DirDsp | Tower displacement | Turmverschiebung | Desplazamiento de torre | Przemieszczenie wieży | Aggregated Tower displacement | mm | mm | Live Value | Double | Live Value | Foundation Monitoring
WTOW.DirDsp_10m_Avg | #N/A | WTOW. | DirDsp_10m_Avg | Tower displacement (avg) | Turmverschiebung (avg) | Desplazamiento de torre (avg) | Przemieszczenie wieży (avg) | Aggregated Tower displacement calculated as 10 minutes sliding average | mm | mm | Average | Double | 10 minute tag | Foundation Monitoring
WTOW.DirDsp_10m_Max | #N/A | WTOW. | DirDsp_10m_Max | Tower displacement (max) | Turmverschiebung (max) | Desplazamiento de torre (max) | Przemieszczenie wieży (max) | Aggregated Tower displacement calculated as 10 minutes sliding average | mm | mm | Maximum | Double | 10 minute tag | Foundation Monitoring
WTOW.DirDsp_10m_Min | #N/A | WTOW. | DirDsp_10m_Min | Tower displacement (min) | Turmverschiebung (min) | Desplazamiento de torre (min) | Przemieszczenie wieży (min) | Aggregated Tower displacement calculated as 10 minutes sliding average | mm | mm | Minimum | Double | 10 minute tag | Foundation Monitoring
WTOW.DirDsp_10m_Std | #N/A | WTOW. | DirDsp_10m_Std | Tower displacement (std) | Turmverschiebung (std) | Desplazamiento de torre (std) | Przemieszczenie wieży (std) | Aggregated Tower displacement calculated as 10 minutes sliding average | mm | mm | Standard Deviation | Double | 10 minute tag | Foundation Monitoring
WTOW.DirDsp1 | #N/A | WTOW. | DirDsp1 | Tower displacement sensor 1 | Turmverschiebungssensor 1 | Sensor 1 de desplazamiento del torre | Czujnik przemieszczenia wieży 1 | Measured tower displacement sensor 1. | mm | mm | Live Value | Double | Live Value | Foundation Monitoring
WTOW.DirDsp1_10m_Avg | #N/A | WTOW. | DirDsp1_10m_Avg | Tower displacement sensor 1 (avg) | Turmverschiebungssensor 1 (avg) | Sensor 1 de desplazamiento del torre (avg) | Czujnik przemieszczenia wieży 1 (avg) | Average tower displacement sensor 1 occurs over a sliding 10 minute window. | mm | mm | Average | Double | 10 minute tag | Foundation Monitoring
WTOW.DirDsp1_10m_Max | #N/A | WTOW. | DirDsp1_10m_Max | Tower displacement sensor 1 (max) | Turmverschiebungssensor 1 (max) | Sensor 1 de desplazamiento del torre (max) | Czujnik przemieszczenia wieży 1 (max) | Average tower displacement sensor 1 occurs over a sliding 10 minute window. | mm | mm | Maximum | Double | 10 minute tag | Foundation Monitoring
WTOW.DirDsp1_10m_Min | #N/A | WTOW. | DirDsp1_10m_Min | Tower displacement sensor 1 (min) | Turmverschiebungssensor 1 (min) | Sensor 1 de desplazamiento del torre (min) | Czujnik przemieszczenia wieży 1 (min) | Average tower displacement sensor 1 occurs over a sliding 10 minute window. | mm | mm | Minimum | Double | 10 minute tag | Foundation Monitoring
WTOW.DirDsp1_10m_Std | #N/A | WTOW. | DirDsp1_10m_Std | Tower displacement sensor 1 (std) | Turmverschiebungssensor 1 (std) | Sensor 1 de desplazamiento del torre (std) | Czujnik przemieszczenia wieży 1 (std) | Average tower displacement sensor 1 occurs over a sliding 10 minute window. | mm | mm | Standard Deviation | Double | 10 minute tag | Foundation Monitoring
WTOW.DirDsp2 | #N/A | WTOW. | DirDsp2 | Tower displacement sensor 2 | Turmverschiebungssensor 2 | Sensor 2 de desplazamiento del torre | Czujnik przemieszczenia wieży 2 | Measured tower displacement sensor 2. | mm | mm | Live Value | Double | Live Value | Foundation Monitoring
WTOW.DirDsp2_10m_Avg | #N/A | WTOW. | DirDsp2_10m_Avg | Tower displacement sensor 2 (avg) | Turmverschiebungssensor 2 (avg) | Sensor 2 de desplazamiento del torre (avg) | Czujnik przemieszczenia wieży 2 (avg) | Average tower displacement sensor 2 occurs over a sliding 10 minute window. | mm | mm | Average | Double | 10 minute tag | Foundation Monitoring
WTOW.DirDsp2_10m_Max | #N/A | WTOW. | DirDsp2_10m_Max | Tower displacement sensor 2 (max) | Turmverschiebungssensor 2 (max) | Sensor 2 de desplazamiento del torre (max) | Czujnik przemieszczenia wieży 2 (max) | Average tower displacement sensor 2 occurs over a sliding 10 minute window. | mm | mm | Maximum | Double | 10 minute tag | Foundation Monitoring
WTOW.DirDsp2_10m_Min | #N/A | WTOW. | DirDsp2_10m_Min | Tower displacement sensor 2 (min) | Turmverschiebungssensor 2 (min) | Sensor 2 de desplazamiento del torre (min) | Czujnik przemieszczenia wieży 2 (min) | Average tower displacement sensor 2 occurs over a sliding 10 minute window. | mm | mm | Minimum | Double | 10 minute tag | Foundation Monitoring
WTOW.DirDsp2_10m_Std | #N/A | WTOW. | DirDsp2_10m_Std | Tower displacement sensor 2 (std) | Turmverschiebungssensor 2 (std) | Sensor 2 de desplazamiento del torre (std) | Czujnik przemieszczenia wieży 2 (std) | Average tower displacement sensor 2 occurs over a sliding 10 minute window. | mm | mm | Standard Deviation | Double | 10 minute tag | Foundation Monitoring
WTOW.DirDsp3 | #N/A | WTOW. | DirDsp3 | Tower displacement sensor 3 | Turmverschiebungssensor 3 | Sensor 3 de desplazamiento del torre | Czujnik przemieszczenia wieży 3 | Measured tower displacement sensor 3. | mm | mm | Live Value | Double | Live Value | Foundation Monitoring
WTOW.DirDsp3_10m_Avg | #N/A | WTOW. | DirDsp3_10m_Avg | Tower displacement sensor 3 (avg) | Turmverschiebungssensor 3 (avg) | Sensor 3 de desplazamiento del torre (avg) | Czujnik przemieszczenia wieży 3 (avg) | Average tower displacement sensor 3 occurs over a sliding 10 minute window. | mm | mm | Average | Double | 10 minute tag | Foundation Monitoring
WTOW.DirDsp3_10m_Max | #N/A | WTOW. | DirDsp3_10m_Max | Tower displacement sensor 3 (max) | Turmverschiebungssensor 3 (max) | Sensor 3 de desplazamiento del torre (max) | Czujnik przemieszczenia wieży 3 (max) | Average tower displacement sensor 3 occurs over a sliding 10 minute window. | mm | mm | Maximum | Double | 10 minute tag | Foundation Monitoring
WTOW.DirDsp3_10m_Min | #N/A | WTOW. | DirDsp3_10m_Min | Tower displacement sensor 3 (min) | Turmverschiebungssensor 3 (min) | Sensor 3 de desplazamiento del torre (min) | Czujnik przemieszczenia wieży 3 (min) | Average tower displacement sensor 3 occurs over a sliding 10 minute window. | mm | mm | Minimum | Double | 10 minute tag | Foundation Monitoring
WTOW.DirDsp3_10m_Std | #N/A | WTOW. | DirDsp3_10m_Std | Tower displacement sensor 3 (std) | Turmverschiebungssensor 3 (std) | Sensor 3 de desplazamiento del torre (std) | Czujnik przemieszczenia wieży 3 (std) | Average tower displacement sensor 3 occurs over a sliding 10 minute window. | mm | mm | Standard Deviation | Double | 10 minute tag | Foundation Monitoring
WTOW.DirDspLvlSpt1 | #N/A | WTOW. | DirDspLvlSpt1 | Tower displacement threshold 1 | Turmverschiebung Schwelle 1 | Desplazamiento de torre límite 1 | Próg przemieszczenia wieży 1 | Default: 4.0 mm. If WTOW.DirDsp deviates more that this level, WTOW.DirDspLvlSt1 is set high. | mm | mm | Setpoint | Double | Live Value | Foundation Monitoring
WTOW.DirDspLvlSpt2 | #N/A | WTOW. | DirDspLvlSpt2 | Tower displacement threshold 2 | Turmverschiebung Schwelle 2 | Desplazamiento de torre límite 2 | Próg przemieszczenia wieży 2 | Default: 5.0 mm. If WTOW.DirDsp deviates more that this level, WTOW.DirDspLvlSt2 is set high. | mm | mm | Setpoint | Double | Live Value | Foundation Monitoring
WTOW.DirDspLvlSpt3 | #N/A | WTOW. | DirDspLvlSpt3 | Tower displacement threshold 3 | Turmverschiebung Schwelle 3 | Desplazamiento de torre límite 3 | Próg przemieszczenia wieży 3 | Default: 10.0 mm. If WTOW.DirDsp deviates more that this level, WTOW.DirDspLvlSt3 is set high. | mm | mm | Setpoint | Double | Live Value | Foundation Monitoring
WTOW.DirDspLvlSt1 | #N/A | WTOW. | DirDspLvlSt1 | Foundation Monitoring Level 1 Status | Status der Fundamentüberwachung Stufe 1 | Estado del nivel 1 de monitoreo de fundación | Monitorowanie fundamentów Poziom 1 Status | High when WTOW.DirDsp deviates more than WTOW.DirDspSpt1. | Enum | Enum | Live Value | Boolean | Live Value | Foundation Monitoring
WTOW.DirDspLvlSt2 | #N/A | WTOW. | DirDspLvlSt2 | Foundation Monitoring Level 2 Status | Status der Fundamentüberwachung Stufe 2 | Estado del nivel 2 de monitoreo de fundación | Monitorowanie fundamentów Poziom 2 Status | High when WTOW.DirDsp deviates more than WTOW.DirDspSpt2. | Enum | Enum | Live Value | Boolean | Live Value | Foundation Monitoring
WTOW.DirDspLvlSt3 | #N/A | WTOW. | DirDspLvlSt3 | Foundation Monitoring Level 3 Status | Status der Fundamentüberwachung Stufe 3 | Estado del nivel 3 de monitoreo de fundación | Monitorowanie fundamentów Poziom 3 Status | High when WTOW.DirDsp deviates more than WTOW.DirDspSpt3. | Enum | Enum | Live Value | Boolean | Live Value | Foundation Monitoring
WTOW.DirDspRst | #N/A | WTOW. | DirDspRst | Foundation Monitoring Calibration command | Fundamentüberwachung Kalibrierungsbefehl | Comando de calibración de monitoreo de fundación | Polecenie Kalibracja monitorowania fundamentów | Instruction to reset calibration of all sensor to present value. | Enum | Enum | Command | Boolean | Live Value | Foundation Monitoring
WTOW.GndCtlTmp | #N/A | WTOW. | GndCtlTmp | Ground Controller Temp | Bodenregler Temperatur | Temperatura del controlador de tierra | Ground kontroler Temp | Temperature in the ground controller | deg_c | °C | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WTOW.GndCtlTmp_10m_Avg | #N/A | WTOW. | GndCtlTmp_10m_Avg | Ground Controller Temp (avg) | Bodenregler Temperatur (avg) | Temperatura del controlador de tierra (avg) | Ground kontroler Temp (avg) | Temperature in the ground controller | deg_c | °C | Average | Double | 10 minute tag
WTOW.GndCtlTmp_10m_Max | #N/A | WTOW. | GndCtlTmp_10m_Max | Ground Controller Temp (max) | Bodenregler Temperatur (max) | Temperatura del controlador de tierra (max) | Ground kontroler Temp (max) | Temperature in the ground controller | deg_c | °C | Maximum | Double | 10 minute tag
WTOW.GndCtlTmp_10m_Min | #N/A | WTOW. | GndCtlTmp_10m_Min | Ground Controller Temp (min) | Bodenregler Temperatur (min) | Temperatura del controlador de tierra (min) | Ground kontroler Temp (min) | Temperature in the ground controller | deg_c | °C | Minimum | Double | 10 minute tag
WTOW.GndCtlTmp_10m_Std | #N/A | WTOW. | GndCtlTmp_10m_Std | Ground Controller Temp (std) | Bodenregler Temperatur (std) | Temperatura del controlador de tierra (std) | Ground kontroler Temp (std) | Temperature in the ground controller | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTOW.HtexSt | WTOW.HtexSt | WTOW. | HtexSt | Heat Exchanger Status | Status des Wärmetauschers | Estado del intercambiador de calor | Stan wymiennika ciepła | Status of heat-exchanger | Enum | Enum | Live Value | Long | Live Value
WTOW.IntnHum | WTOW.IntnHum | WTOW. | IntnHum | Humidity inside tower | Luftfeuchtigkeit im Turm | Humedad en el interior de la torre | Wilgotność wewnątrz wieży | Humidity inside tower | percent | percent | Live Value | Double | Live Value
WTOW.IntnHum_10m_Avg | #N/A | WTOW. | IntnHum_10m_Avg | Humidity inside tower (avg) | Luftfeuchtigkeit im Turm (avg) | Humedad en el interior de la torre (avg) | Wilgotność wewnątrz wieży (avg) | Humidity inside tower | percent | percent | Average | Double | 10 minute tag
WTOW.IntnHum_10m_Max | #N/A | WTOW. | IntnHum_10m_Max | Humidity inside tower (max) | Luftfeuchtigkeit im Turm (max) | Humedad en el interior de la torre (max) | Wilgotność wewnątrz wieży (max) | Humidity inside tower | percent | percent | Maximum | Double | 10 minute tag
WTOW.IntnHum_10m_Min | #N/A | WTOW. | IntnHum_10m_Min | Humidity inside tower (min) | Luftfeuchtigkeit im Turm (min) | Humedad en el interior de la torre (min) | Wilgotność wewnątrz wieży (min) | Humidity inside tower | percent | percent | Minimum | Double | 10 minute tag
WTOW.IntnHum_10m_Std | #N/A | WTOW. | IntnHum_10m_Std | Humidity inside tower (std) | Luftfeuchtigkeit im Turm (std) | Humedad en el interior de la torre (std) | Wilgotność wewnątrz wieży (std) | Humidity inside tower | percent | percent | Standard Deviation | Double | 10 minute tag
WTOW.IntnTmp | #N/A | WTOW. | IntnTmp | Tower Temp | Turmtemperatur | Temperatura de la torre | Wieża Temp | Temperature inside tower | deg_c | °C | Live Value | Double | Live Value
WTOW.IntnTmp_10m_Avg | #N/A | WTOW. | IntnTmp_10m_Avg | Tower Temp (avg) | Turmtemperatur (avg) | Temperatura de la torre (avg) | Wieża Temp (avg) | Temperature inside tower | deg_c | °C | Average | Double | 10 minute tag
WTOW.IntnTmp_10m_Max | #N/A | WTOW. | IntnTmp_10m_Max | Tower Temp (max) | Turmtemperatur (max) | Temperatura de la torre (max) | Wieża Temp (max) | Temperature inside tower | deg_c | °C | Maximum | Double | 10 minute tag
WTOW.IntnTmp_10m_Min | #N/A | WTOW. | IntnTmp_10m_Min | Tower Temp (min) | Turmtemperatur (min) | Temperatura de la torre (min) | Wieża Temp (min) | Temperature inside tower | deg_c | °C | Minimum | Double | 10 minute tag
WTOW.IntnTmp_10m_Std | #N/A | WTOW. | IntnTmp_10m_Std | Tower Temp (std) | Turmtemperatur (std) | Temperatura de la torre (std) | Wieża Temp (std) | Temperature inside tower | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTOW.LftPos | WTOW.LftPos | WTOW. | LftPos | Tower Lift position | Position des Turmaufzugs | Posición del ascensor de la torre | Położenie windy wieżowej | Lift position |  |  | Live Value | Double
WTOW.LftSt | WTOW.LftSt | WTOW. | LftSt | Lift system Status | Status des Aufzugssystems | Estado del ascensor de la torre | Stan systemu podnoszenia | Status of lift system | Enum | Enum | Live Value | Long | Live Value
WTOW.LoIntnTmp | #N/A | WTOW. | LoIntnTmp | Tower Base Temp | Turm Basis Temperatur | Temperatura de la base de la torre | Podstawa wieży Temp | Temperature base tower | deg_c | °C | Live Value | Double | Live Value
WTOW.LoIntnTmp_10m_Avg | #N/A | WTOW. | LoIntnTmp_10m_Avg | Tower Base Temp (avg) | Turm Basis Temperatur (avg) | Temperatura de la base de la torre (avg) | Podstawa wieży Temp (avg) | Temperature base tower | deg_c | °C | Average | Double | 10 minute tag
WTOW.LoIntnTmp_10m_Max | #N/A | WTOW. | LoIntnTmp_10m_Max | Tower Base Temp (max) | Turm Basis Temperatur (max) | Temperatura de la base de la torre (max) | Podstawa wieży Temp (max) | Temperature base tower | deg_c | °C | Maximum | Double | 10 minute tag
WTOW.LoIntnTmp_10m_Min | #N/A | WTOW. | LoIntnTmp_10m_Min | Tower Base Temp (min) | Turm Basis Temperatur (min) | Temperatura de la base de la torre (min) | Podstawa wieży Temp (min) | Temperature base tower | deg_c | °C | Minimum | Double | 10 minute tag
WTOW.LoIntnTmp_10m_Std | #N/A | WTOW. | LoIntnTmp_10m_Std | Tower Base Temp (std) | Turm Basis Temperatur (std) | Temperatura de la base de la torre (std) | Podstawa wieży Temp (std) | Temperature base tower | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTOW.Vbr | #N/A | WTOW. | Vbr | Tower vibration | Turmschwingung | Vibración de la torre | Wibracje wieży | Vibration in the tower |  |  | Live Value | Double | Live Value
WTOW.Vbr_10m_Avg | #N/A | WTOW. | Vbr_10m_Avg | Tower vibration (avg) | Turmschwingung (avg) | Vibración de la torre (avg) | Wibracje wieży (avg) | Vibration in the tower |  |  | Average | Double | 10 minute tag
WTOW.Vbr_10m_Max | #N/A | WTOW. | Vbr_10m_Max | Tower vibration (max) | Turmschwingung (max) | Vibración de la torre (max) | Wibracje wieży (max) | Vibration in the tower |  |  | Maximum | Double | 10 minute tag
WTOW.Vbr_10m_Min | #N/A | WTOW. | Vbr_10m_Min | Tower vibration (min) | Turmschwingung (min) | Vibración de la torre (min) | Wibracje wieży (min) | Vibration in the tower |  |  | Minimum | Double | 10 minute tag
WTOW.Vbr_10m_Std | #N/A | WTOW. | Vbr_10m_Std | Tower vibration (std) | Turmschwingung (std) | Vibración de la torre (std) | Wibracje wieży (std) | Vibration in the tower |  |  | Standard Deviation | Double | 10 minute tag
WTOW.VbrSt | #N/A | WTOW. | VbrSt | Shock detector | Schock-Detektor | Detector de choques | Detektor wstrząsów | Shock detector | Enum | Enum | Live Value | Double | Live Value
WTOW.XdirVbr | #N/A | WTOW. | XdirVbr | Tower vibration in longitudinal direction | Turmschwingung in Längsrichtung | Vibración de la torre en dirección longitudinal | Drgania wieży w kierunku wzdłużnym | Vibration in tower in x direction (longitudinal) cm/s^2 | Enum | Enum | Live Value | Long | Live Value
WTOW.XdirVbr_10m_Avg | #N/A | WTOW. | XdirVbr_10m_Avg | Vibration in tower in longitudinal direction (avg) | Schwingung im Turm in Längsrichtung (avg) | Vibración de la torre en dirección longitudinal (avg) | Drgania w wieży w kierunku wzdłużnym (avg) | Vibration in the tower in longitudinal direction |  |  | Average | Double | 10 minute tag
WTOW.XdirVbr_10m_Max | #N/A | WTOW. | XdirVbr_10m_Max | Vibration in tower in longitudinal direction (max) | Schwingung im Turm in Längsrichtung (max) | Vibración de la torre en dirección longitudinal (max) | Drgania w wieży w kierunku wzdłużnym (max) | Vibration in the tower in longitudinal direction |  |  | Maximum | Double | 10 minute tag
WTOW.XdirVbr_10m_Min | #N/A | WTOW. | XdirVbr_10m_Min | Vibration in tower in longitudinal direction (min) | Schwingung im Turm in Längsrichtung (min) | Vibración de la torre en dirección longitudinal (min) | Drgania w wieży w kierunku wzdłużnym (min) | Vibration in the tower in longitudinal direction |  |  | Minimum | Double | 10 minute tag
WTOW.XdirVbr_10m_Std | #N/A | WTOW. | XdirVbr_10m_Std | Vibration in tower in longitudinal direction (std) | Schwingung im Turm in Längsrichtung (std) | Vibración de la torre en dirección longitudinal (std) | Drgania w wieży w kierunku wzdłużnym (std) | Vibration in the tower in longitudinal direction |  |  | Standard Deviation | Double | 10 minute tag
WTOW.XdirVbrClc_10m_Avg | #N/A | WTOW. | XdirVbrClc_10m_Avg | Vibration in tower in longitudinal direction with input filter (avg) | Schwingungen im Turm in Längsrichtung mit Eingangsfilter (avg) | Vibración de la torre en dirección longitudinal con filtro de entrada (avg) | Drgania w wieży w kierunku wzdłużnym z filtrem wejściowym (avg) | Vibration in the tower in longitudinal direction with input filter |  |  | Average | Double | 10 minute tag
WTOW.XdirVbrClc_10m_Max | #N/A | WTOW. | XdirVbrClc_10m_Max | Vibration in tower in longitudinal direction with input filter (max) | Schwingungen im Turm in Längsrichtung mit Eingangsfilter (max) | Vibración de la torre en dirección longitudinal con filtro de entrada (max) | Drgania w wieży w kierunku wzdłużnym z filtrem wejściowym (max) | Vibration in the tower in longitudinal direction with input filter |  |  | Maximum | Double | 10 minute tag
WTOW.XdirVbrClc_10m_Min | #N/A | WTOW. | XdirVbrClc_10m_Min | Vibration in tower in longitudinal direction with input filter (min) | Schwingungen im Turm in Längsrichtung mit Eingangsfilter (min) | Vibración de la torre en dirección longitudinal con filtro de entrada (min) | Drgania w wieży w kierunku wzdłużnym z filtrem wejściowym (min) | Vibration in the tower in longitudinal direction with input filter |  |  | Minimum | Double | 10 minute tag
WTOW.XdirVbrClc_10m_Std | #N/A | WTOW. | XdirVbrClc_10m_Std | Vibration in tower in longitudinal direction with input filter (std) | Schwingungen im Turm in Längsrichtung mit Eingangsfilter (std) | Vibración de la torre en dirección longitudinal con filtro de entrada (std) | Drgania w wieży w kierunku wzdłużnym z filtrem wejściowym (std) | Vibration in the tower in longitudinal direction with input filter |  |  | Standard Deviation | Double | 10 minute tag
WTOW.YdirVbr | #N/A | WTOW. | YdirVbr | Tower vibration in Lateral direction | Turmschwingungen in seitlicher Richtung | Vibración de la torre en dirección lateral | Drgania wieży w kierunku bocznym | Vibration in tower in Y direction (Lateral) cm/s^2 | Enum | Enum | Live Value | Long | Live Value
WTOW.YdirVbr_10m_Avg | #N/A | WTOW. | YdirVbr_10m_Avg | Vibration in tower in Lateral direction (avg) | Schwingungen im Turm in seitlicher Richtung (avg) | Vibración de la torre en dirección lateral (avg) | Wibracje w wieży w kierunku bocznym (avg) | Vibration in the tower in Lateral direction |  |  | Average | Double | 10 minute tag
WTOW.YdirVbr_10m_Max | #N/A | WTOW. | YdirVbr_10m_Max | Vibration in tower in Lateral direction (max) | Schwingungen im Turm in seitlicher Richtung (max) | Vibración de la torre en dirección lateral (max) | Wibracje w wieży w kierunku bocznym (max) | Vibration in the tower in Lateral direction |  |  | Maximum | Double | 10 minute tag
WTOW.YdirVbr_10m_Min | #N/A | WTOW. | YdirVbr_10m_Min | Vibration in tower in Lateral direction (min) | Schwingungen im Turm in seitlicher Richtung (min) | Vibración de la torre en dirección lateral (min) | Wibracje w wieży w kierunku bocznym (min) | Vibration in the tower in Lateral direction |  |  | Minimum | Double | 10 minute tag
WTOW.YdirVbr_10m_Std | #N/A | WTOW. | YdirVbr_10m_Std | Vibration in tower in Lateral direction (std) | Schwingungen im Turm in seitlicher Richtung (std) | Vibración de la torre en dirección lateral (std) | Wibracje w wieży w kierunku bocznym (std) | Vibration in the tower in Lateral direction |  |  | Standard Deviation | Double | 10 minute tag
WTOW.YdirVbrClc_10m_Avg | #N/A | WTOW. | YdirVbrClc_10m_Avg | Vibration in tower in Lateral direction with input filter (avg) | Schwingung im Turm in seitlicher Richtung mit Eingangsfilter (avg) | Vibración de la torre en dirección lateral con filtro de entrada (avg) | Drgania w wieży w kierunku bocznym z filtrem wejściowym (avg) | Vibration in the tower in Lateral direction with input filter |  |  | Average | Double | 10 minute tag
WTOW.YdirVbrClc_10m_Max | #N/A | WTOW. | YdirVbrClc_10m_Max | Vibration in tower in Lateral direction with input filter (max) | Schwingung im Turm in seitlicher Richtung mit Eingangsfilter (max) | Vibración de la torre en dirección lateral con filtro de entrada (max) | Drgania w wieży w kierunku bocznym z filtrem wejściowym (max) | Vibration in the tower in Lateral direction with input filter |  |  | Maximum | Double | 10 minute tag
WTOW.YdirVbrClc_10m_Min | #N/A | WTOW. | YdirVbrClc_10m_Min | Vibration in tower in Lateral direction with input filter (min) | Schwingung im Turm in seitlicher Richtung mit Eingangsfilter (min) | Vibración de la torre en dirección lateral con filtro de entrada (min) | Drgania w wieży w kierunku bocznym z filtrem wejściowym (min) | Vibration in the tower in Lateral direction with input filter |  |  | Minimum | Double | 10 minute tag
WTOW.YdirVbrClc_10m_Std | #N/A | WTOW. | YdirVbrClc_10m_Std | Vibration in tower in Lateral direction with input filter (std) | Schwingung im Turm in seitlicher Richtung mit Eingangsfilter (std) | Vibración de la torre en dirección lateral con filtro de entrada (std) | Drgania w wieży w kierunku bocznym z filtrem wejściowym (std) | Vibration in the tower in Lateral direction with input filter |  |  | Standard Deviation | Double | 10 minute tag
WTRF.AirOutTmp | #N/A | WTRF. | AirOutTmp | Transformer air Outlet Temp | Transformatorluft Austrittstemperatur | Temperatura de la salida de aire del transformador | Temp wylotu powietrza transformatora | Outlet temperature of high voltage transformer | deg_c | °C | Live Value | Double | Live Value
WTRF.AirOutTmp_10m_Avg | #N/A | WTRF. | AirOutTmp_10m_Avg | Transformer air Outlet Temp (avg) | Transformatorluft Austrittstemperatur (avg) | Temperatura de la salida de aire del transformador (avg) | Temp wylotu powietrza transformatora (avg) | Outlet temperature of high voltage transformer | deg_c | °C | Average | Double | 10 minute tag
WTRF.AirOutTmp_10m_Max | #N/A | WTRF. | AirOutTmp_10m_Max | Transformer air Outlet Temp (max) | Transformatorluft Austrittstemperatur (max) | Temperatura de la salida de aire del transformador (max) | Temp wylotu powietrza transformatora (max) | Outlet temperature of high voltage transformer | deg_c | °C | Maximum | Double | 10 minute tag
WTRF.AirOutTmp_10m_Min | #N/A | WTRF. | AirOutTmp_10m_Min | Transformer air Outlet Temp (min) | Transformatorluft Austrittstemperatur (min) | Temperatura de la salida de aire del transformador (min) | Temp wylotu powietrza transformatora (min) | Outlet temperature of high voltage transformer | deg_c | °C | Minimum | Double | 10 minute tag
WTRF.AuxTmp | #N/A | WTRF. | AuxTmp | Auxiliary Transformer Temp | Temperatur des Hilfstransformators | Temperatura del transformador auxiliar | Pomocniczy transformator Temp | Temperature of AUX transformer | deg_c | °C | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WTRF.AuxTmp_10m_Avg | #N/A | WTRF. | AuxTmp_10m_Avg | Auxiliary Transformer Temp (avg) | Temperatur des Hilfstransformators (avg) | Temperatura del transformador auxiliar (avg) | Pomocniczy transformator Temp (avg) | Temperature of AUX transformer | deg_c | °C | Average | Double | 10 minute tag
WTRF.ClSt | WTRF.ClSt | WTRF. | ClSt | Transformer cooling system status | Status des Kühlsystems des Transformators | Estado del sistema de refrigeración del transformador | Stan układu chłodzenia transformatora | Status of transformer cooling system | Enum | Enum | Live Value | Long | Live Value
WTRF.CoreTmp1 | #N/A | WTRF. | CoreTmp1 | Transformer L1 Core Temp | Transformator L1 Kerntemperatur | Temperatura del núcleo del transformador L1 | Transformator L1 Rdzeń Temp | Transformer temperature core, phase 1 | deg_c | °C | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WTRF.CoreTmp1_10m_Avg | #N/A | WTRF. | CoreTmp1_10m_Avg | Transformer L1 Core Temp (avg) | Transformator L1 Kerntemperatur (avg) | Temperatura del núcleo del transformador L1 (avg) | Transformator L1 Rdzeń Temp (avg) | Transformer temperature core, phase 1 | deg_c | °C | Average | Double | 10 minute tag
WTRF.CoreTmp1_10m_Max | #N/A | WTRF. | CoreTmp1_10m_Max | Transformer L1 Core Temp (max) | Transformator L1 Kerntemperatur (max) | Temperatura del núcleo del transformador L1 (max) | Transformator L1 Rdzeń Temp (max) | Transformer temperature core, phase 1 | deg_c | °C | Maximum | Double | 10 minute tag
WTRF.CoreTmp1_10m_Min | #N/A | WTRF. | CoreTmp1_10m_Min | Transformer L1 Core Temp (min) | Transformator L1 Kerntemperatur (min) | Temperatura del núcleo del transformador L1 (min) | Transformator L1 Rdzeń Temp (min) | Transformer temperature core, phase 1 | deg_c | °C | Minimum | Double | 10 minute tag
WTRF.CoreTmp1_10m_Std | #N/A | WTRF. | CoreTmp1_10m_Std | Transformer L1 Core Temp (std) | Transformator L1 Kerntemperatur (std) | Temperatura del núcleo del transformador L1 (std) | Transformator L1 Rdzeń Temp (std) | Transformer temperature core, phase 1 | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRF.CoreTmp2 | #N/A | WTRF. | CoreTmp2 | Transformer L2 Core Temp | Transformator L2 Kerntemperatur | Temperatura del núcleo del transformador L2 | Transformator L2 Rdzeń Temp | Transformer temperature core, phase 2 | deg_c | °C | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WTRF.CoreTmp2_10m_Avg | #N/A | WTRF. | CoreTmp2_10m_Avg | Transformer L2 Core Temp (avg) | Transformator L2 Kerntemperatur (avg) | Temperatura del núcleo del transformador L2 (avg) | Transformator L2 Rdzeń Temp (avg) | Transformer temperature core, phase 2 | deg_c | °C | Average | Double | 10 minute tag
WTRF.CoreTmp3 | #N/A | WTRF. | CoreTmp3 | Transformer L3 Core Temp | Transformator L3 Kerntemperatur | Temperatura del núcleo del transformador L3 | Transformator L3 Rdzeń Temp | Transformer temperature core, phase 3 | deg_c | °C | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WTRF.CoreTmp3_10m_Avg | #N/A | WTRF. | CoreTmp3_10m_Avg | Transformer L3 Core Temp (avg) | Transformator L3 Kerntemperatur (avg) | Temperatura del núcleo del transformador L3 (avg) | Transformator L3 Rdzeń Temp (avg) | Transformer temperature core, phase 3 | deg_c | °C | Average | Double | 10 minute tag
WTRF.FanCnt_10m_End | #N/A | WTRF. | FanCnt_10m_End | Number of activations of transformer fan (end) | Anzahl der Aktivierungen des Transformatorlüfters (end) | Número de activaciones del ventilador del transformador (end) | Liczba aktywacji wentylatora transformatora (end) | Number of activations of transformer fan | count | Count | Endvalue | Long | 10 minute tag
WTRF.FanHSpdSt | #N/A | WTRF. | FanHSpdSt | Transformer fan High Speed | Transformatorlüfter Hochgeschwindigkeit | Velocidad alta del ventilador del transformador | Wentylator transformatora Wys. Prędk. | Feedback Fan Transformer room High Speed | Enum | Enum | Live Value | Long | Live Value
WTRF.FanLSpdSt | #N/A | WTRF. | FanLSpdSt | Transformer fanLow Speed | Transformatorlüfter niedrige Geschwindigkeit | Velocidad baja del ventilador del transformador | Wentylator transformatora Niska prędk. | Feedback Fan Transformer room Low Speed | Enum | Enum | Live Value | Long | Live Value
WTRF.FanTms_10m_End | #N/A | WTRF. | FanTms_10m_End | Time transformer fan has been activated (end) | Zeit, in der der Transformatorlüfter aktiviert wurde (end) | Tiempo que el ventilador del transformador ha estado activado (end) | Czas aktywacji wentylatora transformatora (end) | Time transformer fan has been activated | s | seconds | Endvalue | Long | 10 minute tag
WTRF.GriA | WTRF.GriA | WTRF. | GriA | Transformer Grid Side Current | Transformator netzseitiger Strom | Corriente en el lado de la red eléctrica del transformador | Prąd sieci strona transformatora | Grid side 3 phase current | A | A | Live Value | Double | Live Value
WTRF.GriPNV | WTRF.GriPNV | WTRF. | GriPNV | Transformer P-N Voltage Grid side | Transformator P-N Spannung Netzseite | Tensión P-N del transformador en el lado de la red eléctrica | Transformator P-P Nap. strona sieci | Grid side 3 phase-to-neutral voltage | V | V | Live Value | Double | Live Value
WTRF.GriPPV | WTRF.GriPPV | WTRF. | GriPPV | Transformer P-P Voltage Grid side | Transformator P-P Spannung Netzseite | Tensión P-P del transformador en el lado de la red eléctrica | Transformator P-N Nap. strona sieci | Grid side 3 phase phase-to-phase voltage | V | V | Live Value | Double | Live Value
WTRF.GriSwOp | WTRF.GriSwOp | WTRF. | GriSwOp | Main grid switch command | Hauptnetzschaltbefehl | Comando de conmutación de la red eléctrica principal | Polecenie głów. przełącznika sieci | Main grid switch command | Enum | Enum | Live Value | Long
WTRF.GriTmp | WTRF.GriTmp | WTRF. | GriTmp | Transformer Grid Side Temp | Transformator Netzseitige Temperatur | Temperatura en el lado de la red eléctrica del transformador | Transformator Temp. po stronie sieci | Transformer temperature on grid side | deg_c | °C | Live Value | Double | Live Value
WTRF.GriTmp_10m_Avg | #N/A | WTRF. | GriTmp_10m_Avg | Transformer Grid Side Temp (avg) | Transformator Netzseitige Temperatur (avg) | Temperatura en el lado de la red eléctrica del transformador (avg) | Transformator Temp. po stronie sieci (avg) | Transformer temperature on grid side | deg_c | °C | Average | Double | 10 minute tag
WTRF.GriTmp_10m_Max | #N/A | WTRF. | GriTmp_10m_Max | Transformer Grid Side Temp (max) | Transformator Netzseitige Temperatur (max) | Temperatura en el lado de la red eléctrica del transformador (max) | Transformator Temp. po stronie sieci (max) | Transformer temperature on grid side | deg_c | °C | Maximum | Double | 10 minute tag
WTRF.GriTmp_10m_Min | #N/A | WTRF. | GriTmp_10m_Min | Transformer Grid Side Temp (min) | Transformator Netzseitige Temperatur (min) | Temperatura en el lado de la red eléctrica del transformador (min) | Transformator Temp. po stronie sieci (min) | Transformer temperature on grid side | deg_c | °C | Minimum | Double | 10 minute tag
WTRF.GriTmp_10m_Std | #N/A | WTRF. | GriTmp_10m_Std | Transformer Grid Side Temp (std) | Transformator Netzseitige Temperatur (std) | Temperatura en el lado de la red eléctrica del transformador (std) | Transformator Temp. po stronie sieci (std) | Transformer temperature on grid side | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRF.IntnRoomTmp | #N/A | WTRF. | IntnRoomTmp | Transformer Internal Room Temp | Transformator Innenraumtemperatur | Temperatura de la sala interna del transformador | Transformator wewn.Temp pom. | Transformer internal room temperature | deg_c | °C | Live Value | Double | Live Value
WTRF.IntnRoomTmp_10m_Avg | #N/A | WTRF. | IntnRoomTmp_10m_Avg | Transformer Internal Room Temp (avg) | Transformator Innenraumtemperatur (avg) | Temperatura de la sala interna del transformador (avg) | Transformator wewn.Temp pom. (avg) | Transformer internal room temperature | deg_c | °C | Average | Double | 10 minute tag
WTRF.IntnRoomTmp_10m_Max | #N/A | WTRF. | IntnRoomTmp_10m_Max | Transformer Internal Room Temp (max) | Transformator Innenraumtemperatur (max) | Temperatura de la sala interna del transformador (max) | Transformator wewn.Temp pom. (max) | Transformer internal room temperature | deg_c | °C | Maximum | Double | 10 minute tag
WTRF.IntnRoomTmp_10m_Min | #N/A | WTRF. | IntnRoomTmp_10m_Min | Transformer Internal Room Temp (min) | Transformator Innenraumtemperatur (min) | Temperatura de la sala interna del transformador (min) | Transformator wewn.Temp pom. (min) | Transformer internal room temperature | deg_c | °C | Minimum | Double | 10 minute tag
WTRF.IntnRoomTmp_10m_Std | #N/A | WTRF. | IntnRoomTmp_10m_Std | Transformer Internal Room Temp (std) | Transformator Innenraumtemperatur (std) | Temperatura de la sala interna del transformador (std) | Transformator wewn.Temp pom. (std) | Transformer internal room temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRF.IntnTmp | #N/A | WTRF. | IntnTmp | Transformer Internal Temp | Transformator Innentemperatur | Temperatura interna del transformador | Transformator wewn. Temp | Transformer internal temperature | deg_c | °C | Live Value | Double | Live Value
WTRF.IntnTmp_10m_Avg | #N/A | WTRF. | IntnTmp_10m_Avg | Transformer Internal Temp (avg) | Transformator Innentemperatur (avg) | Temperatura interna del transformador (avg) | Transformator wewn. Temp (avg) | Transformer internal temperature | deg_c | °C | Average | Double | 10 minute tag
WTRF.IntnTmp_10m_Max | #N/A | WTRF. | IntnTmp_10m_Max | Transformer Internal Temp (max) | Transformator Innentemperatur (max) | Temperatura interna del transformador (max) | Transformator wewn. Temp (max) | Transformer internal temperature | deg_c | °C | Maximum | Double | 10 minute tag
WTRF.IntnTmp_10m_Min | #N/A | WTRF. | IntnTmp_10m_Min | Transformer Internal Temp (min) | Transformator Innentemperatur (min) | Temperatura interna del transformador (min) | Transformator wewn. Temp (min) | Transformer internal temperature | deg_c | °C | Minimum | Double | 10 minute tag
WTRF.IntnTmp_10m_Std | #N/A | WTRF. | IntnTmp_10m_Std | Transformer Internal Temp (std) | Transformator Innentemperatur (std) | Temperatura interna del transformador (std) | Transformator wewn. Temp (std) | Transformer internal temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRF.IntnTmp1 | #N/A | WTRF. | IntnTmp1 | Transformer Internal Temp1 | Transformator Innentemperatur 1 | Temperatura 1 interna del transformador | Transformator wewn. Temp1 | Transformer internal temperature1 | deg_c | °C | Live Value | Double | Live Value
WTRF.IntnTmp1_10m_Avg | #N/A | WTRF. | IntnTmp1_10m_Avg | Transformer Internal Temp1 (avg) | Transformator Innentemperatur 1 (avg) | Temperatura 1 interna del transformador (avg) | Transformator wewn. Temp1 (avg) | Transformer internal temperature1 | deg_c | °C | Average | Double | 10 minute tag
WTRF.IntnTmp2 | #N/A | WTRF. | IntnTmp2 | Transformer Internal Temp2 | Transformator Innentemperatur 2 | Temperatura 2 interna del transformador | Transformator wewn. Temp2 | Transformer internal temperature2 | deg_c | °C | Live Value | Double | Live Value
WTRF.IntnTmp2_10m_Avg | #N/A | WTRF. | IntnTmp2_10m_Avg | Transformer Internal Temp2 (avg) | Transformator Innentemperatur 2 (avg) | Temperatura 2 interna del transformador (avg) | Transformator wewn. Temp2 (avg) | Transformer internal temperature2 | deg_c | °C | Average | Double | 10 minute tag
WTRF.IntnTmp3 | #N/A | WTRF. | IntnTmp3 | Transformer Internal Temp3 | Transformator Innentemperatur 3 | Temperatura 3 interna del transformador | Transformator wewn. Temp3 | Transformer internal temperature3 | deg_c | °C | Live Value | Double | Live Value
WTRF.IntnTmp3_10m_Avg | #N/A | WTRF. | IntnTmp3_10m_Avg | Transformer Internal Temp3 (avg) | Transformator Innentemperatur 3 (avg) | Temperatura 3 interna del transformador (avg) | Transformator wewn. Temp3 (avg) | Transformer internal temperature3 | deg_c | °C | Average | Double | 10 minute tag
WTRF.IntnTmp4 | #N/A | WTRF. | IntnTmp4 | Transformer Internal Temp4 | Transformator Innentemperatur 4 | Temperatura 4 interna del transformador | Transformator wewn. Temp4 | Transformer internal temperature4 | deg_c | °C | Live Value | Double | Live Value
WTRF.IntnTmp4_10m_Avg | #N/A | WTRF. | IntnTmp4_10m_Avg | Transformer Internal Temp4 (avg) | Transformator Innentemperatur 4 (avg) | Temperatura 4 interna del transformador (avg) | Transformator wewn. Temp4 (avg) | Transformer internal temperature4 | deg_c | °C | Average | Double | 10 minute tag
WTRF.OilLevSt | WTRF.OilLevSt | WTRF. | OilLevSt | Transforme Oil Level Status | Transformator-Ölstand Status | Estado del nivel del aceite del transformador | Stan poziomu oleju Transforme | Oil level status information for oil filled transformers | Enum | Enum | Live Value | Long | Live Value
WTRF.OilTmp | #N/A | WTRF. | OilTmp | Transformer Oil Temp | Transformator-Öltemperatur | Temperatura del aceite del transformador | Temp oleju transformatorowego | Transformer oil temperature | deg_c | °C | Live Value | Double | Live Value
WTRF.OilTmp_10m_Avg | #N/A | WTRF. | OilTmp_10m_Avg | Transformer Oil Temp (avg) | Transformator-Öltemperatur (avg) | Temperatura del aceite del transformador (avg) | Temp oleju transformatorowego (avg) | Transformer oil temperature | deg_c | °C | Average | Double | 10 minute tag
WTRF.OilTmp_10m_Max | #N/A | WTRF. | OilTmp_10m_Max | Transformer Oil Temp (max) | Transformator-Öltemperatur (max) | Temperatura del aceite del transformador (max) | Temp oleju transformatorowego (max) | Transformer oil temperature | deg_c | °C | Maximum | Double | 10 minute tag
WTRF.OilTmp_10m_Min | #N/A | WTRF. | OilTmp_10m_Min | Transformer Oil Temp (min) | Transformator-Öltemperatur (min) | Temperatura del aceite del transformador (min) | Temp oleju transformatorowego (min) | Transformer oil temperature | deg_c | °C | Minimum | Double | 10 minute tag
WTRF.OilTmp_10m_Std | #N/A | WTRF. | OilTmp_10m_Std | Transformer Oil Temp (std) | Transformator-Öltemperatur (std) | Temperatura del aceite del transformador (std) | Temp oleju transformatorowego (std) | Transformer oil temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRF.OpTmsRs | WTRF.OpTmsRs | WTRF. | OpTmsRs | Transformer operation time | Betriebszeit des Transformators | Tiempo de funcionamiento del transformador | Czas pracy transformatora | Transformer operation time in seconds (vendor specific) | s | seconds | Total Counter | Long | Live Value
WTRF.PnlTmp | #N/A | WTRF. | PnlTmp | Transformer Panel Temp | Transformator-Panel-Temperatur | Temperatura del panel del transformador | Temp panelu transformatora | Transformer Panel/Controllerbox temperature | deg_c | °C | Live Value | Double | Live Value
WTRF.PnlTmp_10m_Avg | #N/A | WTRF. | PnlTmp_10m_Avg | Transformer Panel Temp (avg) | Transformator-Panel-Temperatur (avg) | Temperatura del panel del transformador (avg) | Temp panelu transformatora (avg) | Transformer Panel/Controllerbox temperature | deg_c | °C | Average | Double | 10 minute tag
WTRF.PnlTmp_10m_Max | #N/A | WTRF. | PnlTmp_10m_Max | Transformer Panel Temp (max) | Transformator-Panel-Temperatur (max) | Temperatura del panel del transformador (max) | Temp panelu transformatora (max) | Transformer Panel/Controllerbox temperature | deg_c | °C | Maximum | Double | 10 minute tag
WTRF.PnlTmp_10m_Min | #N/A | WTRF. | PnlTmp_10m_Min | Transformer Panel Temp (min) | Transformator-Panel-Temperatur (min) | Temperatura del panel del transformador (min) | Temp panelu transformatora (min) | Transformer Panel/Controllerbox temperature | deg_c | °C | Minimum | Double | 10 minute tag
WTRF.PnlTmp_10m_Std | #N/A | WTRF. | PnlTmp_10m_Std | Transformer Panel Temp (std) | Transformator-Panel-Temperatur (std) | Temperatura del panel del transformador (std) | Temp panelu transformatora (std) | Transformer Panel/Controllerbox temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRF.TnkPresSt | WTRF.TnkPresSt | WTRF. | TnkPresSt | Transformer Gas Pressure Status | Status des Trafogasdrucks | Estado de presión del gas del transformador | Stan ciśnienia gazu transformatora | Gas pressure status of main tank for oil filled transformers | Enum | Enum | Live Value | Long | Live Value
WTRF.TurA | WTRF.TurA | WTRF. | TurA | Transformer Turbine Side Current | Transformator Turbinenseitiger Strom | Corriente en el lado de la turbina del transformador | Prąd boczny turbiny transformatora | Turbine side 3 phase current | A | A | Live Value | Double | Live Value
WTRF.TurPNV | WTRF.TurPNV | WTRF. | TurPNV | Transformer P-N Voltage Turbine side | Transformator P-N Spannung Turbinenseite | Tensión P-N del transformador en el lado de la turbina | Transformator P-N Napięcie po stronie turbiny | Turbine side 3 phase-to-neutral voltage | V | V | Live Value | Double | Live Value
WTRF.TurPPV | WTRF.TurPPV | WTRF. | TurPPV | Transformer P-P Voltage Turbine side | Transformator P-P Spannung Turbinenseite | Tensión P-P del transformador en el lado de la turbina | Transformator P-P Napięcie po stronie turbiny | Turbine side 3 phase phase-to-phase voltage | V | V | Live Value | Double | Live Value
WTRF.TurTmp | WTRF.TurTmp | WTRF. | TurTmp | Transformer Turbine side Temp | Transformator Turbinenseite Temperatur | Temperatura en el lado de la turbina del transformador | Transformator Temp po stronie turbiny | Transformer temperature on turbine side | deg_c | °C | Live Value | Double | Live Value
WTRF.TurTmp_10m_Avg | #N/A | WTRF. | TurTmp_10m_Avg | Transformer Turbine side Temp (avg) | Transformator Turbinenseite Temperatur (avg) | Temperatura en el lado de la turbina del transformador (avg) | Transformator Temp po stronie turbiny (avg) | Transformer temperature on turbine side | deg_c | °C | Average | Double | 10 minute tag
WTRF.TurTmp_10m_Max | #N/A | WTRF. | TurTmp_10m_Max | Transformer Turbine side Temp (max) | Transformator Turbinenseite Temperatur (max) | Temperatura en el lado de la turbina del transformador (max) | Transformator Temp po stronie turbiny (max) | Transformer temperature on turbine side | deg_c | °C | Maximum | Double | 10 minute tag
WTRF.TurTmp_10m_Min | #N/A | WTRF. | TurTmp_10m_Min | Transformer Turbine side Temp (min) | Transformator Turbinenseite Temperatur (min) | Temperatura en el lado de la turbina del transformador (min) | Transformator Temp po stronie turbiny (min) | Transformer temperature on turbine side | deg_c | °C | Minimum | Double | 10 minute tag
WTRF.TurTmp_10m_Std | #N/A | WTRF. | TurTmp_10m_Std | Transformer Turbine side Temp (std) | Transformator Turbinenseite Temperatur (std) | Temperatura en el lado de la turbina del transformador (std) | Transformator Temp po stronie turbiny (std) | Transformer temperature on turbine side | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRF.TurTmp1 | #N/A | WTRF. | TurTmp1 | Transformer Turbine Side L1 Temp | Transformator Turbinenseite L1 Temperatur | Temperatura L1 en el lado de la turbina del transformador | Transformator strona turbiny L1 Temp | Transformer temperature on turbine side phase L1 | deg_c | °C | Live Value | Double | Live Value | Used in some specialised presentations
WTRF.TurTmp1_10m_Avg | #N/A | WTRF. | TurTmp1_10m_Avg | Transformer Turbine Side L1 Temp (avg) | Transformator Turbinenseite L1 Temperatur (avg) | Temperatura L1 en el lado de la turbina del transformador (avg) | Transformator strona turbiny L1 Temp (avg) | Transformer temperature on turbine side phase L1 | deg_c | °C | Average | Double | 10 minute tag | Common tags for analysis
WTRF.TurTmp1_10m_Max | #N/A | WTRF. | TurTmp1_10m_Max | Transformer Turbine Side L1 Temp (max) | Transformator Turbinenseite L1 Temperatur (max) | Temperatura L1 en el lado de la turbina del transformador (max) | Transformator strona turbiny L1 Temp (max) | Transformer temperature on turbine side phase L1 | deg_c | °C | Maximum | Double | 10 minute tag | Common tags for analysis
WTRF.TurTmp1_10m_Min | #N/A | WTRF. | TurTmp1_10m_Min | Transformer Turbine Side L1 Temp (min) | Transformator Turbinenseite L1 Temperatur (min) | Temperatura L1 en el lado de la turbina del transformador (min) | Transformator strona turbiny L1 Temp (min) | Transformer temperature on turbine side phase L1 | deg_c | °C | Minimum | Double | 10 minute tag | Common tags for analysis
WTRF.TurTmp1_10m_Std | #N/A | WTRF. | TurTmp1_10m_Std | Transformer Turbine Side L1 Temp (std) | Transformator Turbinenseite L1 Temperatur (std) | Temperatura L1 en el lado de la turbina del transformador (std) | Transformator strona turbiny L1 Temp (std) | Transformer temperature on turbine side phase L1 | deg_c | °C | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WTRF.TurTmp2 | #N/A | WTRF. | TurTmp2 | Transformer Turbine Side L2 Temp | Transformator Turbinenseite L2 Temperatur | Temperatura L2 en el lado de la turbina del transformador | Transformator strona turbiny L2 Temp | Transformer temperature on turbine side phase L2 | deg_c | °C | Live Value | Double | Live Value | Used in some specialised presentations
WTRF.TurTmp2_10m_Avg | #N/A | WTRF. | TurTmp2_10m_Avg | Transformer Turbine Side L2 Temp (avg) | Transformator Turbinenseite L2 Temperatur (avg) | Temperatura L2 en el lado de la turbina del transformador (avg) | Transformator strona turbiny L2 Temp (avg) | Transformer temperature on turbine side phase L2 | deg_c | °C | Average | Double | 10 minute tag | Common tags for analysis
WTRF.TurTmp2_10m_Max | #N/A | WTRF. | TurTmp2_10m_Max | Transformer Turbine Side L2 Temp (max) | Transformator Turbinenseite L2 Temperatur (max) | Temperatura L2 en el lado de la turbina del transformador (max) | Transformator strona turbiny L2 Temp (max) | Transformer temperature on turbine side phase L2 | deg_c | °C | Maximum | Double | 10 minute tag | Common tags for analysis
WTRF.TurTmp2_10m_Min | #N/A | WTRF. | TurTmp2_10m_Min | Transformer Turbine Side L2 Temp (min) | Transformator Turbinenseite L2 Temperatur (min) | Temperatura L2 en el lado de la turbina del transformador (min) | Transformator strona turbiny L2 Temp (min) | Transformer temperature on turbine side phase L2 | deg_c | °C | Minimum | Double | 10 minute tag | Common tags for analysis
WTRF.TurTmp2_10m_Std | #N/A | WTRF. | TurTmp2_10m_Std | Transformer Turbine Side L2 Temp (std) | Transformator Turbinenseite L2 Temperatur (std) | Temperatura L2 en el lado de la turbina del transformador (std) | Transformator strona turbiny L2 Temp (std) | Transformer temperature on turbine side phase L2 | deg_c | °C | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WTRF.TurTmp3 | #N/A | WTRF. | TurTmp3 | Transformer Turbine Side L3 Temp | Transformator Turbinenseite L3 Temperatur | Temperatura L3 en el lado de la turbina del transformador | Transformator strona turbiny L3 Temp | Transformer temperature on turbine side phase L3 | deg_c | °C | Live Value | Double | Live Value | Used in some specialised presentations
WTRF.TurTmp3_10m_Avg | #N/A | WTRF. | TurTmp3_10m_Avg | Transformer Turbine Side L3 Temp (avg) | Transformator Turbinenseite L3 Temperatur (avg) | Temperatura L3 en el lado de la turbina del transformador (avg) | Transformator strona turbiny L3 Temp (avg) | Transformer temperature on turbine side phase L3 | deg_c | °C | Average | Double | 10 minute tag | Common tags for analysis
WTRF.TurTmp3_10m_Max | #N/A | WTRF. | TurTmp3_10m_Max | Transformer Turbine Side L3 Temp (max) | Transformator Turbinenseite L3 Temperatur (max) | Temperatura L3 en el lado de la turbina del transformador (max) | Transformator strona turbiny L3 Temp (max) | Transformer temperature on turbine side phase L3 | deg_c | °C | Maximum | Double | 10 minute tag | Common tags for analysis
WTRF.TurTmp3_10m_Min | #N/A | WTRF. | TurTmp3_10m_Min | Transformer Turbine Side L3 Temp (min) | Transformator Turbinenseite L3 Temperatur (min) | Temperatura L3 en el lado de la turbina del transformador (min) | Transformator strona turbiny L3 Temp (min) | Transformer temperature on turbine side phase L3 | deg_c | °C | Minimum | Double | 10 minute tag | Common tags for analysis
WTRF.TurTmp3_10m_Std | #N/A | WTRF. | TurTmp3_10m_Std | Transformer Turbine Side L3 Temp (std) | Transformator Turbinenseite L3 Temperatur (std) | Temperatura L3 en el lado de la turbina del transformador (std) | Transformator strona turbiny L3 Temp (std) | Transformer temperature on turbine side phase L3 | deg_c | °C | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WTRM.BrkAccuPres | #N/A | WTRM. | BrkAccuPres | Hydraulic pressure for brake accumulator | Hydraulischer Druck für Bremsspeicher | Presión hidráulica para el acumulador de los frenos | Ciśnienie hydrauliczne dla akum. hamulc. | Hydraulic pressure for brake accumulator | bar | bar | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WTRM.BrkAccuPres_10m_Avg | #N/A | WTRM. | BrkAccuPres_10m_Avg | Hydraulic pressure for brake accumulator (avg) | Hydraulischer Druck für Bremsspeicher (avg) | Presión hidráulica para el acumulador de los frenos (avg) | Ciśnienie hydrauliczne dla akum. hamulc. (avg) | Hydraulic pressure for brake accumulator | bar | bar | Average | Double | 10 minute tag
WTRM.BrkAccuPres_10m_Max | #N/A | WTRM. | BrkAccuPres_10m_Max | Hydraulic pressure for brake accumulator (max) | Hydraulischer Druck für Bremsspeicher (max) | Presión hidráulica para el acumulador de los frenos (max) | Ciśnienie hydrauliczne dla akum. hamulc. (max) | Hydraulic pressure for brake accumulator | bar | bar | Maximum | Double | 10 minute tag
WTRM.BrkAccuPres_10m_Min | #N/A | WTRM. | BrkAccuPres_10m_Min | Hydraulic pressure for brake accumulator (min) | Hydraulischer Druck für Bremsspeicher (min) | Presión hidráulica para el acumulador de los frenos (min) | Ciśnienie hydrauliczne dla akum. hamulc. (min) | Hydraulic pressure for brake accumulator | bar | bar | Minimum | Double | 10 minute tag
WTRM.BrkAccuPres_10m_Std | #N/A | WTRM. | BrkAccuPres_10m_Std | Hydraulic pressure for brake accumulator (std) | Hydraulischer Druck für Bremsspeicher (std) | Presión hidráulica para el acumulador de los frenos (std) | Ciśnienie hydrauliczne dla akum. hamulc. (std) | Hydraulic pressure for brake accumulator | bar | bar | Standard Deviation | Double | 10 minute tag
WTRM.BrkCnt | #N/A | WTRM. | BrkCnt | Number of activations of the shaft brake | Anzahl der Betätigungen der Wellenbremse | Número de activaciones del freno del eje | Liczba aktywacji hamulca wału | Number of activations of the shaft brake | count | Count | Total Counter | Long | Live Value
WTRM.BrkCnt_10m_End | #N/A | WTRM. | BrkCnt_10m_End | Number of activations of the shaft brake (end) | Anzahl der Betätigungen der Wellenbremse (end) | Número de activaciones del freno del eje (end) | Liczba aktywacji hamulca wału (end) | Number of activations of the shaft brake | count | Count | Endvalue | Long | 10 minute tag
WTRM.BrkHyPres | WTRM.BrkHyPres | WTRM. | BrkHyPres | Hydraulic Oil Shaft Brake Pressure | Hydrauliköl Wellenbremsdruck | Presión del freno del eje de aceite hidráulico | Ciśnienie hamowania wału oleju hydr. | Hydraulic oil pressure shaft brake | bar | bar | Live Value | Double | Live Value
WTRM.BrkHyPres_10m_Avg | #N/A | WTRM. | BrkHyPres_10m_Avg | Hydraulic Oil Shaft Brake Pressure (avg) | Hydrauliköl Wellenbremsdruck (avg) | Presión del freno del eje de aceite hidráulico (avg) | Ciśnienie hamowania wału oleju hydr. (avg) | Hydraulic oil pressure shaft brake | bar | bar | Average | Double | 10 minute tag
WTRM.BrkHyPres_10m_Max | #N/A | WTRM. | BrkHyPres_10m_Max | Hydraulic Oil Shaft Brake Pressure (max) | Hydrauliköl Wellenbremsdruck (max) | Presión del freno del eje de aceite hidráulico (max) | Ciśnienie hamowania wału oleju hydr. (max) | Hydraulic oil pressure shaft brake | bar | bar | Maximum | Double | 10 minute tag
WTRM.BrkHyPres_10m_Min | #N/A | WTRM. | BrkHyPres_10m_Min | Hydraulic Oil Shaft Brake Pressure (min) | Hydrauliköl Wellenbremsdruck (min) | Presión del freno del eje de aceite hidráulico (min) | Ciśnienie hamowania wału oleju hydr. (min) | Hydraulic oil pressure shaft brake | bar | bar | Minimum | Double | 10 minute tag
WTRM.BrkHyPres_10m_Std | #N/A | WTRM. | BrkHyPres_10m_Std | Hydraulic Oil Shaft Brake Pressure (std) | Hydrauliköl Wellenbremsdruck (std) | Presión del freno del eje de aceite hidráulico (std) | Ciśnienie hamowania wału oleju hydr. (std) | Hydraulic oil pressure shaft brake | bar | bar | Standard Deviation | Double | 10 minute tag
WTRM.BrkOpSt | WTRM.BrkOpSt | WTRM. | BrkOpSt | Shaft Brake Status | Status der Wellenbremse | Estado del freno del eje | Stan hamulca wału | Status of shaft brake | Enum | Enum | Live Value | Long | Live Value
WTRM.BrkOpStManuStr | #N/A | WTRM. | BrkOpStManuStr | Brake State | Status der Bremse | Estado del freno | Stan hamulca | Brake state | Enum | Enum | Live Value | String | Live Value
WTRM.BrkPmpSt | #N/A | WTRM. | BrkPmpSt | Hydraulic pump for disc brake | Hydraulikpumpe für Scheibenbremse | Bomba hidráulica para el freno de disco | Pompa hydrauliczna dla hamulca tarczy | Feedback Hydraulic pump for brake | Enum | Enum | Live Value | Long | Live Value
WTRM.BrkSt | #N/A | WTRM. | BrkSt | Disc Brake Status | Status der Scheibenbremse | Estado del freno de disco | Stan hamulca tarczy | Feedback Brake | Enum | Enum | Live Value | Long | Live Value
WTRM.BrkThmSt | #N/A | WTRM. | BrkThmSt | Thermistors Brake system | Thermistoren Bremssystem | Sistema de freno de los termistores | Thermistory Układ hamulcowy | Thermistors Brake system | Enum | Enum | Live Value | Long | Live Value
WTRM.BrkTms | #N/A | WTRM. | BrkTms | Time the shaft brake has been activated | Zeit, in der die Wellenbremse aktiviert wurde | Tiempo que el freno del eje ha estado activado | Czas aktywacji hamulca wału | Time the shaft brake has been activated | s | seconds | Total Counter | Long | Live Value
WTRM.BrkTms_10m_End | #N/A | WTRM. | BrkTms_10m_End | Time the shaft brake has been activated (end) | Zeit, in der die Wellenbremse aktiviert wurde (end) | Tiempo que el freno del eje ha estado activado (end) | Czas aktywacji hamulca wału (end) | Time the shaft brake has been activated | s | seconds | Endvalue | Long | 10 minute tag
WTRM.ClSt | WTRM.ClSt | WTRM. | ClSt | Transmission cooling system Status | Status des Getriebekühlsystem | Estado del sistema de refrigeración de transmisión | Stan układu chłodzenia przekładni | Status of transmission cooling system | Enum | Enum | Live Value | Long | Live Value
WTRM.ClWtrFanOp | #N/A | WTRM. | ClWtrFanOp | Start fans Gearbox Cooling water | Start Lüfter Getriebekühlwasser | Iniciar ventiladores del agua de refrigeración de la caja de cambios | Start went. przekładnia Woda chłodząca | Start fans gear (Cooling water) | Enum | Enum | Live Value | Long | Live Value
WTRM.ClWtrFanSpd | #N/A | WTRM. | ClWtrFanSpd | Speed fans Gearbox Cooling water | Drehzahl Lüfter des Getriebekühlwassers | Velocidad del agua de refrigeración de la caja de cambios de los ventiladores | Wentylatory prędkości przekładnia Woda chłodząca | Speed fans gear (Cooling water) | rpm | RPM | Live Value | Double | Live Value
WTRM.ClWtrFanSt1 | #N/A | WTRM. | ClWtrFanSt1 | Running fan 1 Gearbox Cooling water | Laufender Lüfter 1 Getriebekühlwasser | Ventilador 1 en funcionamiento Agua de refrigeración de la caja de cambios | Wentylator 1 przekładnia Woda chłodząca | Running fan 1 gear (Cooling water) | Enum | Enum | Live Value | Long | Live Value
WTRM.ClWtrFanSt2 | #N/A | WTRM. | ClWtrFanSt2 | Running fan 2 Gearbox Cooling water | Laufender Lüfter 2 Getriebekühlwasser | Ventilador 2 en funcionamiento Agua de refrigeración de la caja de cambios | Wentylator biegowy 2 przekładnia Woda chłodząca | Running fan 2 gear (Cooling water) | Enum | Enum | Live Value | Long | Live Value
WTRM.ClWtrLevSt | #N/A | WTRM. | ClWtrLevSt | Gearbox cooling water level | Getriebekühlwasserstand | Nivel de agua de refrigeración de la caja de cambios | Poziom wody chłodzącej przekładni | Level Gear cooling water | Enum | Enum | Live Value | Long | Live Value
WTRM.ClWtrPmpPres | #N/A | WTRM. | ClWtrPmpPres | Gear cooling water pump pressure | Druck der Getriebekühlwasserpumpe | Presión de la bomba de agua de refrigeración del engranaje | Ciśnienie pompy wody chłodzącej przekładnię | Gear cooling water pump pressure | bar | bar | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WTRM.ClWtrPmpPres_10m_Avg | #N/A | WTRM. | ClWtrPmpPres_10m_Avg | Gear cooling water pump pressure (avg) | Druck der Getriebekühlwasserpumpe (avg) | Presión de la bomba de agua de refrigeración del engranaje (avg) | Ciśnienie pompy wody chłodzącej przekładnię (avg) | Gear cooling water pump pressure | bar | bar | Average | Double | 10 minute tag
WTRM.ClWtrPmpPres_10m_Max | #N/A | WTRM. | ClWtrPmpPres_10m_Max | Gear cooling water pump pressure (max) | Druck der Getriebekühlwasserpumpe (max) | Presión de la bomba de agua de refrigeración del engranaje (max) | Ciśnienie pompy wody chłodzącej przekładnię (max) | Gear cooling water pump pressure | bar | bar | Maximum | Double | 10 minute tag
WTRM.ClWtrPmpPres_10m_Min | #N/A | WTRM. | ClWtrPmpPres_10m_Min | Gear cooling water pump pressure (min) | Druck der Getriebekühlwasserpumpe (min) | Presión de la bomba de agua de refrigeración del engranaje (min) | Ciśnienie pompy wody chłodzącej przekładnię (min) | Gear cooling water pump pressure | bar | bar | Minimum | Double | 10 minute tag
WTRM.ClWtrPmpPres_10m_Std | #N/A | WTRM. | ClWtrPmpPres_10m_Std | Gear cooling water pump pressure (std) | Druck der Getriebekühlwasserpumpe (std) | Presión de la bomba de agua de refrigeración del engranaje (std) | Ciśnienie pompy wody chłodzącej przekładnię (std) | Gear cooling water pump pressure | bar | bar | Standard Deviation | Double | 10 minute tag
WTRM.ClWtrPmpSt | #N/A | WTRM. | ClWtrPmpSt | Waterpump Oil Circuit | Ölkreislauf der Wasserpumpe | Circuito de aceite de la bomba de agua | Obwód oleju z pompą wodną | Feedback Waterpump Oil Circuit | Enum | Enum | Live Value | Long | Live Value
WTRM.ClWtrTmp | #N/A | WTRM. | ClWtrTmp | Gear Cooling Water Temp | Temperatur des Getriebekühlwassers | Temperatura del agua de refrigeración del engranaje | Temp wody chłodzącej przekładnię | Gear cooling water temperature | deg_c | °C | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WTRM.ClWtrTmp_10m_Avg | #N/A | WTRM. | ClWtrTmp_10m_Avg | Gear Cooling Water Temp (avg) | Temperatur des Getriebekühlwassers (avg) | Temperatura del agua de refrigeración del engranaje (avg) | Temp wody chłodzącej przekładnię (avg) | Gear cooling water temperature | deg_c | °C | Average | Double | 10 minute tag
WTRM.ClWtrTnkPres | #N/A | WTRM. | ClWtrTnkPres | Gear cooling water tank pressure | Druck im Getriebekühlwassertank | Presión del depósito de agua de refrigeración del engranaje | Ciśnienie w zbiorniku wody chłodzącej przekładnię | Gear cooling water tank pressure | bar | bar | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WTRM.ClWtrTnkPres_10m_Avg | #N/A | WTRM. | ClWtrTnkPres_10m_Avg | Gear cooling water tank pressure (avg) | Druck im Getriebekühlwassertank (avg) | Presión del depósito de agua de refrigeración del engranaje (avg) | Ciśnienie w zbiorniku wody chłodzącej przekładnię (avg) | Gear cooling water tank pressure | bar | bar | Average | Double | 10 minute tag
WTRM.ClWtrTnkPres_10m_Max | #N/A | WTRM. | ClWtrTnkPres_10m_Max | Gear cooling water tank pressure (max) | Druck im Getriebekühlwassertank (max) | Presión del depósito de agua de refrigeración del engranaje (max) | Ciśnienie w zbiorniku wody chłodzącej przekładnię (max) | Gear cooling water tank pressure | bar | bar | Maximum | Double | 10 minute tag
WTRM.ClWtrTnkPres_10m_Min | #N/A | WTRM. | ClWtrTnkPres_10m_Min | Gear cooling water tank pressure (min) | Druck im Getriebekühlwassertank (min) | Presión del depósito de agua de refrigeración del engranaje (min) | Ciśnienie w zbiorniku wody chłodzącej przekładnię (min) | Gear cooling water tank pressure | bar | bar | Minimum | Double | 10 minute tag
WTRM.ClWtrTnkPres_10m_Std | #N/A | WTRM. | ClWtrTnkPres_10m_Std | Gear cooling water tank pressure (std) | Druck im Getriebekühlwassertank (std) | Presión del depósito de agua de refrigeración del engranaje (std) | Ciśnienie w zbiorniku wody chłodzącej przekładnię (std) | Gear cooling water tank pressure | bar | bar | Standard Deviation | Double | 10 minute tag
WTRM.FilSt | WTRM.FilSt | WTRM. | FilSt | Filtration System Status | Status des Filtersystems | Estado del sistema de filtración | Stan systemu filtracji | Status of filtration system | Enum | Enum | Live Value | Long | Live Value
WTRM.GbxBrgHSGenTmp | #N/A | WTRM. | GbxBrgHSGenTmp | Gearbox High Speed Bearing Generator End Temp | Endtemperatur Lager schnelle Welle Getriebe Generator | Temperatura final de la caja de cambios del cojinete de alta velocidad del generador | Przekładnia łożysko wysokoobrotowe Generator End Temp | Gearbox high speed bearing temperature generator end (HSGEN) | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxBrgHSGenTmp_10m_Avg | #N/A | WTRM. | GbxBrgHSGenTmp_10m_Avg | Gearbox High Speed Bearing Generator End Temp (avg) | Endtemperatur Lager schnelle Welle Getriebe Generator (avg) | Temperatura final de la caja de cambios del cojinete de alta velocidad del generador (avg) | Przekładnia łożysko wysokoobrotowe Generator End Temp (avg) | Gearbox high speed bearing temperature generator end (HSGEN) | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp_10m_Max | #N/A | WTRM. | GbxBrgHSGenTmp_10m_Max | Gearbox High Speed Bearing Generator End Temp (max) | Endtemperatur Lager schnelle Welle Getriebe Generator (max) | Temperatura final de la caja de cambios del cojinete de alta velocidad del generador (max) | Przekładnia łożysko wysokoobrotowe Generator End Temp (max) | Gearbox high speed bearing temperature generator end (HSGEN) | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp_10m_Min | #N/A | WTRM. | GbxBrgHSGenTmp_10m_Min | Gearbox High Speed Bearing Generator End Temp (min) | Endtemperatur Lager schnelle Welle Getriebe Generator (min) | Temperatura final de la caja de cambios del cojinete de alta velocidad del generador (min) | Przekładnia łożysko wysokoobrotowe Generator End Temp (min) | Gearbox high speed bearing temperature generator end (HSGEN) | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp_10m_Std | #N/A | WTRM. | GbxBrgHSGenTmp_10m_Std | Gearbox High Speed Bearing Generator End Temp (std) | Endtemperatur Lager schnelle Welle Getriebe Generator (std) | Temperatura final de la caja de cambios del cojinete de alta velocidad del generador (std) | Przekładnia łożysko wysokoobrotowe Generator End Temp (std) | Gearbox high speed bearing temperature generator end (HSGEN) | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp1 | #N/A | WTRM. | GbxBrgHSGenTmp1 | Gearbox High Speed Bearing 1 Generator End Temp | Endtemperatur Lager 1 schnelle Welle Getriebe Generator | Temperatura final de la caja de cambios del cojinete 1 de alta velocidad del generador | Przekładnia Łożysko wysokoobrotowe 1 Temp Generator End | Gearbox high speed bearing 1 temperature generator end (HSGEN) | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxBrgHSGenTmp1_10m_Avg | #N/A | WTRM. | GbxBrgHSGenTmp1_10m_Avg | Gearbox High Speed Bearing 1 Generator End Temp (avg) | Endtemperatur Lager 1 schnelle Welle Getriebe Generator (avg) | Temperatura final de la caja de cambios del cojinete 1 de alta velocidad del generador (avg) | Przekładnia Łożysko wysokoobrotowe 1 Temp Generator End (avg) | Gearbox high speed bearing 1 temperature generator end (HSGEN) | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp1_10m_Max | #N/A | WTRM. | GbxBrgHSGenTmp1_10m_Max | Gearbox High Speed Bearing 1 Generator End Temp (max) | Endtemperatur Lager 1 schnelle Welle Getriebe Generator (max) | Temperatura final de la caja de cambios del cojinete 1 de alta velocidad del generador (max) | Przekładnia Łożysko wysokoobrotowe 1 Temp Generator End (max) | Gearbox high speed bearing 1 temperature generator end (HSGEN) | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp1_10m_Min | #N/A | WTRM. | GbxBrgHSGenTmp1_10m_Min | Gearbox High Speed Bearing 1 Generator End Temp (min) | Endtemperatur Lager 1 schnelle Welle Getriebe Generator (min) | Temperatura final de la caja de cambios del cojinete 1 de alta velocidad del generador (min) | Przekładnia Łożysko wysokoobrotowe 1 Temp Generator End (min) | Gearbox high speed bearing 1 temperature generator end (HSGEN) | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp1_10m_Std | #N/A | WTRM. | GbxBrgHSGenTmp1_10m_Std | Gearbox High Speed Bearing 1 Generator End Temp (std) | Endtemperatur Lager 1 schnelle Welle Getriebe Generator (std) | Temperatura final de la caja de cambios del cojinete 1 de alta velocidad del generador (std) | Przekładnia Łożysko wysokoobrotowe 1 Temp Generator End (std) | Gearbox high speed bearing 1 temperature generator end (HSGEN) | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp2 | #N/A | WTRM. | GbxBrgHSGenTmp2 | Gearbox High Speed Bearing 2 Generator End Temp | Endtemperatur Lager 2 schnelle Welle Getriebe Generator | Temperatura final de la caja de cambios del cojinete 2 de alta velocidad del generador | Przekładnia Łożysko wysokoobrotowe 2 Temp Generator End | Gearbox high speed bearing 2 temperature generator end (HSGEN) | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxBrgHSGenTmp2_10m_Avg | #N/A | WTRM. | GbxBrgHSGenTmp2_10m_Avg | Gearbox High Speed Bearing 2 Generator End Temp (avg) | Endtemperatur Lager 2 schnelle Welle Getriebe Generator (avg) | Temperatura final de la caja de cambios del cojinete 2 de alta velocidad del generador (avg) | Przekładnia Łożysko wysokoobrotowe 2 Temp Generator End (avg) | Gearbox high speed bearing 2 temperature generator end (HSGEN) | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp2_10m_Max | #N/A | WTRM. | GbxBrgHSGenTmp2_10m_Max | Gearbox High Speed Bearing 2 Generator End Temp (max) | Endtemperatur Lager 2 schnelle Welle Getriebe Generator (max) | Temperatura final de la caja de cambios del cojinete 2 de alta velocidad del generador (max) | Przekładnia Łożysko wysokoobrotowe 2 Temp Generator End (max) | Gearbox high speed bearing 2 temperature generator end (HSGEN) | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp2_10m_Min | #N/A | WTRM. | GbxBrgHSGenTmp2_10m_Min | Gearbox High Speed Bearing 2 Generator End Temp (min) | Endtemperatur Lager 2 schnelle Welle Getriebe Generator (min) | Temperatura final de la caja de cambios del cojinete 2 de alta velocidad del generador (min) | Przekładnia Łożysko wysokoobrotowe 2 Temp Generator End (min) | Gearbox high speed bearing 2 temperature generator end (HSGEN) | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp2_10m_Std | #N/A | WTRM. | GbxBrgHSGenTmp2_10m_Std | Gearbox High Speed Bearing 2 Generator End Temp (std) | Endtemperatur Lager 2 schnelle Welle Getriebe Generator (std) | Temperatura final de la caja de cambios del cojinete 2 de alta velocidad del generador (std) | Przekładnia Łożysko wysokoobrotowe 2 Temp Generator End (std) | Gearbox high speed bearing 2 temperature generator end (HSGEN) | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp3 | #N/A | WTRM. | GbxBrgHSGenTmp3 | Gearbox High Speed Bearing 3 Generator End Temp | Endtemperatur Lager 3 schnelle Welle Getriebe Generator | Temperatura final de la caja de cambios del cojinete 3 de alta velocidad del generador | Przekładnia Łożysko wysokoobrotowe 3 Temp Generator End | Gearbox high speed bearing 3 temperature generator end (HSGEN) | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxBrgHSGenTmp3_10m_Avg | #N/A | WTRM. | GbxBrgHSGenTmp3_10m_Avg | Gearbox High Speed Bearing 3 Generator End Temp (avg) | Endtemperatur Lager 3 schnelle Welle Getriebe Generator (avg) | Temperatura final de la caja de cambios del cojinete 3 de alta velocidad del generador (avg) | Przekładnia Łożysko wysokoobrotowe 3 Temp Generator End (avg) | Gearbox high speed bearing 3 temperature generator end (HSGEN) | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp3_10m_Max | #N/A | WTRM. | GbxBrgHSGenTmp3_10m_Max | Gearbox High Speed Bearing 3 Generator End Temp (max) | Endtemperatur Lager 3 schnelle Welle Getriebe Generator (max) | Temperatura final de la caja de cambios del cojinete 3 de alta velocidad del generador (max) | Przekładnia Łożysko wysokoobrotowe 3 Temp Generator End (max) | Gearbox high speed bearing 3 temperature generator end (HSGEN) | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp3_10m_Min | #N/A | WTRM. | GbxBrgHSGenTmp3_10m_Min | Gearbox High Speed Bearing 3 Generator End Temp (min) | Endtemperatur Lager 3 schnelle Welle Getriebe Generator (min) | Temperatura final de la caja de cambios del cojinete 3 de alta velocidad del generador (min) | Przekładnia Łożysko wysokoobrotowe 3 Temp Generator End (min) | Gearbox high speed bearing 3 temperature generator end (HSGEN) | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp3_10m_Std | #N/A | WTRM. | GbxBrgHSGenTmp3_10m_Std | Gearbox High Speed Bearing 3 Generator End Temp (std) | Endtemperatur Lager 3 schnelle Welle Getriebe Generator (std) | Temperatura final de la caja de cambios del cojinete 3 de alta velocidad del generador (std) | Przekładnia Łożysko wysokoobrotowe 3 Temp Generator End (std) | Gearbox high speed bearing 3 temperature generator end (HSGEN) | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp4 | #N/A | WTRM. | GbxBrgHSGenTmp4 | Gearbox High Speed Bearing 4 Generator End Temp | Endtemperatur Lager 4 schnelle Welle Getriebe Generator | Temperatura final de la caja de cambios del cojinete 4 de alta velocidad del generador | Przekładnia Łożysko wysokoobrotowe 4 Temp Generator End | Gearbox high speed bearing 4 temperature generator end (HSGEN) | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxBrgHSGenTmp4_10m_Avg | #N/A | WTRM. | GbxBrgHSGenTmp4_10m_Avg | Gearbox High Speed Bearing 4 Generator End Temp (avg) | Endtemperatur Lager 4 schnelle Welle Getriebe Generator (avg) | Temperatura final de la caja de cambios del cojinete 4 de alta velocidad del generador (avg) | Przekładnia Łożysko wysokoobrotowe 4 Temp Generator End (avg) | Gearbox high speed bearing 4 temperature generator end (HSGEN) | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp4_10m_Max | #N/A | WTRM. | GbxBrgHSGenTmp4_10m_Max | Gearbox High Speed Bearing 4 Generator End Temp (max) | Endtemperatur Lager 4 schnelle Welle Getriebe Generator (max) | Temperatura final de la caja de cambios del cojinete 4 de alta velocidad del generador (max) | Przekładnia Łożysko wysokoobrotowe 4 Temp Generator End (max) | Gearbox high speed bearing 4 temperature generator end (HSGEN) | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp4_10m_Min | #N/A | WTRM. | GbxBrgHSGenTmp4_10m_Min | Gearbox High Speed Bearing 4 Generator End Temp (min) | Endtemperatur Lager 4 schnelle Welle Getriebe Generator (min) | Temperatura final de la caja de cambios del cojinete 4 de alta velocidad del generador (min) | Przekładnia Łożysko wysokoobrotowe 4 Temp Generator End (min) | Gearbox high speed bearing 4 temperature generator end (HSGEN) | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxBrgHSGenTmp4_10m_Std | #N/A | WTRM. | GbxBrgHSGenTmp4_10m_Std | Gearbox High Speed Bearing 4 Generator End Temp (std) | Endtemperatur Lager 4 schnelle Welle Getriebe Generator (std) | Temperatura final de la caja de cambios del cojinete 4 de alta velocidad del generador (std) | Przekładnia Łożysko wysokoobrotowe 4 Temp Generator End (std) | Gearbox high speed bearing 4 temperature generator end (HSGEN) | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.GbxBrgHSMidTmp | #N/A | WTRM. | GbxBrgHSMidTmp | Gearbox High Speed Bearing Middel Temp | Mitteltemperatur Lager schnelle Welle Getriebe Generator | Temperatura media del cojinete de alta velocidad de la caja de cambios | Przekładnia Łożysko wysokoobrotowe Middel Temp | Gearbox high speed bearing temperature middel (HSMID) | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxBrgHSMidTmp_10m_Avg | #N/A | WTRM. | GbxBrgHSMidTmp_10m_Avg | Gearbox High Speed Bearing Middel Temp (avg) | Mitteltemperatur Lager schnelle Welle Getriebe Generator (avg) | Temperatura media del cojinete de alta velocidad de la caja de cambios (avg) | Przekładnia Łożysko wysokoobrotowe Middel Temp (avg) | Gearbox high speed bearing temperature middel (HSMID) | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxBrgHSMidTmp_10m_Max | #N/A | WTRM. | GbxBrgHSMidTmp_10m_Max | Gearbox High Speed Bearing Middel Temp (max) | Mitteltemperatur Lager schnelle Welle Getriebe Generator (max) | Temperatura media del cojinete de alta velocidad de la caja de cambios (max) | Przekładnia Łożysko wysokoobrotowe Middel Temp (max) | Gearbox high speed bearing temperature middel (HSMID) | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxBrgHSMidTmp_10m_Min | #N/A | WTRM. | GbxBrgHSMidTmp_10m_Min | Gearbox High Speed Bearing Middel Temp (min) | Mitteltemperatur Lager schnelle Welle Getriebe Generator (min) | Temperatura media del cojinete de alta velocidad de la caja de cambios (min) | Przekładnia Łożysko wysokoobrotowe Middel Temp (min) | Gearbox high speed bearing temperature middel (HSMID) | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxBrgHSMidTmp_10m_Std | #N/A | WTRM. | GbxBrgHSMidTmp_10m_Std | Gearbox High Speed Bearing Middel Temp (std) | Mitteltemperatur Lager schnelle Welle Getriebe Generator (std) | Temperatura media del cojinete de alta velocidad de la caja de cambios (std) | Przekładnia Łożysko wysokoobrotowe Middel Temp (std) | Gearbox high speed bearing temperature middel (HSMID) | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.GbxBrgHSRotTmp | #N/A | WTRM. | GbxBrgHSRotTmp | Gearbox High Speed Bearing Rotor End Temp | Endtemperatur Lager schnelle Welle Getriebe Rotor | Temperatura final del rotor del cojinete de alta velocidad de la caja de cambios | Przekładnia wysokoobrotowa łożysko Rotor End Temp | Gearbox high speed bearing temperature rotor end (HSROT) | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxBrgHSRotTmp_10m_Avg | #N/A | WTRM. | GbxBrgHSRotTmp_10m_Avg | Gearbox High Speed Bearing Rotor End Temp (avg) | Endtemperatur Lager schnelle Welle Getriebe Rotor (avg) | Temperatura final del rotor del cojinete de alta velocidad de la caja de cambios (avg) | Przekładnia wysokoobrotowa łożysko Rotor End Temp (avg) | Gearbox high speed bearing temperature rotor end (HSROT) | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxBrgHSRotTmp_10m_Max | #N/A | WTRM. | GbxBrgHSRotTmp_10m_Max | Gearbox High Speed Bearing Rotor End Temp (max) | Endtemperatur Lager schnelle Welle Getriebe Rotor (max) | Temperatura final del rotor del cojinete de alta velocidad de la caja de cambios (max) | Przekładnia wysokoobrotowa łożysko Rotor End Temp (max) | Gearbox high speed bearing temperature rotor end (HSROT) | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxBrgHSRotTmp_10m_Min | #N/A | WTRM. | GbxBrgHSRotTmp_10m_Min | Gearbox High Speed Bearing Rotor End Temp (min) | Endtemperatur Lager schnelle Welle Getriebe Rotor (min) | Temperatura final del rotor del cojinete de alta velocidad de la caja de cambios (min) | Przekładnia wysokoobrotowa łożysko Rotor End Temp (min) | Gearbox high speed bearing temperature rotor end (HSROT) | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxBrgHSRotTmp_10m_Std | #N/A | WTRM. | GbxBrgHSRotTmp_10m_Std | Gearbox High Speed Bearing Rotor End Temp (std) | Endtemperatur Lager schnelle Welle Getriebe Rotor (std) | Temperatura final del rotor del cojinete de alta velocidad de la caja de cambios (std) | Przekładnia wysokoobrotowa łożysko Rotor End Temp (std) | Gearbox high speed bearing temperature rotor end (HSROT) | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.GbxBrgIMSGenTmp | #N/A | WTRM. | GbxBrgIMSGenTmp | Gearbox Intermediate Speed Bearing Generator End Temp | Endtemperatur Lager mittlere Welle Getriebe Generator | Temperatura final del generador del cojinete de velocidad intermedia de la caja de cambios | Przekładnia Łożysko średnioobrotowe Generator End Temp | Gearbox intermediate speed bearing temperature generator end (IMSGEN) | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxBrgIMSGenTmp_10m_Avg | #N/A | WTRM. | GbxBrgIMSGenTmp_10m_Avg | Gearbox Intermediate Speed Bearing Generator End Temp (avg) | Endtemperatur Lager mittlere Welle Getriebe Generator (avg) | Temperatura final del generador del cojinete de velocidad intermedia de la caja de cambios (avg) | Przekładnia Łożysko średnioobrotowe Generator End Temp (avg) | Gearbox intermediate speed bearing temperature generator end (IMSGEN) | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxBrgIMSGenTmp_10m_Max | #N/A | WTRM. | GbxBrgIMSGenTmp_10m_Max | Gearbox Intermediate Speed Bearing Generator End Temp (max) | Endtemperatur Lager mittlere Welle Getriebe Generator (max) | Temperatura final del generador del cojinete de velocidad intermedia de la caja de cambios (max) | Przekładnia Łożysko średnioobrotowe Generator End Temp (max) | Gearbox intermediate speed bearing temperature generator end (IMSGEN) | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxBrgIMSGenTmp_10m_Min | #N/A | WTRM. | GbxBrgIMSGenTmp_10m_Min | Gearbox Intermediate Speed Bearing Generator End Temp (min) | Endtemperatur Lager mittlere Welle Getriebe Generator (min) | Temperatura final del generador del cojinete de velocidad intermedia de la caja de cambios (min) | Przekładnia Łożysko średnioobrotowe Generator End Temp (min) | Gearbox intermediate speed bearing temperature generator end (IMSGEN) | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxBrgIMSGenTmp_10m_Std | #N/A | WTRM. | GbxBrgIMSGenTmp_10m_Std | Gearbox Intermediate Speed Bearing Generator End Temp (std) | Endtemperatur Lager mittlere Welle Getriebe Generator (std) | Temperatura final del generador del cojinete de velocidad intermedia de la caja de cambios (std) | Przekładnia Łożysko średnioobrotowe Generator End Temp (std) | Gearbox intermediate speed bearing temperature generator end (IMSGEN) | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.GbxBrgIMSRotTmp | #N/A | WTRM. | GbxBrgIMSRotTmp | Gearbox Intermediate Speed Bearing Rotor End Temp | Endtemperatur Lager mittlere Welle Getriebe Rotor | Temperatura final del rotor del cojinete de velocidad intermedia de la caja de cambios | Przekładnia łożysko średnioobrotowe Rotor End Temp | Gearbox intermediate speed bearing temperature rotor end (IMSROT) | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxBrgIMSRotTmp_10m_Avg | #N/A | WTRM. | GbxBrgIMSRotTmp_10m_Avg | Gearbox Intermediate Speed Bearing Rotor End Temp (avg) | Endtemperatur Lager mittlere Welle Getriebe Rotor (avg) | Temperatura final del rotor del cojinete de velocidad intermedia de la caja de cambios (avg) | Przekładnia łożysko średnioobrotowe Rotor End Temp (avg) | Gearbox intermediate speed bearing temperature rotor end (IMSROT) | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxBrgIMSRotTmp_10m_Max | #N/A | WTRM. | GbxBrgIMSRotTmp_10m_Max | Gearbox Intermediate Speed Bearing Rotor End Temp (max) | Endtemperatur Lager mittlere Welle Getriebe Rotor (max) | Temperatura final del rotor del cojinete de velocidad intermedia de la caja de cambios (max) | Przekładnia łożysko średnioobrotowe Rotor End Temp (max) | Gearbox intermediate speed bearing temperature rotor end (IMSROT) | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxBrgIMSRotTmp_10m_Min | #N/A | WTRM. | GbxBrgIMSRotTmp_10m_Min | Gearbox Intermediate Speed Bearing Rotor End Temp (min) | Endtemperatur Lager mittlere Welle Getriebe Rotor (min) | Temperatura final del rotor del cojinete de velocidad intermedia de la caja de cambios (min) | Przekładnia łożysko średnioobrotowe Rotor End Temp (min) | Gearbox intermediate speed bearing temperature rotor end (IMSROT) | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxBrgIMSRotTmp_10m_Std | #N/A | WTRM. | GbxBrgIMSRotTmp_10m_Std | Gearbox Intermediate Speed Bearing Rotor End Temp (std) | Endtemperatur Lager mittlere Welle Getriebe Rotor (std) | Temperatura final del rotor del cojinete de velocidad intermedia de la caja de cambios (std) | Przekładnia łożysko średnioobrotowe Rotor End Temp (std) | Gearbox intermediate speed bearing temperature rotor end (IMSROT) | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.GbxBrgLSGenTmp | #N/A | WTRM. | GbxBrgLSGenTmp | Gearbox Low Speed Bearing Generator End Temp | Endtemperatur Lager langsame Welle Getriebe Generator | Temperatura final del generador del cojinete de baja velocidad de la caja de cambios | Przekładnia Łożysko niskoobrotowe Generator End Temp | Gearbox low speed bearing temperature generator end (LSGEN) | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxBrgLSGenTmp_10m_Avg | #N/A | WTRM. | GbxBrgLSGenTmp_10m_Avg | Gearbox Low Speed Bearing Generator End Temp (avg) | Endtemperatur Lager langsame Welle Getriebe Generator (avg) | Temperatura final del generador del cojinete de baja velocidad de la caja de cambios (avg) | Przekładnia Łożysko niskoobrotowe Generator End Temp (avg) | Gearbox low speed bearing temperature generator end (LSGEN) | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxBrgLSGenTmp_10m_Max | #N/A | WTRM. | GbxBrgLSGenTmp_10m_Max | Gearbox Low Speed Bearing Generator End Temp (max) | Endtemperatur Lager langsame Welle Getriebe Generator (max) | Temperatura final del generador del cojinete de baja velocidad de la caja de cambios (max) | Przekładnia Łożysko niskoobrotowe Generator End Temp (max) | Gearbox low speed bearing temperature generator end (LSGEN) | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxBrgLSGenTmp_10m_Min | #N/A | WTRM. | GbxBrgLSGenTmp_10m_Min | Gearbox Low Speed Bearing Generator End Temp (min) | Endtemperatur Lager langsame Welle Getriebe Generator (min) | Temperatura final del generador del cojinete de baja velocidad de la caja de cambios (min) | Przekładnia Łożysko niskoobrotowe Generator End Temp (min) | Gearbox low speed bearing temperature generator end (LSGEN) | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxBrgLSGenTmp_10m_Std | #N/A | WTRM. | GbxBrgLSGenTmp_10m_Std | Gearbox Low Speed Bearing Generator End Temp (std) | Endtemperatur Lager langsame Welle Getriebe Generator (std) | Temperatura final del generador del cojinete de baja velocidad de la caja de cambios (std) | Przekładnia Łożysko niskoobrotowe Generator End Temp (std) | Gearbox low speed bearing temperature generator end (LSGEN) | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.GbxBrgLSRotTmp | #N/A | WTRM. | GbxBrgLSRotTmp | Gearbox Low Speed Bearing Rotor End Temp | Endtemperatur Lager langsame Welle Getriebe Rotor | Temperatura final del rotor del cojinete de baja velocidad de la caja de cambios | Przekładnia łożysko niskoobrotowe Rotor End Temp | Gearbox low speed bearing temperature rotor end (LSROT) | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxBrgLSRotTmp_10m_Avg | #N/A | WTRM. | GbxBrgLSRotTmp_10m_Avg | Gearbox Low Speed Bearing Rotor End Temp (avg) | Endtemperatur Lager langsame Welle Getriebe Rotor (avg) | Temperatura final del rotor del cojinete de baja velocidad de la caja de cambios (avg) | Przekładnia łożysko niskoobrotowe Rotor End Temp (avg) | Gearbox low speed bearing temperature rotor end (LSROT) | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxBrgLSRotTmp_10m_Max | #N/A | WTRM. | GbxBrgLSRotTmp_10m_Max | Gearbox Low Speed Bearing Rotor End Temp (max) | Endtemperatur Lager langsame Welle Getriebe Rotor (max) | Temperatura final del rotor del cojinete de baja velocidad de la caja de cambios (max) | Przekładnia łożysko niskoobrotowe Rotor End Temp (max) | Gearbox low speed bearing temperature rotor end (LSROT) | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxBrgLSRotTmp_10m_Min | #N/A | WTRM. | GbxBrgLSRotTmp_10m_Min | Gearbox Low Speed Bearing Rotor End Temp (min) | Endtemperatur Lager langsame Welle Getriebe Rotor (min) | Temperatura final del rotor del cojinete de baja velocidad de la caja de cambios (min) | Przekładnia łożysko niskoobrotowe Rotor End Temp (min) | Gearbox low speed bearing temperature rotor end (LSROT) | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxBrgLSRotTmp_10m_Std | #N/A | WTRM. | GbxBrgLSRotTmp_10m_Std | Gearbox Low Speed Bearing Rotor End Temp (std) | Endtemperatur Lager langsame Welle Getriebe Rotor (std) | Temperatura final del rotor del cojinete de baja velocidad de la caja de cambios (std) | Przekładnia łożysko niskoobrotowe Rotor End Temp (std) | Gearbox low speed bearing temperature rotor end (LSROT) | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.GbxBrgTmp1 | #N/A | WTRM. | GbxBrgTmp1 | Gearbox Bearing 1 Temp | Getriebe Lager 1 Temperatur | Temperatura del cojinete 1 de la caja de cambios | Przekładnia 1 Temp | Gearbox bearing 1 temperature | deg_c | °C | Live Value | Double | Live Value | Used in some specialised presentations
WTRM.GbxBrgTmp1_10m_Avg | #N/A | WTRM. | GbxBrgTmp1_10m_Avg | Gearbox Bearing 1 Temp (avg) | Getriebe Lager 1 Temperatur (avg) | Temperatura del cojinete 1 de la caja de cambios (avg) | Przekładnia 1 Temp (avg) | Gearbox bearing 1 temperature | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxBrgTmp1_10m_Max | #N/A | WTRM. | GbxBrgTmp1_10m_Max | Gearbox Bearing 1 Temp (max) | Getriebe Lager 1 Temperatur (max) | Temperatura del cojinete 1 de la caja de cambios (max) | Przekładnia 1 Temp (max) | Gearbox bearing 1 temperature | deg_c | °C | Maximum | Double | 10 minute tag | Common tags for analysis
WTRM.GbxBrgTmp1_10m_Min | #N/A | WTRM. | GbxBrgTmp1_10m_Min | Gearbox Bearing 1 Temp (min) | Getriebe Lager 1 Temperatur (min) | Temperatura del cojinete 1 de la caja de cambios (min) | Przekładnia 1 Temp (min) | Gearbox bearing 1 temperature | deg_c | °C | Minimum | Double | 10 minute tag | Common tags for analysis
WTRM.GbxBrgTmp1_10m_Std | #N/A | WTRM. | GbxBrgTmp1_10m_Std | Gearbox Bearing 1 Temp (std) | Getriebe Lager 1 Temperatur (std) | Temperatura del cojinete 1 de la caja de cambios (std) | Przekładnia 1 Temp (std) | Gearbox bearing 1 temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WTRM.GbxBrgTmp2 | #N/A | WTRM. | GbxBrgTmp2 | Gearbox Bearing 2 Temp | Getriebe Lager 2 Temperatur | Temperatura del cojinete 2 de la caja de cambios | Przekładnia 2 Temp | Gearbox bearing 2 temperature | deg_c | °C | Live Value | Double | Live Value | Used in some specialised presentations
WTRM.GbxBrgTmp2_10m_Avg | #N/A | WTRM. | GbxBrgTmp2_10m_Avg | Gearbox Bearing 2 Temp (avg) | Getriebe Lager 2 Temperatur (avg) | Temperatura del cojinete 2 de la caja de cambios (avg) | Przekładnia 2 Temp (avg) | Gearbox bearing 2 temperature | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxBrgTmp2_10m_Max | #N/A | WTRM. | GbxBrgTmp2_10m_Max | Gearbox Bearing 2 Temp (max) | Getriebe Lager 2 Temperatur (max) | Temperatura del cojinete 2 de la caja de cambios (max) | Przekładnia 2 Temp (max) | Gearbox bearing 2 temperature | deg_c | °C | Maximum | Double | 10 minute tag | Common tags for analysis
WTRM.GbxBrgTmp2_10m_Min | #N/A | WTRM. | GbxBrgTmp2_10m_Min | Gearbox Bearing 2 Temp (min) | Getriebe Lager 2 Temperatur (min) | Temperatura del cojinete 2 de la caja de cambios (min) | Przekładnia 2 Temp (min) | Gearbox bearing 2 temperature | deg_c | °C | Minimum | Double | 10 minute tag | Common tags for analysis
WTRM.GbxBrgTmp2_10m_Std | #N/A | WTRM. | GbxBrgTmp2_10m_Std | Gearbox Bearing 2 Temp (std) | Getriebe Lager 2 Temperatur (std) | Temperatura del cojinete 2 de la caja de cambios (std) | Przekładnia 2 Temp (std) | Gearbox bearing 2 temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WTRM.GbxBrgTmp3 | #N/A | WTRM. | GbxBrgTmp3 | Gearbox Bearing 3 Temp | Getriebe Lager 3 Temperatur | Temperatura del cojinete 3 de la caja de cambios | Przekładnia 3 Temp | Gearbox bearing 3 temperature | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxBrgTmp3_10m_Avg | #N/A | WTRM. | GbxBrgTmp3_10m_Avg | Gearbox Bearing 3 Temp (avg) | Getriebe Lager 3 Temperatur (avg) | Temperatura del cojinete 3 de la caja de cambios (avg) | Przekładnia 3 Temp (avg) | Gearbox bearing 3 temperature | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxBrgTmp3_10m_Max | #N/A | WTRM. | GbxBrgTmp3_10m_Max | Gearbox Bearing 3 Temp (max) | Getriebe Lager 3 Temperatur (max) | Temperatura del cojinete 3 de la caja de cambios (max) | Przekładnia 3 Temp (max) | Gearbox bearing 3 temperature | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxBrgTmp3_10m_Min | #N/A | WTRM. | GbxBrgTmp3_10m_Min | Gearbox Bearing 3 Temp (min) | Getriebe Lager 3 Temperatur (min) | Temperatura del cojinete 3 de la caja de cambios (min) | Przekładnia 3 Temp (min) | Gearbox bearing 3 temperature | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxBrgTmp3_10m_Std | #N/A | WTRM. | GbxBrgTmp3_10m_Std | Gearbox Bearing 3 Temp (std) | Getriebe Lager 3 Temperatur (std) | Temperatura del cojinete 3 de la caja de cambios (std) | Przekładnia 3 Temp (std) | Gearbox bearing 3 temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.GbxBrgTmp4 | #N/A | WTRM. | GbxBrgTmp4 | Gearbox Bearing 4 Temp | Getriebe Lager 4 Temperatur | Temperatura del cojinete 4 de la caja de cambios | Przekładnia 4 Temp | Gearbox bearing 4 temperature | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxBrgTmp4_10m_Avg | #N/A | WTRM. | GbxBrgTmp4_10m_Avg | Gearbox Bearing 4 Temp (avg) | Getriebe Lager 4 Temperatur (avg) | Temperatura del cojinete 4 de la caja de cambios (avg) | Przekładnia 4 Temp (avg) | Gearbox bearing 4 temperature | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxBrgTmp4_10m_Max | #N/A | WTRM. | GbxBrgTmp4_10m_Max | Gearbox Bearing 4 Temp (max) | Getriebe Lager 4 Temperatur (max) | Temperatura del cojinete 4 de la caja de cambios (max) | Przekładnia 4 Temp (max) | Gearbox bearing 4 temperature | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxBrgTmp4_10m_Min | #N/A | WTRM. | GbxBrgTmp4_10m_Min | Gearbox Bearing 4 Temp (min) | Getriebe Lager 4 Temperatur (min) | Temperatura del cojinete 4 de la caja de cambios (min) | Przekładnia 4 Temp (min) | Gearbox bearing 4 temperature | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxBrgTmp4_10m_Std | #N/A | WTRM. | GbxBrgTmp4_10m_Std | Gearbox Bearing 4 Temp (std) | Getriebe Lager 4 Temperatur (std) | Temperatura del cojinete 4 de la caja de cambios (std) | Przekładnia 4 Temp (std) | Gearbox bearing 4 temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.GbxBrgTmp5 | #N/A | WTRM. | GbxBrgTmp5 | Gearbox Bearing 5 Temp | Getriebe Lager 5 Temperatur | Temperatura del cojinete 5 de la caja de cambios | Przekładnia 5 Temp | Actual gear bearing IMS2 (Rear) temperature | deg_c | °C | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WTRM.GbxEmgLuSt | #N/A | WTRM. | GbxEmgLuSt | Gearbox Emergency lubrication | Getriebe Notschmierung | Lubricación de emergencia de la caja de cambios | Przekładnia Smarowanie awaryjne | Gear Emergency lubrication system Turbine OK | Enum | Enum | Live Value | Long | Live Value
WTRM.GbxOilClPmpCnt | #N/A | WTRM. | GbxOilClPmpCnt | Number of activations of Gearbox oil cooling pump | Anzahl der Aktivierungen der Getriebeöl-Kühlpumpe | Número de activaciones de la bomba de refrigeración de la caja de cambios | Liczba aktywacji pompy chłodzenia oleju przekładni | Number of activations of Gearbox oil cooling pump | count | Count | Total Counter | Long | Live Value
WTRM.GbxOilClPmpCnt_10m_End | #N/A | WTRM. | GbxOilClPmpCnt_10m_End | Number of activations of Gearbox oil cooling pump (end) | Anzahl der Aktivierungen der Getriebeöl-Kühlpumpe (end) | Número de activaciones de la bomba de refrigeración de la caja de cambios (end) | Liczba aktywacji pompy chłodzenia oleju przekładni (end) | Number of activations of Gearbox oil cooling pump | count | Count | Endvalue | Long | 10 minute tag
WTRM.GbxOilClPmpTms | #N/A | WTRM. | GbxOilClPmpTms | Time the Gearbox oil cooling pump has been activated | Zeit, in der die Getriebeöl-Kühlpumpe aktiviert wurde | Tiempo que la bomba de refrigeración de aceite de la caja de cambios ha estado activada | Czas aktywacji pompy chłodzenia oleju przekładni | Time the Gearbox oil cooling pump has been activated | s | seconds | Total Counter | Long | Live Value
WTRM.GbxOilClPmpTms_10m_End | #N/A | WTRM. | GbxOilClPmpTms_10m_End | Time the Gearbox oil cooling pump has been activated (end) | Zeit, in der die Getriebeöl-Kühlpumpe aktiviert wurde (end) | Tiempo que la bomba de refrigeración de aceite de la caja de cambios ha estado activada (end) | Czas aktywacji pompy chłodzenia oleju przekładni (end) | Time the Gearbox oil cooling pump has been activated | s | seconds | Endvalue | Long | 10 minute tag
WTRM.GbxOilFanHSpdCnt | #N/A | WTRM. | GbxOilFanHSpdCnt | Number of activations of gear oil pump high speed fan | Anzahl der Aktivierungen schnelle Welle Lüfter der Getriebeölpumpe | Número de activaciones del ventilador de alta velocidad de la bomba de aceite del engranaje | Liczba aktywacji wysokoodbiegowego wentylatora pompy oleju przekładni | Number of activations of gear oil pump high speed fan | count | Count | Total Counter | Long | Live Value
WTRM.GbxOilFanHSpdCnt_10m_End | #N/A | WTRM. | GbxOilFanHSpdCnt_10m_End | Number of activations of gear oil pump high speed fan (end) | Anzahl der Aktivierungen schnelle Welle Lüfter der Getriebeölpumpe (end) | Número de activaciones del ventilador de alta velocidad de la bomba de aceite del engranaje (end) | Liczba aktywacji wysokoodbiegowego wentylatora pompy oleju przekładni (end) | Number of activations of gear oil pump high speed fan | count | Count | Endvalue | Long | 10 minute tag
WTRM.GbxOilFanHSpdTms | #N/A | WTRM. | GbxOilFanHSpdTms | Time the gear oil pump high speed fan has been activated | Zeit, in der schnelle Welle Lüfter der Getriebeölpumpe aktiviert wurde | Tiempo que el ventilador de alta velocidad de la bomba de aceite del engranaje ha estado activado | Czas aktywacji wysokoodyżnego wentylatora pompy oleju przekładni | Time the gear oil pump high speed fan has been activated | s | seconds | Total Counter | Long | Live Value
WTRM.GbxOilFanHSpdTms_10m_End | #N/A | WTRM. | GbxOilFanHSpdTms_10m_End | Time the gear oil pump high speed fan has been activated (end) | Zeit, in der schnelle Welle Lüfter der Getriebeölpumpe aktiviert wurde (end) | Tiempo que el ventilador de alta velocidad de la bomba de aceite del engranaje ha estado activado (end) | Czas aktywacji wysokoodyżnego wentylatora pompy oleju przekładni (end) | Time the gear oil pump high speed fan has been activated | s | seconds | Endvalue | Long | 10 minute tag
WTRM.GbxOilFanLSpdCnt | #N/A | WTRM. | GbxOilFanLSpdCnt | Number of activations of gear oil pump low speed fan | Anzahl der Aktivierungen langsame Welle Lüfter der Getriebeölpumpe | Número de activaciones del ventilador de baja velocidad de la bomba de aceite del engranaje | Liczba aktywacji wentylatora niskobieżnego pompy oleju przekładni | Number of activations of gear oil pump low speed fan | count | Count | Total Counter | Long | Live Value
WTRM.GbxOilFanLSpdCnt_10m_End | #N/A | WTRM. | GbxOilFanLSpdCnt_10m_End | Number of activations of gear oil pump low speed fan (end) | Anzahl der Aktivierungen langsame Welle Lüfter der Getriebeölpumpe (end) | Número de activaciones del ventilador de baja velocidad de la bomba de aceite del engranaje (end) | Liczba aktywacji wentylatora niskobieżnego pompy oleju przekładni (end) | Number of activations of gear oil pump low speed fan | count | Count | Endvalue | Long | 10 minute tag
WTRM.GbxOilFanLSpdTms | #N/A | WTRM. | GbxOilFanLSpdTms | Time the gear oil pump low speed fan has been activated | Zeit, in der langsame Welle Lüfter der Getriebeölpumpe aktiviert wurde | Tiempo que el ventilador de baja velocidad de la bomba de aceite del engranaje ha estado activado | Czas aktywacji wentylatora niskobieżnego pompy oleju przekładni | Time the gear oil pump low speed fan has been activated | s | seconds | Total Counter | Long | Live Value
WTRM.GbxOilFanLSpdTms_10m_End | #N/A | WTRM. | GbxOilFanLSpdTms_10m_End | Time the gear oil pump low speed fan has been activated (end) | Zeit, in der langsame Welle Lüfter der Getriebeölpumpe aktiviert wurde (end) | Tiempo que el ventilador de baja velocidad de la bomba de aceite del engranaje ha estado activado (end) | Czas aktywacji wentylatora niskobieżnego pompy oleju przekładni (end) | Time the gear oil pump low speed fan has been activated | s | seconds | Endvalue | Long | 10 minute tag
WTRM.GbxOilFanMSpdCnt | #N/A | WTRM. | GbxOilFanMSpdCnt | Number of activations of gear oil pump medium speed fan | Anzahl der Aktivierungen mittlere Welle Lüfter der Getriebeölpumpe | Número de activaciones del ventilador de media velocidad de la bomba de aceite del engranaje | Liczba aktywacji średniobieżnego wentylatora pompy oleju przekładni | Number of activations of gear oil pump medium speed fan | count | Count | Total Counter | Long | Live Value
WTRM.GbxOilFanMSpdCnt_10m_End | #N/A | WTRM. | GbxOilFanMSpdCnt_10m_End | Number of activations of gear oil pump medium speed fan (end) | Anzahl der Aktivierungen mittlere Welle Lüfter der Getriebeölpumpe (end) | Número de activaciones del ventilador de media velocidad de la bomba de aceite del engranaje (end) | Liczba aktywacji średniobieżnego wentylatora pompy oleju przekładni (end) | Number of activations of gear oil pump medium speed fan | count | Count | Endvalue | Long | 10 minute tag
WTRM.GbxOilFilInPres | #N/A | WTRM. | GbxOilFilInPres | Gearbox oil filter pressure at inlet | Druck des Getriebeölfilters am Einlass | Presión de filtro de aceite de la caja de cambios en la entrada | Ciśnienie w filtrze oleju przekładni na wlocie | Gearbox oil filter pressure at inlet | bar | bar | Live Value | Double | Live Value
WTRM.GbxOilFilInPres_10m_Avg | #N/A | WTRM. | GbxOilFilInPres_10m_Avg | Gearbox oil filter pressure at inlet (avg) | Druck des Getriebeölfilters am Einlass (avg) | Presión de filtro de aceite de la caja de cambios en la entrada (avg) | Ciśnienie w filtrze oleju przekładni na wlocie (avg) | Gearbox oil filter pressure at inlet | bar | bar | Average | Double | 10 minute tag
WTRM.GbxOilFilInPres_10m_Max | #N/A | WTRM. | GbxOilFilInPres_10m_Max | Gearbox oil filter pressure at inlet (max) | Druck des Getriebeölfilters am Einlass (max) | Presión de filtro de aceite de la caja de cambios en la entrada (max) | Ciśnienie w filtrze oleju przekładni na wlocie (max) | Gearbox oil filter pressure at inlet | bar | bar | Maximum | Double | 10 minute tag
WTRM.GbxOilFilInPres_10m_Min | #N/A | WTRM. | GbxOilFilInPres_10m_Min | Gearbox oil filter pressure at inlet (min) | Druck des Getriebeölfilters am Einlass (min) | Presión de filtro de aceite de la caja de cambios en la entrada (min) | Ciśnienie w filtrze oleju przekładni na wlocie (min) | Gearbox oil filter pressure at inlet | bar | bar | Minimum | Double | 10 minute tag
WTRM.GbxOilFilInPres_10m_Std | #N/A | WTRM. | GbxOilFilInPres_10m_Std | Gearbox oil filter pressure at inlet (std) | Druck des Getriebeölfilters am Einlass (std) | Presión de filtro de aceite de la caja de cambios en la entrada (std) | Ciśnienie w filtrze oleju przekładni na wlocie (std) | Gearbox oil filter pressure at inlet | bar | bar | Standard Deviation | Double | 10 minute tag
WTRM.GbxOilFilOutPres | #N/A | WTRM. | GbxOilFilOutPres | Gearbox oil filter pressure at outlet | Druck des Getriebeölfilters am Ausgang | Presión de filtro de aceite de la caja de cambios en la salida | Ciśnienie filtra oleju przekładni na wylocie | Gearbox oil filter pressure at outlet | bar | bar | Live Value | Double | Live Value
WTRM.GbxOilFilOutPres_10m_Avg | #N/A | WTRM. | GbxOilFilOutPres_10m_Avg | Gearbox oil filter pressure at outlet (avg) | Druck des Getriebeölfilters am Ausgang (avg) | Presión de filtro de aceite de la caja de cambios en la salida (avg) | Ciśnienie filtra oleju przekładni na wylocie (avg) | Gearbox oil filter pressure at outlet | bar | bar | Average | Double | 10 minute tag
WTRM.GbxOilFilOutPres_10m_Max | #N/A | WTRM. | GbxOilFilOutPres_10m_Max | Gearbox oil filter pressure at outlet (max) | Druck des Getriebeölfilters am Ausgang (max) | Presión de filtro de aceite de la caja de cambios en la salida (max) | Ciśnienie filtra oleju przekładni na wylocie (max) | Gearbox oil filter pressure at outlet | bar | bar | Maximum | Double | 10 minute tag
WTRM.GbxOilFilOutPres_10m_Min | #N/A | WTRM. | GbxOilFilOutPres_10m_Min | Gearbox oil filter pressure at outlet (min) | Druck des Getriebeölfilters am Ausgang (min) | Presión de filtro de aceite de la caja de cambios en la salida (min) | Ciśnienie filtra oleju przekładni na wylocie (min) | Gearbox oil filter pressure at outlet | bar | bar | Minimum | Double | 10 minute tag
WTRM.GbxOilFilOutPres_10m_Std | #N/A | WTRM. | GbxOilFilOutPres_10m_Std | Gearbox oil filter pressure at outlet (std) | Druck des Getriebeölfilters am Ausgang (std) | Presión de filtro de aceite de la caja de cambios en la salida (std) | Ciśnienie filtra oleju przekładni na wylocie (std) | Gearbox oil filter pressure at outlet | bar | bar | Standard Deviation | Double | 10 minute tag
WTRM.GbxOilFilPres | #N/A | WTRM. | GbxOilFilPres | Gearbox oil filter pressure | Druck des Getriebeölfilters | Presión de filtro de aceite de la caja de cambios | Ciśnienie w filtrze oleju przekładni | Gearbox oil filter pressure | bar | bar | Live Value | Double | Live Value
WTRM.GbxOilFilPres_10m_Avg | #N/A | WTRM. | GbxOilFilPres_10m_Avg | Gearbox oil filter pressure (avg) | Druck des Getriebeölfilters (avg) | Presión de filtro de aceite de la caja de cambios (avg) | Ciśnienie w filtrze oleju przekładni (avg) | Gearbox oil filter pressure | bar | bar | Average | Double | 10 minute tag
WTRM.GbxOilFilPres_10m_Max | #N/A | WTRM. | GbxOilFilPres_10m_Max | Gearbox oil filter pressure (max) | Druck des Getriebeölfilters (max) | Presión de filtro de aceite de la caja de cambios (max) | Ciśnienie w filtrze oleju przekładni (max) | Gearbox oil filter pressure | bar | bar | Maximum | Double | 10 minute tag
WTRM.GbxOilFilPres_10m_Min | #N/A | WTRM. | GbxOilFilPres_10m_Min | Gearbox oil filter pressure (min) | Druck des Getriebeölfilters (min) | Presión de filtro de aceite de la caja de cambios (min) | Ciśnienie w filtrze oleju przekładni (min) | Gearbox oil filter pressure | bar | bar | Minimum | Double | 10 minute tag
WTRM.GbxOilFilPres_10m_Std | #N/A | WTRM. | GbxOilFilPres_10m_Std | Gearbox oil filter pressure (std) | Druck des Getriebeölfilters (std) | Presión de filtro de aceite de la caja de cambios (std) | Ciśnienie w filtrze oleju przekładni (std) | Gearbox oil filter pressure | bar | bar | Standard Deviation | Double | 10 minute tag
WTRM.GbxOilFilTmp | #N/A | WTRM. | GbxOilFilTmp | Gearbox Oil Filter Temp | Getriebeöl-Filtertemperatur | Temperatura de filtro de aceite de la caja de cambios | Temp filtra oleju przekładni | Gearbox oil filter temperature | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxOilFilTmp_10m_Avg | #N/A | WTRM. | GbxOilFilTmp_10m_Avg | Gearbox Oil Filter Temp (avg) | Getriebeöl-Filtertemperatur (avg) | Temperatura de filtro de aceite de la caja de cambios (avg) | Temp filtra oleju przekładni (avg) | Gearbox oil filter temperature | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxOilFilTmp_10m_Max | #N/A | WTRM. | GbxOilFilTmp_10m_Max | Gearbox Oil Filter Temp (max) | Getriebeöl-Filtertemperatur (max) | Temperatura de filtro de aceite de la caja de cambios (max) | Temp filtra oleju przekładni (max) | Gearbox oil filter temperature | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxOilFilTmp_10m_Min | #N/A | WTRM. | GbxOilFilTmp_10m_Min | Gearbox Oil Filter Temp (min) | Getriebeöl-Filtertemperatur (min) | Temperatura de filtro de aceite de la caja de cambios (min) | Temp filtra oleju przekładni (min) | Gearbox oil filter temperature | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxOilFilTmp_10m_Std | #N/A | WTRM. | GbxOilFilTmp_10m_Std | Gearbox Oil Filter Temp (std) | Getriebeöl-Filtertemperatur (std) | Temperatura de filtro de aceite de la caja de cambios (std) | Temp filtra oleju przekładni (std) | Gearbox oil filter temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.GbxOilHtCnt | #N/A | WTRM. | GbxOilHtCnt | Number of activations of the Gearbox oil heat | Anzahl der Aktivierungen der Getriebeölheizung | Número de activaciones del calentador de aceite de la caja de cambios | Liczba aktywacji ogrz. oleju przekładni | Number of activations of the Gearbox oil heat | count | Count | Total Counter | Long | Live Value
WTRM.GbxOilHtCnt_10m_End | #N/A | WTRM. | GbxOilHtCnt_10m_End | Number of activations of the Gearbox oil heat (end) | Anzahl der Aktivierungen der Getriebeölheizung (end) | Número de activaciones del calentador de aceite de la caja de cambios (end) | Liczba aktywacji ogrz. oleju przekładni (end) | Number of activations of the Gearbox oil heat | count | Count | Endvalue | Long | 10 minute tag
WTRM.GbxOilHtTms | #N/A | WTRM. | GbxOilHtTms | Time the Gearbox oil heat has been activated | Zeit, in der die Getriebeölheizung aktiviert wurde | Tiempo que el calentador de aceite de la caja de cambios ha estado activado | Czas aktywacji ogrz. oleju przekładni | Time the Gearbox oil heat has been activated | s | seconds | Total Counter | Long | Live Value
WTRM.GbxOilHtTms_10m_End | #N/A | WTRM. | GbxOilHtTms_10m_End | Time the Gearbox oil heat has been activated (end) | Zeit, in der die Getriebeölheizung aktiviert wurde (end) | Tiempo que el calentador de aceite de la caja de cambios ha estado activado (end) | Czas aktywacji ogrz. oleju przekładni (end) | Time the Gearbox oil heat has been activated | s | seconds | Endvalue | Long | 10 minute tag
WTRM.GbxOilInletPres | #N/A | WTRM. | GbxOilInletPres | Gear oil inlet pressure | Getriebeöl-Eingangsdruck | Presión de entrada de aceite del engranaje | Ciśnienie na wlocie oleju przekładni | Gear oil inlet pressure | bar | bar | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WTRM.GbxOilInletPres_10m_Avg | #N/A | WTRM. | GbxOilInletPres_10m_Avg | Gear oil inlet pressure (avg) | Getriebeöl-Eingangsdruck (avg) | Presión de entrada de aceite del engranaje (avg) | Ciśnienie na wlocie oleju przekładni (avg) | Gear oil inlet pressure | bar | bar | Average | Double | 10 minute tag
WTRM.GbxOilInletPres_10m_Max | #N/A | WTRM. | GbxOilInletPres_10m_Max | Gear oil inlet pressure (max) | Getriebeöl-Eingangsdruck (max) | Presión de entrada de aceite del engranaje (max) | Ciśnienie na wlocie oleju przekładni (max) | Gear oil inlet pressure | bar | bar | Maximum | Double | 10 minute tag
WTRM.GbxOilInletPres_10m_Min | #N/A | WTRM. | GbxOilInletPres_10m_Min | Gear oil inlet pressure (min) | Getriebeöl-Eingangsdruck (min) | Presión de entrada de aceite del engranaje (min) | Ciśnienie na wlocie oleju przekładni (min) | Gear oil inlet pressure | bar | bar | Minimum | Double | 10 minute tag
WTRM.GbxOilInletPres_10m_Std | #N/A | WTRM. | GbxOilInletPres_10m_Std | Gear oil inlet pressure (std) | Getriebeöl-Eingangsdruck (std) | Presión de entrada de aceite del engranaje (std) | Ciśnienie na wlocie oleju przekładni (std) | Gear oil inlet pressure | bar | bar | Standard Deviation | Double | 10 minute tag
WTRM.GbxOilInLetTmp | #N/A | WTRM. | GbxOilInLetTmp | Gearbox Oil Inlet Temp | Getriebeöl-Eintrittstemperatur | Temperatura de entrada de aceite de la caja de cambios | Temp wlotu oleju w przekładni | Gearbox oil inlet temperature | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxOilInLetTmp_10m_Avg | #N/A | WTRM. | GbxOilInLetTmp_10m_Avg | Gearbox Oil Inlet Temp (avg) | Getriebeöl-Eintrittstemperatur (avg) | Temperatura de entrada de aceite de la caja de cambios (avg) | Temp wlotu oleju w przekładni (avg) | Gearbox oil inlet temperature | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxOilInLetTmp_10m_Max | #N/A | WTRM. | GbxOilInLetTmp_10m_Max | Gearbox Oil Inlet Temp (max) | Getriebeöl-Eintrittstemperatur (max) | Temperatura de entrada de aceite de la caja de cambios (max) | Temp wlotu oleju w przekładni (max) | Gearbox oil inlet temperature | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxOilInLetTmp_10m_Min | #N/A | WTRM. | GbxOilInLetTmp_10m_Min | Gearbox Oil Inlet Temp (min) | Getriebeöl-Eintrittstemperatur (min) | Temperatura de entrada de aceite de la caja de cambios (min) | Temp wlotu oleju w przekładni (min) | Gearbox oil inlet temperature | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxOilInLetTmp_10m_Std | #N/A | WTRM. | GbxOilInLetTmp_10m_Std | Gearbox Oil Inlet Temp (std) | Getriebeöl-Eintrittstemperatur (std) | Temperatura de entrada de aceite de la caja de cambios (std) | Temp wlotu oleju w przekładni (std) | Gearbox oil inlet temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.GbxOilInlFil | #N/A | WTRM. | GbxOilInlFil | Inline filter contamination | Verschmutzung des Inline-Filters | Contaminación del filtro en línea | Zanieczyszczenie filtra aktyw. | Inline filter contamination | bar | bar | Live Value | Double | Live Value
WTRM.GbxOilInlFil_10m_Avg | #N/A | WTRM. | GbxOilInlFil_10m_Avg | Inline filter contamination (avg) | Verschmutzung des Inline-Filters (avg) | Contaminación del filtro en línea (avg) | Zanieczyszczenie filtra aktyw. (avg) | Inline filter contamination | bar | bar | Average | Double | 10 minute tag
WTRM.GbxOilInlFil_10m_Max | #N/A | WTRM. | GbxOilInlFil_10m_Max | Inline filter contamination (max) | Verschmutzung des Inline-Filters (max) | Contaminación del filtro en línea (max) | Zanieczyszczenie filtra aktyw. (max) | Inline filter contamination | bar | bar | Maximum | Double | 10 minute tag
WTRM.GbxOilInlFil_10m_Min | #N/A | WTRM. | GbxOilInlFil_10m_Min | Inline filter contamination (min) | Verschmutzung des Inline-Filters (min) | Contaminación del filtro en línea (min) | Zanieczyszczenie filtra aktyw. (min) | Inline filter contamination | bar | bar | Minimum | Double | 10 minute tag
WTRM.GbxOilInlFil_10m_Std | #N/A | WTRM. | GbxOilInlFil_10m_Std | Inline filter contamination (std) | Verschmutzung des Inline-Filters (std) | Contaminación del filtro en línea (std) | Zanieczyszczenie filtra aktyw. (std) | Inline filter contamination | bar | bar | Standard Deviation | Double | 10 minute tag
WTRM.GbxOilInlFilSt | #N/A | WTRM. | GbxOilInlFilSt | Inline filter contamination Status | Verschmutzung des Inline-Filters Status | Estado de contaminación del filtro en línea | Stan zanieczyszczenia filtra aktyw. | Status of inline filter contamination | Enum | Enum | Live Value | Long | Live Value
WTRM.GbxOilLev | WTRM.GbxOilLev | WTRM. | GbxOilLev | Oil level in gearbox sump | Ölstand in der Getriebeölwanne | Nivel de aceite en el sumidero de la caja de cambios | Poziom oleju w miskachy przekładni | Oil level in gearbox sump | Enum | Enum | Live Value | Double
WTRM.GbxOilLevSt | #N/A | WTRM. | GbxOilLevSt | Oil level in gearbox sump Status | Ölstand in der Getriebeölwanne Status | Estado del nivel de aceite en el sumidero de la caja de cambios | Poziom oleju w przekładni Stan miski olejowej | Status of oil level in gearbox sump | Enum | Enum | Live Value | Long | Live Value
WTRM.GbxOilMetalParCnt | #N/A | WTRM. | GbxOilMetalParCnt | Gearbox Contamination | Verschmutzung des Getriebes | Contaminación de la caja de cambios | Zanieczyszczenie przekładni | Gearbox contamination, counts number of Metallic particles in the gearbox oil | count | Count | Live Value | Double | Live Value
WTRM.GbxOilMetalParCnt_10m_Avg | #N/A | WTRM. | GbxOilMetalParCnt_10m_Avg | Gearbox Contamination (avg) | Verschmutzung des Getriebes (avg) | Contaminación de la caja de cambios (avg) | Zanieczyszczenie przekładni (avg) | Gearbox contamination, counts number of Metallic particles in the gearbox oil | count | Count | Average | Double | 10 minute tag
WTRM.GbxOilMetalParCnt_10m_End | #N/A | WTRM. | GbxOilMetalParCnt_10m_End | Gearbox Contamination (end) | Verschmutzung des Getriebes (end) | Contaminación de la caja de cambios (end) | Zanieczyszczenie przekładni (end) | Gearbox contamination, counts number of Metallic particles in the gearbox oil | count | Count | Endvalue | Double | 10 minute tag
WTRM.GbxOilMetalParCnt_10m_Max | #N/A | WTRM. | GbxOilMetalParCnt_10m_Max | Gearbox Contamination (max) | Verschmutzung des Getriebes (max) | Contaminación de la caja de cambios (max) | Zanieczyszczenie przekładni (max) | Gearbox contamination, counts number of Metallic particles in the gearbox oil | count | Count | Maximum | Double | 10 minute tag
WTRM.GbxOilMetalParCnt_10m_Min | #N/A | WTRM. | GbxOilMetalParCnt_10m_Min | Gearbox Contamination (min) | Verschmutzung des Getriebes (min) | Contaminación de la caja de cambios (min) | Zanieczyszczenie przekładni (min) | Gearbox contamination, counts number of Metallic particles in the gearbox oil | count | Count | Minimum | Double | 10 minute tag
WTRM.GbxOilMetalParCnt_10m_Std | #N/A | WTRM. | GbxOilMetalParCnt_10m_Std | Gearbox Contamination (std) | Verschmutzung des Getriebes (std) | Contaminación de la caja de cambios (std) | Zanieczyszczenie przekładni (std) | Gearbox contamination, counts number of Metallic particles in the gearbox oil | count | Count | Standard Deviation | Double | 10 minute tag
WTRM.GbxOilOfFil | #N/A | WTRM. | GbxOilOfFil | Offline filter contamination | Verschmutzung des Nebenstromfilters | Contaminación del filtro sin conexión | Zanieczyszczenie filtra nieaktyw. | Offline filter contamination | Enum | Enum | Live Value | Double
WTRM.GbxOilOfFilInPres | #N/A | WTRM. | GbxOilOfFilInPres | Gearbox oil offline pressure after filter | Getriebeöl-Nebendruck nach dem Filter | Presión del aceite de la caja de cambios detrás del del filtro sin conexión | Ciśnienie oleju przekładni po filtrze | Gear oil offline pressure after filter | bar | bar | Live Value | Double | Live Value
WTRM.GbxOilOfFilOutPres | #N/A | WTRM. | GbxOilOfFilOutPres | Gearbox oil offline pressure before filter | Getriebeöl-Nebendruck vor dem Filter | Presión del aceite de la caja de cambios delante del del filtro sin conexión | Ciśnienie oleju przekładni przed filtrem | Gear oil offline pressure before filter | bar | bar | Live Value | Double | Live Value
WTRM.GbxOilOfFilPmpCnt_10m_End | #N/A | WTRM. | GbxOilOfFilPmpCnt_10m_End | Number of activations of the off-line filter pump (end) | Anzahl der Aktivierungen der Nebenstromfilterpumpe (end) | Número de activaciones de la bomba de filtro sin conexión (end) | Liczba aktywacji pompy filtra nieaktyw. (end) | Number of activations of the off-line filter pump | count | Count | Endvalue | Long | 10 minute tag
WTRM.GbxOilOfFilPmpSt | #N/A | WTRM. | GbxOilOfFilPmpSt | Gearbox oil pump Offline filtration | Getriebeölpumpe Nebenstromfiltration | Filtración de la bomba de aceite de la caja de cambios sin conexión | Pompa oleju przekładni Filtracja nieaktyw. | Feedback Offline filtration | Enum | Enum | Live Value | Double | Live Value
WTRM.GbxOilOfFilPmpTms_10m_End | #N/A | WTRM. | GbxOilOfFilPmpTms_10m_End | Time off-line filter pump has been activated (end) | Zeit, in der die Nebenstromfilterpumpe aktiviert wurde (end) | Tiempo que la bomba de filtro sin conexión ha estado activada (end) | Pompa filtra Time off-line została aktywowana (end) | Time off-line filter pump has been activated | s | seconds | Endvalue | Long | 10 minute tag
WTRM.GbxOilOfFilPres | #N/A | WTRM. | GbxOilOfFilPres | Gear oil filter after offline pressure | Getriebeölfilter nach Nebendruck | Filtro de aceite del engranaje después de presión sin conexión | Filtr oleju przekładni po nieaktyw. ciśnienie | Gear oil filter after offline pressure | bar | bar | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WTRM.GbxOilOfFilPres_10m_Avg | #N/A | WTRM. | GbxOilOfFilPres_10m_Avg | Gear oil filter after offline pressure (avg) | Getriebeölfilter nach Nebendruck (avg) | Filtro de aceite del engranaje después de presión sin conexión (avg) | Filtr oleju przekładni nieaktyw. ciśnienie (avg) | Gear oil filter after offline pressure | bar | bar | Average | Double | 10 minute tag
WTRM.GbxOilOfFilPres_10m_Max | #N/A | WTRM. | GbxOilOfFilPres_10m_Max | Gear oil filter after offline pressure (max) | Getriebeölfilter nach Nebendruck (max) | Filtro de aceite del engranaje después de presión sin conexión (max) | Filtr oleju przekładni nieaktyw. ciśnienie (max) | Gear oil filter after offline pressure | bar | bar | Maximum | Double | 10 minute tag
WTRM.GbxOilOfFilPres_10m_Min | #N/A | WTRM. | GbxOilOfFilPres_10m_Min | Gear oil filter after offline pressure (min) | Getriebeölfilter nach Nebendruck (min) | Filtro de aceite del engranaje después de presión sin conexión (min) | Filtr oleju przekładni nieaktyw. ciśnienie (min) | Gear oil filter after offline pressure | bar | bar | Minimum | Double | 10 minute tag
WTRM.GbxOilOfFilPres_10m_Std | #N/A | WTRM. | GbxOilOfFilPres_10m_Std | Gear oil filter after offline pressure (std) | Getriebeölfilter nach Nebendruck (std) | Filtro de aceite del engranaje después de presión sin conexión (std) | Filtr oleju przekładni nieaktyw. ciśnienie (std) | Gear oil filter after offline pressure | bar | bar | Standard Deviation | Double | 10 minute tag
WTRM.GbxOilOfFilSt | #N/A | WTRM. | GbxOilOfFilSt | Offline filter contamination Status | Nebenstromfilter Verschmutzung Status | Estado de contaminación del filtro sin conexión | Stan zanieczyszczenia filtra po wył. | Status of offline filter contamination | Enum | Enum | Live Value | Long | Live Value
WTRM.GbxOilOfFilTmp | #N/A | WTRM. | GbxOilOfFilTmp | Gear oil offline filter Temp | Getriebeöl Nebenstromfilter Temp | Temperatura del filtro de aceite del engranajesin conexión | Filtr oleju nieaktyw. przekładni Temp | Temperature gear oil offline filter | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxOilOutTmp | #N/A | WTRM. | GbxOilOutTmp | Gearbox Oil Temp After Heat Exchanger | Getriebeöltemperatur nach Wärmetauscher | Temperatura del aceite de la caja de cambios detrás del intercambiador de calor | Temp oleju przekładni po wymienniku ogrz. | Gearbox oil temperature after the heat exchanger | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxOilOutTmp_10m_Avg | #N/A | WTRM. | GbxOilOutTmp_10m_Avg | Gearbox Oil Temp After Heat Exchanger (avg) | Getriebeöltemperatur nach Wärmetauscher (avg) | Temperatura del aceite de la caja de cambios detrás del intercambiador de calor (avg) | Temp oleju przekładni po wymienniku ogrz. (avg) | Gearbox oil temperature after the heat exchanger | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxOilOutTmp_10m_Max | #N/A | WTRM. | GbxOilOutTmp_10m_Max | Gearbox Oil Temp After Heat Exchanger (max) | Getriebeöltemperatur nach Wärmetauscher (max) | Temperatura del aceite de la caja de cambios detrás del intercambiador de calor (max) | Temp oleju przekładni po wymienniku ogrz. (max) | Gearbox oil temperature after the heat exchanger | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxOilOutTmp_10m_Min | #N/A | WTRM. | GbxOilOutTmp_10m_Min | Gearbox Oil Temp After Heat Exchanger (min) | Getriebeöltemperatur nach Wärmetauscher (min) | Temperatura del aceite de la caja de cambios detrás del intercambiador de calor (min) | Temp oleju przekładni po wymienniku ogrz. (min) | Gearbox oil temperature after the heat exchanger | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxOilOutTmp_10m_Std | #N/A | WTRM. | GbxOilOutTmp_10m_Std | Gearbox Oil Temp After Heat Exchanger (std) | Getriebeöltemperatur nach Wärmetauscher (std) | Temperatura del aceite de la caja de cambios detrás del intercambiador de calor (std) | Temp oleju przekładni po wymienniku ogrz. (std) | Gearbox oil temperature after the heat exchanger | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.GbxOilPmpCnt | #N/A | WTRM. | GbxOilPmpCnt | Number of activations of the Gearbox oil pump | Anzahl der Aktivierungen der Getriebeölpumpe | Número de activaciones de la bomba de aceite de la caja de cambios | Liczba aktywacji pompy oleju przekładni | Number of activations of the Gearbox oil pump | count | Count | Total Counter | Long | Live Value
WTRM.GbxOilPmpCnt_10m_End | #N/A | WTRM. | GbxOilPmpCnt_10m_End | Number of activations of the Gearbox oil pump (end) | Anzahl der Aktivierungen der Getriebeölpumpe (end) | Número de activaciones de la bomba de aceite de la caja de cambios (end) | Liczba aktywacji pompy oleju przekładni (end) | Number of activations of the Gearbox oil pump | count | Count | Endvalue | Long | 10 minute tag
WTRM.GbxOilPmpSpd_10m_Avg | #N/A | WTRM. | GbxOilPmpSpd_10m_Avg | Gearbox Oil Pump RPM (avg) | Getriebeölpumpe Drehzahl (avg) | RPM de la bomba de aceite de la caja de cambios (avg) | Pompa oleju przekładni RPM (avg) | Gearbox oil pump speed | rpm | RPM | Average | Double | 10 minute tag
WTRM.GbxOilPmpSpd_10m_Max | #N/A | WTRM. | GbxOilPmpSpd_10m_Max | Gearbox Oil Pump RPM (max) | Getriebeölpumpe Drehzahl (max) | RPM de la bomba de aceite de la caja de cambios (max) | Pompa oleju przekładni RPM (max) | Gearbox oil pump speed | rpm | RPM | Maximum | Double | 10 minute tag
WTRM.GbxOilPmpSpd_10m_Min | #N/A | WTRM. | GbxOilPmpSpd_10m_Min | Gearbox Oil Pump RPM (min) | Getriebeölpumpe Drehzahl (min) | RPM de la bomba de aceite de la caja de cambios (min) | Pompa oleju przekładni RPM (min) | Gearbox oil pump speed | rpm | RPM | Minimum | Double | 10 minute tag
WTRM.GbxOilPmpSpd_10m_Std | #N/A | WTRM. | GbxOilPmpSpd_10m_Std | Gearbox Oil Pump RPM (std) | Getriebeölpumpe Drehzahl (std) | RPM de la bomba de aceite de la caja de cambios (std) | Pompa oleju przekładni RPM (std) | Gearbox oil pump speed | rpm | RPM | Standard Deviation | Double | 10 minute tag
WTRM.GbxOilPmpSt | #N/A | WTRM. | GbxOilPmpSt | Gearbox oil pump | Getriebeölpumpe | Bomba de aceite de la caja de cambios | Pompa oleju przekładni | Gear oil pump | Enum | Enum | Live Value | Double | Live Value
WTRM.GbxOilPmpTms | #N/A | WTRM. | GbxOilPmpTms | Time the Gearbox oil pump has been activated | Zeit, in der die Getriebeölpumpe aktiviert wurde | Tiempo que la bomba de aceite de la caja de cambios ha estado activada | Czas aktywacji pompy oleju przekładni | Time the Gearbox oil pump has been activated | s | seconds | Total Counter | Long | Live Value
WTRM.GbxOilPmpTms_10m_End | #N/A | WTRM. | GbxOilPmpTms_10m_End | Time the Gearbox oil pump has been activated (end) | Zeit, in der die Getriebeölpumpe aktiviert wurde (end) | Tiempo que la bomba de aceite de la caja de cambios ha estado activada (end) | Czas aktywacji pompy oleju przekładni (end) | Time the Gearbox oil pump has been activated | s | seconds | Endvalue | Long | 10 minute tag
WTRM.GbxOilPres | WTRM.GbxOilPres | WTRM. | GbxOilPres | Gearbox oil pressure | Getriebeöldruck | Presión de aceite de la caja de cambios | Ciśnienie oleju w przekładni | Gearbox oil pressure | bar | bar | Live Value | Double | Live Value
WTRM.GbxOilPres_10m_Avg | #N/A | WTRM. | GbxOilPres_10m_Avg | Gearbox oil pressure (avg) | Getriebeöldruck (avg) | Presión de aceite de la caja de cambios (avg) | Ciśnienie oleju w przekładni (avg) | Gearbox oil pressure | bar | bar | Average | Double | 10 minute tag | Rare tags for analysis
WTRM.GbxOilPres_10m_Max | #N/A | WTRM. | GbxOilPres_10m_Max | Gearbox oil pressure (max) | Getriebeöldruck (max) | Presión de aceite de la caja de cambios (max) | Ciśnienie oleju w przekładni (max) | Gearbox oil pressure | bar | bar | Maximum | Double | 10 minute tag | Rare tags for analysis
WTRM.GbxOilPres_10m_Min | #N/A | WTRM. | GbxOilPres_10m_Min | Gearbox oil pressure (min) | Getriebeöldruck (min) | Presión de aceite de la caja de cambios (min) | Ciśnienie oleju w przekładni (min) | Gearbox oil pressure | bar | bar | Minimum | Double | 10 minute tag | Rare tags for analysis
WTRM.GbxOilPres_10m_Std | #N/A | WTRM. | GbxOilPres_10m_Std | Gearbox oil pressure (std) | Getriebeöldruck (std) | Presión de aceite de la caja de cambios (std) | Ciśnienie oleju w przekładni (std) | Gearbox oil pressure | bar | bar | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WTRM.GbxOilPres1 | #N/A | WTRM. | GbxOilPres1 | Gearbox oil pressure at pump 1 | Getriebeöldruck an Pumpe 1 | Presión de aceite de la caja de cambios en la bomba 1 | Ciśnienie oleju w przekładni przy pompie 1 | Gearbox oil pressure at pump 1 | bar | bar | Live Value | Double | Live Value
WTRM.GbxOilPres1_10m_Avg | #N/A | WTRM. | GbxOilPres1_10m_Avg | Gearbox oil pressure at pump 1 (avg) | Getriebeöldruck an Pumpe 1 (avg) | Presión de aceite de la caja de cambios en la bomba 1 (avg) | Ciśnienie oleju w przekładni przy pompie 1 (avg) | Gearbox oil pressure at pump 1 | bar | bar | Average | Double | 10 minute tag
WTRM.GbxOilPres1_10m_Max | #N/A | WTRM. | GbxOilPres1_10m_Max | Gearbox oil pressure at pump 1 (max) | Getriebeöldruck an Pumpe 1 (max) | Presión de aceite de la caja de cambios en la bomba 1 (max) | Ciśnienie oleju w przekładni przy pompie 1 (max) | Gearbox oil pressure at pump 1 | bar | bar | Maximum | Double | 10 minute tag
WTRM.GbxOilPres1_10m_Min | #N/A | WTRM. | GbxOilPres1_10m_Min | Gearbox oil pressure at pump 1 (min) | Getriebeöldruck an Pumpe 1 (min) | Presión de aceite de la caja de cambios en la bomba 1 (min) | Ciśnienie oleju w przekładni przy pompie 1 (min) | Gearbox oil pressure at pump 1 | bar | bar | Minimum | Double | 10 minute tag
WTRM.GbxOilPres1_10m_Std | #N/A | WTRM. | GbxOilPres1_10m_Std | Gearbox oil pressure at pump 1 (std) | Getriebeöldruck an Pumpe 1 (std) | Presión de aceite de la caja de cambios en la bomba 1 (std) | Ciśnienie oleju w przekładni przy pompie 1 (std) | Gearbox oil pressure at pump 1 | bar | bar | Standard Deviation | Double | 10 minute tag
WTRM.GbxOilPres2 | #N/A | WTRM. | GbxOilPres2 | Gearbox oil pressure at pump 2 | Getriebeöldruck an Pumpe 2 | Presión de aceite de la caja de cambios en la bomba 2 | Ciśnienie oleju w przekładni przy pompie 2 | Gearbox oil pressure at pump 2 | bar | bar | Live Value | Double | Live Value
WTRM.GbxOilPres2_10m_Avg | #N/A | WTRM. | GbxOilPres2_10m_Avg | Gearbox oil pressure at pump 2 (avg) | Getriebeöldruck an Pumpe 2 (avg) | Presión de aceite de la caja de cambios en la bomba 2 (avg) | Ciśnienie oleju w przekładni przy pompie 2 (avg) | Gearbox oil pressure at pump 2 | bar | bar | Average | Double | 10 minute tag
WTRM.GbxOilPres2_10m_Max | #N/A | WTRM. | GbxOilPres2_10m_Max | Gearbox oil pressure at pump 2 (max) | Getriebeöldruck an Pumpe 2 (max) | Presión de aceite de la caja de cambios en la bomba 2 (max) | Ciśnienie oleju w przekładni przy pompie 2 (max) | Gearbox oil pressure at pump 2 | bar | bar | Maximum | Double | 10 minute tag
WTRM.GbxOilPres2_10m_Min | #N/A | WTRM. | GbxOilPres2_10m_Min | Gearbox oil pressure at pump 2 (min) | Getriebeöldruck an Pumpe 2 (min) | Presión de aceite de la caja de cambios en la bomba 2 (min) | Ciśnienie oleju w przekładni przy pompie 2 (min) | Gearbox oil pressure at pump 2 | bar | bar | Minimum | Double | 10 minute tag
WTRM.GbxOilPres2_10m_Std | #N/A | WTRM. | GbxOilPres2_10m_Std | Gearbox oil pressure at pump 2 (std) | Getriebeöldruck an Pumpe 2 (std) | Presión de aceite de la caja de cambios en la bomba 2 (std) | Ciśnienie oleju w przekładni przy pompie 2 (std) | Gearbox oil pressure at pump 2 | bar | bar | Standard Deviation | Double | 10 minute tag
WTRM.GbxOilTmp | WTRM.GbxOilTmp | WTRM. | GbxOilTmp | Gearbox Oil Temp | Getriebeöltemperatur | Temperatura de aceite de la caja de cambios | Temp oleju przekładni | Gearbox oil temperature | deg_c | °C | Live Value | Double | Live Value | Used in some specialised presentations
WTRM.GbxOilTmp_10m_Avg | #N/A | WTRM. | GbxOilTmp_10m_Avg | Gearbox Oil Temp (avg) | Getriebeöltemperatur (avg) | Temperatura de aceite de la caja de cambios (avg) | Temp oleju przekładni (avg) | Gearbox oil temperature | deg_c | °C | Average | Double | 10 minute tag | Common tags for analysis
WTRM.GbxOilTmp_10m_Max | #N/A | WTRM. | GbxOilTmp_10m_Max | Gearbox Oil Temp (max) | Getriebeöltemperatur (max) | Temperatura de aceite de la caja de cambios (max) | Temp oleju przekładni (max) | Gearbox oil temperature | deg_c | °C | Maximum | Double | 10 minute tag | Common tags for analysis
WTRM.GbxOilTmp_10m_Min | #N/A | WTRM. | GbxOilTmp_10m_Min | Gearbox Oil Temp (min) | Getriebeöltemperatur (min) | Temperatura de aceite de la caja de cambios (min) | Temp oleju przekładni (min) | Gearbox oil temperature | deg_c | °C | Minimum | Double | 10 minute tag | Common tags for analysis
WTRM.GbxOilTmp_10m_Std | #N/A | WTRM. | GbxOilTmp_10m_Std | Gearbox Oil Temp (std) | Getriebeöltemperatur (std) | Temperatura de aceite de la caja de cambios (std) | Temp oleju przekładni (std) | Gearbox oil temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WTRM.GbxOilTmp1 | #N/A | WTRM. | GbxOilTmp1 | Gearbox Oil Temp1 | Getriebeöltemperatur 1 | Temperatura 1 de aceite de la caja de cambios | Olej przekładni Temp1 | Gearbox oil temperature sensor 1 | deg_c | °C | Live Value | Double | Live Value | Used in some specialised presentations
WTRM.GbxOilTmp1_10m_Avg | #N/A | WTRM. | GbxOilTmp1_10m_Avg | Gearbox Oil Temp1 (avg) | Getriebeöltemperatur 1 (avg) | Temperatura 1 de aceite de la caja de cambios (avg) | Olej przekładni Temp1 (avg) | Gearbox oil temperature sensor 1 | deg_c | °C | Average | Double | 10 minute tag | Common tags for analysis
WTRM.GbxOilTmp1_10m_Max | #N/A | WTRM. | GbxOilTmp1_10m_Max | Gearbox Oil Temp1 (max) | Getriebeöltemperatur 1 (max) | Temperatura 1 de aceite de la caja de cambios (max) | Olej przekładni Temp1 (max) | Gearbox oil temperature sensor 1 | deg_c | °C | Maximum | Double | 10 minute tag | Common tags for analysis
WTRM.GbxOilTmp1_10m_Min | #N/A | WTRM. | GbxOilTmp1_10m_Min | Gearbox Oil Temp1 (min) | Getriebeöltemperatur 1 (min) | Temperatura 1 de aceite de la caja de cambios (min) | Olej przekładni Temp1 (min) | Gearbox oil temperature sensor 1 | deg_c | °C | Minimum | Double | 10 minute tag | Common tags for analysis
WTRM.GbxOilTmp1_10m_Std | #N/A | WTRM. | GbxOilTmp1_10m_Std | Gearbox Oil Temp1 (std) | Getriebeöltemperatur 1 (std) | Temperatura 1 de aceite de la caja de cambios (std) | Olej przekładni Temp1 (std) | Gearbox oil temperature sensor 1 | deg_c | °C | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WTRM.GbxOilTmp2 | #N/A | WTRM. | GbxOilTmp2 | Gearbox Oil Temp2 | Getriebeöltemperatur 2 | Temperatura 2 de aceite de la caja de cambios | Olej przekładni Temp2 | Gearbox oil temperature sensor 2 | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxOilTmp2_10m_Avg | #N/A | WTRM. | GbxOilTmp2_10m_Avg | Gearbox Oil Temp2 (avg) | Getriebeöltemperatur 2 (avg) | Temperatura 2 de aceite de la caja de cambios (avg) | Olej przekładni Temp2 (avg) | Gearbox oil temperature sensor 2 | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxOilTmp2_10m_Max | #N/A | WTRM. | GbxOilTmp2_10m_Max | Gearbox Oil Temp2 (max) | Getriebeöltemperatur 2 (max) | Temperatura 2 de aceite de la caja de cambios (max) | Olej przekładni Temp2 (max) | Gearbox oil temperature sensor 2 | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxOilTmp2_10m_Min | #N/A | WTRM. | GbxOilTmp2_10m_Min | Gearbox Oil Temp2 (min) | Getriebeöltemperatur 2 (min) | Temperatura 2 de aceite de la caja de cambios (min) | Olej przekładni Temp2 (min) | Gearbox oil temperature sensor 2 | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxOilTmp3 | #N/A | WTRM. | GbxOilTmp3 | Gearbox Oil Temp3 | Getriebeöltemperatur 3 | Temperatura 3 de aceite de la caja de cambios | Olej przekładni Temp3 | Gearbox oil temperature sensor 3 | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxOilTmp3_10m_Avg | #N/A | WTRM. | GbxOilTmp3_10m_Avg | Gearbox Oil Temp3 (avg) | Getriebeöltemperatur 3 (avg) | Temperatura 3 de aceite de la caja de cambios (avg) | Olej przekładni Temp3 (avg) | Gearbox oil temperature sensor 3 | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxOilTmp3_10m_Max | #N/A | WTRM. | GbxOilTmp3_10m_Max | Gearbox Oil Temp3 (max) | Getriebeöltemperatur 3 (max) | Temperatura 3 de aceite de la caja de cambios (max) | Olej przekładni Temp3 (max) | Gearbox oil temperature sensor 3 | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxOilTmp3_10m_Min | #N/A | WTRM. | GbxOilTmp3_10m_Min | Gearbox Oil Temp3 (min) | Getriebeöltemperatur 3 (min) | Temperatura 3 de aceite de la caja de cambios (min) | Olej przekładni Temp3 (min) | Gearbox oil temperature sensor 3 | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxStg1SwfSt | #N/A | WTRM. | GbxStg1SwfSt | Gearbox Stage 1 Swarf indicator | Getriebe Stufe 1 Späneanzeiger | Indicador de virutas de la fase 1 de la caja de cambios | Wskaźnik wiórów przekładni poz. 1 | Swarf indicator Gearbox Stage 1 | Enum | Enum | Live Value | Long | Live Value
WTRM.GbxStg2SwfSt | #N/A | WTRM. | GbxStg2SwfSt | Gearbox Stage 2 Swarf indicator | Getriebe Stufe 2 Späneanzeiger | Indicador de virutas de la fase 2 de la caja de cambios | Wskaźnik wiórów przekładni poz. 2 | Swarf indicator Gearbox Stage 2 | Enum | Enum | Live Value | Long | Live Value
WTRM.GbxStg3SwfSt | #N/A | WTRM. | GbxStg3SwfSt | Gearbox Stage 3 Swarf indicator | Getriebe Stufe 3 Späneanzeiger | Indicador de virutas de la fase 3 de la caja de cambios | Wskaźnik wiórów przekładni poz. 3 | Swarf indicator Gearbox Stage 3 | Enum | Enum | Live Value | Long | Live Value
WTRM.GbxTmp | #N/A | WTRM. | GbxTmp | Gearbox Temp | Getriebetemperatur | Temperatura de la caja de cambios | Temp przekładni | Gearbox temperature | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxTmp_10m_Avg | #N/A | WTRM. | GbxTmp_10m_Avg | Gearbox Temp (avg) | Getriebetemperatur (avg) | Temperatura de la caja de cambios (avg) | Temp przekładni (avg) | Gearbox temperature | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxTmp_10m_Max | #N/A | WTRM. | GbxTmp_10m_Max | Gearbox Temp (max) | Getriebetemperatur (max) | Temperatura de la caja de cambios (max) | Temp przekładni (max) | Gearbox temperature | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxTmp_10m_Min | #N/A | WTRM. | GbxTmp_10m_Min | Gearbox Temp (min) | Getriebetemperatur (min) | Temperatura de la caja de cambios (min) | Temp przekładni (min) | Gearbox temperature | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxTmp_10m_Std | #N/A | WTRM. | GbxTmp_10m_Std | Gearbox Temp (std) | Getriebetemperatur (std) | Temperatura de la caja de cambios (std) | Temp przekładni (std) | Gearbox temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.GbxVbr | WTRM.GbxVbr | WTRM. | GbxVbr | Vibration in the gearbox | Schwingung im Getriebe | Vibración en la caja de cambios | Wibracje w przekładni | Vibration in the gearbox |  |  | Live Value | Double
WTRM.GbxVbr_10m_Avg | #N/A | WTRM. | GbxVbr_10m_Avg | Gearbox vibration (avg) | Getriebeschwingung (avg) | Vibración de la caja de cambios (avg) | Wibracje przekładni (avg) | Vibration in the gearbox sensor |  |  | Average | Double | 10 minute tag
WTRM.GbxVbr_10m_Max | #N/A | WTRM. | GbxVbr_10m_Max | Gearbox vibration (max) | Getriebeschwingung (max) | Vibración de la caja de cambios (max) | Wibracje przekładni (max) | Vibration in the gearbox sensor |  |  | Maximum | Double | 10 minute tag
WTRM.GbxVbr_10m_Min | #N/A | WTRM. | GbxVbr_10m_Min | Gearbox vibration (min) | Getriebeschwingung (min) | Vibración de la caja de cambios (min) | Wibracje przekładni (min) | Vibration in the gearbox sensor |  |  | Minimum | Double | 10 minute tag
WTRM.GbxVbr_10m_Std | #N/A | WTRM. | GbxVbr_10m_Std | Gearbox vibration (std) | Getriebeschwingung (std) | Vibración de la caja de cambios (std) | Wibracje przekładni (std) | Vibration in the gearbox sensor |  |  | Standard Deviation | Double | 10 minute tag
WTRM.GbxVbr1_10m_Avg | #N/A | WTRM. | GbxVbr1_10m_Avg | Vibration in the gearbox sensor1 (avg) | Schwingungen im Getriebesensor1 (avg) | Vibración en el sensor 1 de la caja de cambios (avg) | Drgania w czujniku przekładni 1 (avg) | Vibration in the gearbox sensor1 |  |  | Average | Double | 10 minute tag
WTRM.GbxVbr1_10m_Max | #N/A | WTRM. | GbxVbr1_10m_Max | Vibration in the gearbox sensor1 (max) | Schwingungen im Getriebesensor1 (max) | Vibración en el sensor 1 de la caja de cambios (max) | Drgania w czujniku przekładni 1 (max) | Vibration in the gearbox sensor1 |  |  | Maximum | Double | 10 minute tag
WTRM.GbxVbr1_10m_Min | #N/A | WTRM. | GbxVbr1_10m_Min | Vibration in the gearbox sensor1 (min) | Schwingungen im Getriebesensor1 (min) | Vibración en el sensor 1 de la caja de cambios (min) | Drgania w czujniku przekładni 1 (min) | Vibration in the gearbox sensor1 |  |  | Minimum | Double | 10 minute tag
WTRM.GbxVbr1_10m_Std | #N/A | WTRM. | GbxVbr1_10m_Std | Vibration in the gearbox sensor1 (std) | Schwingungen im Getriebesensor1 (std) | Vibración en el sensor 1 de la caja de cambios (std) | Drgania w czujniku przekładni 1 (std) | Vibration in the gearbox sensor1 |  |  | Standard Deviation | Double | 10 minute tag
WTRM.GbxVbr2_10m_Avg | #N/A | WTRM. | GbxVbr2_10m_Avg | Vibration in the gearbox sensor2 (avg) | Schwingungen im Getriebesensor2 (avg) | Vibración en el sensor 2 de la caja de cambios (avg) | Drgania w czujniku przekładni 2 (avg) | Vibration in the gearbox sensor2 |  |  | Average | Double | 10 minute tag
WTRM.GbxVbr2_10m_Max | #N/A | WTRM. | GbxVbr2_10m_Max | Vibration in the gearbox sensor2 (max) | Schwingungen im Getriebesensor2 (max) | Vibración en el sensor 2 de la caja de cambios (max) | Drgania w czujniku przekładni 2 (max) | Vibration in the gearbox sensor2 |  |  | Maximum | Double | 10 minute tag
WTRM.GbxVbr2_10m_Min | #N/A | WTRM. | GbxVbr2_10m_Min | Vibration in the gearbox sensor2 (min) | Schwingungen im Getriebesensor2 (min) | Vibración en el sensor 2 de la caja de cambios (min) | Drgania w czujniku przekładni 2 (min) | Vibration in the gearbox sensor2 |  |  | Minimum | Double | 10 minute tag
WTRM.GbxVbr2_10m_Std | #N/A | WTRM. | GbxVbr2_10m_Std | Vibration in the gearbox sensor2 (std) | Schwingungen im Getriebesensor2 (std) | Vibración en el sensor 2 de la caja de cambios (std) | Drgania w czujniku przekładni 2 (std) | Vibration in the gearbox sensor2 |  |  | Standard Deviation | Double | 10 minute tag
WTRM.GbxWtrPmpCnt_10m_End | #N/A | WTRM. | GbxWtrPmpCnt_10m_End | Number of activations of Gearbox cooling water pump (end) | Anzahl der Aktivierungen der Kühlwasserpumpe des Getriebes (end) | Número de activaciones de la bomba de agua de refrigeración de la caja de cambios (end) | Liczba aktywacji pompy wody chłodzącej przekładni (end) | Number of activations of Gearbox cooling water pump | count | Count | Endvalue | Long | 10 minute tag
WTRM.GbxWtrPmpTms_10m_End | #N/A | WTRM. | GbxWtrPmpTms_10m_End | Time the Gearbox cooling water pump has been activated (end) | Zeit, in der die Kühlwasserpumpe des Getriebes aktiviert wurde (end) | Tiempo que la bomba de agua de refrigeración de la caja de cambios ha estado activada (end) | Czas aktywacji pompy wody chłodzącej przekładni (end) | Time the Gearbox cooling water pump has been activated | s | seconds | Endvalue | Long | 10 minute tag
WTRM.GsLev | WTRM.GsLev | WTRM. | GsLev | Grease level in the main bearing lubrication tank | Fettstand im Hauptlagerschmierbehälter | Nivel de grasa del depósito de lubricación del cojinete principal | Poziom smaru w zbiorniku smarowania łożyska głównego | Grease level in the main bearing lubrication tank | percent | percent | Live Value | Double | Live Value
WTRM.GsLev_10m_Avg | #N/A | WTRM. | GsLev_10m_Avg | Grease level in the main bearing lubrication tank (avg) | Fettstand im Hauptlagerschmierbehälter (avg) | Nivel de grasa del depósito de lubricación del cojinete principal (avg) | Poziom smaru w zbiorniku smarowania łożyska głównego (avg) | Grease level in the main bearing lubrication tank | percent | percent | Average | Double | 10 minute tag
WTRM.GsLev_10m_Max | #N/A | WTRM. | GsLev_10m_Max | Grease level in the main bearing lubrication tank (max) | Fettstand im Hauptlagerschmierbehälter (max) | Nivel de grasa del depósito de lubricación del cojinete principal (max) | Poziom smaru w zbiorniku smarowania łożyska głównego (max) | Grease level in the main bearing lubrication tank | percent | percent | Maximum | Double | 10 minute tag
WTRM.GsLev_10m_Min | #N/A | WTRM. | GsLev_10m_Min | Grease level in the main bearing lubrication tank (min) | Fettstand im Hauptlagerschmierbehälter (min) | Nivel de grasa del depósito de lubricación del cojinete principal (min) | Poziom smaru w zbiorniku smarowania łożyska głównego (min) | Grease level in the main bearing lubrication tank | percent | percent | Minimum | Double | 10 minute tag
WTRM.GsLev_10m_Std | #N/A | WTRM. | GsLev_10m_Std | Grease level in the main bearing lubrication tank (std) | Fettstand im Hauptlagerschmierbehälter (std) | Nivel de grasa del depósito de lubricación del cojinete principal (std) | Poziom smaru w zbiorniku smarowania łożyska głównego (std) | Grease level in the main bearing lubrication tank | percent | percent | Standard Deviation | Double | 10 minute tag
WTRM.GtyTnkPres | #N/A | WTRM. | GtyTnkPres | Gear oil gravity tank pressure | Getriebeöl Schwerkraft Tankdruck | Presión del tanque de gravedad de aceite del engranaje | Ciśnienie grawitacyjne w zbiorniku oleju przekładni | Gear oil gravity tank pressure | bar | bar | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WTRM.GtyTnkPres_10m_Avg | #N/A | WTRM. | GtyTnkPres_10m_Avg | Gear oil gravity tank pressure (avg) | Getriebeöl Schwerkraft Tankdruck (avg) | Presión del tanque de gravedad de aceite del engranaje (avg) | Ciśnienie grawitacyjne w zbiorniku oleju przekładni (avg) | Gear oil gravity tank pressure | bar | bar | Average | Double | 10 minute tag
WTRM.GtyTnkPres_10m_Max | #N/A | WTRM. | GtyTnkPres_10m_Max | Gear oil gravity tank pressure (max) | Getriebeöl Schwerkraft Tankdruck (max) | Presión del tanque de gravedad de aceite del engranaje (max) | Ciśnienie grawitacyjne w zbiorniku oleju przekładni (max) | Gear oil gravity tank pressure | bar | bar | Maximum | Double | 10 minute tag
WTRM.GtyTnkPres_10m_Min | #N/A | WTRM. | GtyTnkPres_10m_Min | Gear oil gravity tank pressure (min) | Getriebeöl Schwerkraft Tankdruck (min) | Presión del tanque de gravedad de aceite del engranaje (min) | Ciśnienie grawitacyjne w zbiorniku oleju przekładni (min) | Gear oil gravity tank pressure | bar | bar | Minimum | Double | 10 minute tag
WTRM.GtyTnkPres_10m_Std | #N/A | WTRM. | GtyTnkPres_10m_Std | Gear oil gravity tank pressure (std) | Getriebeöl Schwerkraft Tankdruck (std) | Presión del tanque de gravedad de aceite del engranaje (std) | Ciśnienie grawitacyjne w zbiorniku oleju przekładni (std) | Gear oil gravity tank pressure | bar | bar | Standard Deviation | Double | 10 minute tag
WTRM.HtSt | WTRM.HtSt | WTRM. | HtSt | Heating system Status | Status des Heizsystems | Estado del sistema de calefacción | Stan systemu grzewczego | Status of heating system | Enum | Enum | Live Value | Long | Live Value
WTRM.InlFil | WTRM.InlFil | WTRM. | InlFil | Inline filter contamination | Verschmutzung des Inline-Filters | Contaminación del filtro en línea | Zanieczyszczenie filtra aktyw. | Inline filter contamination | Enum | Enum | Live Value | Double | Live Value
WTRM.InlFil_10m_Avg | #N/A | WTRM. | InlFil_10m_Avg | Inline filter contamination (avg) | Verschmutzung des Inline-Filters (avg) | Contaminación del filtro en línea (avg) | Zanieczyszczenie filtra aktyw. (avg) | Inline filter contamination | Enum | Enum | Average | Double | 10 minute tag
WTRM.InlFil_10m_Max | #N/A | WTRM. | InlFil_10m_Max | Inline filter contamination (max) | Verschmutzung des Inline-Filters (max) | Contaminación del filtro en línea (max) | Zanieczyszczenie filtra aktyw. (max) | Inline filter contamination | Enum | Enum | Maximum | Double | 10 minute tag
WTRM.InlFil_10m_Min | #N/A | WTRM. | InlFil_10m_Min | Inline filter contamination (min) | Verschmutzung des Inline-Filters (min) | Contaminación del filtro en línea (min) | Zanieczyszczenie filtra aktyw. (min) | Inline filter contamination | Enum | Enum | Minimum | Double | 10 minute tag
WTRM.InlFil_10m_Std | #N/A | WTRM. | InlFil_10m_Std | Inline filter contamination (std) | Verschmutzung des Inline-Filters (std) | Contaminación del filtro en línea (std) | Zanieczyszczenie filtra aktyw. (std) | Inline filter contamination | Enum | Enum | Standard Deviation | Double | 10 minute tag
WTRM.LuSt | WTRM.LuSt | WTRM. | LuSt | Gearbox lubrication system Status | Status des Getriebeschmiersystems | Estado del sistema de lubricación de la caja de cambios | Stan układu smarowania przekładni | Status of gearbox lubrication system | Enum | Enum | Live Value | Long | Live Value
WTRM.MainBrgNRETmp | #N/A | WTRM. | MainBrgNRETmp | Main Bearing Non Rotor End Temp | Temperatur des Hauptlagers ohne Rotorende | Temperatura final del no rotor del cojinete principal | Łożysko główne Non Rotor End Temp | Main bearing temperature, i.e. Main bearing, in non rotor end | deg_c | °C | Live Value | Double | Live Value
WTRM.MainBrgNRETmp_10m_Avg | #N/A | WTRM. | MainBrgNRETmp_10m_Avg | Main Bearing Non Rotor End Temp (avg) | Temperatur des Hauptlagers ohne Rotorende (avg) | Temperatura final del no rotor del cojinete principal (avg) | Łożysko główne Non Rotor End Temp (avg) | Main bearing temperature, i.e. Main bearing, in non rotor end | deg_c | °C | Average | Double | 10 minute tag
WTRM.MainBrgNRETmp_10m_Max | #N/A | WTRM. | MainBrgNRETmp_10m_Max | Main Bearing Non Rotor End Temp (max) | Temperatur des Hauptlagers ohne Rotorende (max) | Temperatura final del no rotor del cojinete principal (max) | Łożysko główne Non Rotor End Temp (max) | Main bearing temperature, i.e. Main bearing, in non rotor end | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.MainBrgNRETmp_10m_Min | #N/A | WTRM. | MainBrgNRETmp_10m_Min | Main Bearing Non Rotor End Temp (min) | Temperatur des Hauptlagers ohne Rotorende (min) | Temperatura final del no rotor del cojinete principal (min) | Łożysko główne Non Rotor End Temp (min) | Main bearing temperature, i.e. Main bearing, in non rotor end | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.MainBrgNRETmp_10m_Std | #N/A | WTRM. | MainBrgNRETmp_10m_Std | Main Bearing Non Rotor End Temp (std) | Temperatur des Hauptlagers ohne Rotorende (std) | Temperatura final del no rotor del cojinete principal (std) | Łożysko główne Non Rotor End Temp (std) | Main bearing temperature, i.e. Main bearing, in non rotor end | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.MainBrgPmpCnt_10m_End | #N/A | WTRM. | MainBrgPmpCnt_10m_End | Number of activations of the main bearing pump (end) | Anzahl der Aktivierungen der Hauptlagerpumpe (end) | Número de activaciones de la bomba del cojinete principal (end) | Liczba aktywacji pompy łożyska głównego (end) | Number of activations of the main bearing pump | count | Count | Endvalue | Long | 10 minute tag
WTRM.MainBrgPmpTms_10m_End | #N/A | WTRM. | MainBrgPmpTms_10m_End | Time the main bearing pump has been activated (end) | Zeit, in der die Hauptlagerpumpe aktiviert wurde (end) | Tiempo que la bomba del cojinete principal ha estado activada (end) | Czas aktywacji pompy łożyska głównego (end) | Time the main bearing pump has been activated | s | seconds | Endvalue | Long | 10 minute tag
WTRM.MainBrgRETmp | #N/A | WTRM. | MainBrgRETmp | Main Bearing Rotor End Temp | Temperatur am Rotorende des Hauptlagers | Temperatura final del rotor del cojinete principal | Temp końcowa rotora łożyska głównego | Main bearing temperature, i.e. Main bearing, in rotor end | deg_c | °C | Live Value | Double | Live Value
WTRM.MainBrgRETmp_10m_Avg | #N/A | WTRM. | MainBrgRETmp_10m_Avg | Main Bearing Rotor End Temp (avg) | Temperatur am Rotorende des Hauptlagers (avg) | Temperatura final del rotor del cojinete principal (avg) | Temp końcowa rotora łożyska głównego (avg) | Main bearing temperature, i.e. Main bearing, in rotor end | deg_c | °C | Average | Double | 10 minute tag
WTRM.MainBrgRETmp_10m_Max | #N/A | WTRM. | MainBrgRETmp_10m_Max | Main Bearing Rotor End Temp (max) | Temperatur am Rotorende des Hauptlagers (max) | Temperatura final del rotor del cojinete principal (max) | Temp końcowa rotora łożyska głównego (max) | Main bearing temperature, i.e. Main bearing, in rotor end | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.MainBrgRETmp_10m_Min | #N/A | WTRM. | MainBrgRETmp_10m_Min | Main Bearing Rotor End Temp (min) | Temperatur am Rotorende des Hauptlagers (min) | Temperatura final del rotor del cojinete principal (min) | Temp końcowa rotora łożyska głównego (min) | Main bearing temperature, i.e. Main bearing, in rotor end | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.MainBrgRETmp_10m_Std | #N/A | WTRM. | MainBrgRETmp_10m_Std | Main Bearing Rotor End Temp (std) | Temperatur am Rotorende des Hauptlagers (std) | Temperatura final del rotor del cojinete principal (std) | Temp końcowa rotora łożyska głównego (std) | Main bearing temperature, i.e. Main bearing, in rotor end | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.MainBrgSwfSt | #N/A | WTRM. | MainBrgSwfSt | Main bearingSwarf indicator | Hauptlager Späneanzeige | Indicador de virutas del cojinete principal | Łożysko główneWzrusz wiórów | Swarf indicator Main bearings | Enum | Enum | Live Value | Long | Live Value
WTRM.MainBrgTmp | #N/A | WTRM. | MainBrgTmp | Main Bearing Temp | Hauptlager Temperatur | Temperatura del cojinete principal | Temp łożyska głównego | Main bearing temperature, i.e. the bearing carrying the rotor | deg_c | °C | Live Value | Double | Live Value
WTRM.MainBrgTmp_10m_Avg | #N/A | WTRM. | MainBrgTmp_10m_Avg | Main Bearing Temp (avg) | Hauptlager Temperatur (avg) | Temperatura del cojinete principal (avg) | Temp łożyska głównego (avg) | Main bearing temperature, i.e. the bearing carrying the rotor | deg_c | °C | Average | Double | 10 minute tag | Rare tags for analysis
WTRM.MainBrgTmp_10m_Max | #N/A | WTRM. | MainBrgTmp_10m_Max | Main Bearing Temp (max) | Hauptlager Temperatur (max) | Temperatura del cojinete principal (max) | Temp łożyska głównego (max) | Main bearing temperature, i.e. the bearing carrying the rotor | deg_c | °C | Maximum | Double | 10 minute tag | Rare tags for analysis
WTRM.MainBrgTmp_10m_Min | #N/A | WTRM. | MainBrgTmp_10m_Min | Main Bearing Temp (min) | Hauptlager Temperatur (min) | Temperatura del cojinete principal (min) | Temp łożyska głównego (min) | Main bearing temperature, i.e. the bearing carrying the rotor | deg_c | °C | Minimum | Double | 10 minute tag | Rare tags for analysis
WTRM.MainBrgTmp_10m_Std | #N/A | WTRM. | MainBrgTmp_10m_Std | Main Bearing Temp (std) | Hauptlager Temperatur (std) | Temperatura del cojinete principal (std) | Temp łożyska głównego (std) | Main bearing 1 temperature, i.e. the bearing carrying the rotor | deg_c | °C | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WTRM.MainBrgTmp1 | #N/A | WTRM. | MainBrgTmp1 | Main Bearing 1 Temp | Hauptlager 1 Temperatur | Temperatura del cojinete principal 1 | Łożysko główne 1 Temp | Main bearing 1 temperature, i.e. the bearing carrying the rotor | deg_c | °C | Live Value | Double | Live Value
WTRM.MainBrgTmp1_10m_Avg | #N/A | WTRM. | MainBrgTmp1_10m_Avg | Main Bearing 1 Temp (avg) | Hauptlager 1 Temperatur (avg) | Temperatura del cojinete principal 1 (avg) | Łożysko główne 1 Temp (avg) | Main bearing 1 temperature, i.e. the bearing carrying the rotor | deg_c | °C | Average | Double | 10 minute tag | Rare tags for analysis
WTRM.MainBrgTmp1_10m_Max | #N/A | WTRM. | MainBrgTmp1_10m_Max | Main Bearing 1 Temp (max) | Hauptlager 1 Temperatur (max) | Temperatura del cojinete principal 1 (max) | Łożysko główne 1 Temp (max) | Main bearing 1 temperature, i.e. the bearing carrying the rotor | deg_c | °C | Maximum | Double | 10 minute tag | Rare tags for analysis
WTRM.MainBrgTmp1_10m_Min | #N/A | WTRM. | MainBrgTmp1_10m_Min | Main Bearing 1 Temp (min) | Hauptlager 1 Temperatur (min) | Temperatura del cojinete principal 1 (min) | Łożysko główne 1 Temp (min) | Main bearing 1 temperature, i.e. the bearing carrying the rotor | deg_c | °C | Minimum | Double | 10 minute tag | Rare tags for analysis
WTRM.MainBrgTmp1_10m_Std | #N/A | WTRM. | MainBrgTmp1_10m_Std | Main Bearing 1 Temp (std) | Hauptlager 1 Temperatur (std) | Temperatura del cojinete principal 1 (std) | Łożysko główne 1 Temp (std) | Main bearing 1 temperature, i.e. the bearing carrying the rotor | deg_c | °C | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WTRM.MainBrgTmp2 | #N/A | WTRM. | MainBrgTmp2 | Main Bearing 2 Temp | Hauptlager 2 Temperatur | Temperatura del cojinete principal 2 | Łożysko główne 2 Temp | Main bearing 2 temperature, i.e. the bearing carrying the rotor | deg_c | °C | Live Value | Double | Live Value
WTRM.MainBrgTmp2_10m_Avg | #N/A | WTRM. | MainBrgTmp2_10m_Avg | Main Bearing 2 Temp (avg) | Hauptlager 2 Temperatur (avg) | Temperatura del cojinete principal 2 (avg) | Łożysko główne 2 Temp (avg) | Main bearing 2 temperature, i.e. the bearing carrying the rotor | deg_c | °C | Average | Double | 10 minute tag
WTRM.MainBrgTmp2_10m_Max | #N/A | WTRM. | MainBrgTmp2_10m_Max | Main Bearing 2 Temp (max) | Hauptlager 2 Temperatur (max) | Temperatura del cojinete principal 2 (max) | Łożysko główne 2 Temp (max) | Main bearing 2 temperature, i.e. the bearing carrying the rotor | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.MainBrgTmp2_10m_Min | #N/A | WTRM. | MainBrgTmp2_10m_Min | Main Bearing 2 Temp (min) | Hauptlager 2 Temperatur (min) | Temperatura del cojinete principal 2 (min) | Łożysko główne 2 Temp (min) | Main bearing 2 temperature, i.e. the bearing carrying the rotor | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.MainBrgTmp2_10m_Std | #N/A | WTRM. | MainBrgTmp2_10m_Std | Main Bearing 2 Temp (std) | Hauptlager 2 Temperatur (std) | Temperatura del cojinete principal 2 (std) | Łożysko główne 2 Temp (std) | Main bearing 2 temperature, i.e. the bearing carrying the rotor | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.MainTnkPres | #N/A | WTRM. | MainTnkPres | Gear oil main tank pressure | Druck im Haupttank des Getriebeöls | Presión del tanque principal de aceite del engranaje | Ciśnienie w zbiorniku głównym oleju przekładni | Gear oil main tank pressure | bar | bar | Live Value | Double | Live Value
WTRM.MainTnkPres_10m_Avg | #N/A | WTRM. | MainTnkPres_10m_Avg | Gear oil main tank pressure (avg) | Druck im Haupttank des Getriebeöls (avg) | Presión del tanque principal de aceite del engranaje (avg) | Ciśnienie w zbiorniku głównym oleju przekładni (avg) | Gear oil main tank pressure | bar | bar | Average | Double | 10 minute tag
WTRM.MainTnkPres_10m_Max | #N/A | WTRM. | MainTnkPres_10m_Max | Gear oil main tank pressure (max) | Druck im Haupttank des Getriebeöls (max) | Presión del tanque principal de aceite del engranaje (max) | Ciśnienie w zbiorniku głównym oleju przekładni (max) | Gear oil main tank pressure | bar | bar | Maximum | Double | 10 minute tag
WTRM.MainTnkPres_10m_Min | #N/A | WTRM. | MainTnkPres_10m_Min | Gear oil main tank pressure (min) | Druck im Haupttank des Getriebeöls (min) | Presión del tanque principal de aceite del engranaje (min) | Ciśnienie w zbiorniku głównym oleju przekładni (min) | Gear oil main tank pressure | bar | bar | Minimum | Double | 10 minute tag
WTRM.MainTnkPres_10m_Std | #N/A | WTRM. | MainTnkPres_10m_Std | Gear oil main tank pressure (std) | Druck im Haupttank des Getriebeöls (std) | Presión del tanque principal de aceite del engranaje (std) | Ciśnienie w zbiorniku głównym oleju przekładni (std) | Gear oil main tank pressure | bar | bar | Standard Deviation | Double | 10 minute tag
WTRM.RotSpd | #N/A | WTRM. | RotSpd | Gearbox RPM | Getriebedrehzahl | RPM de la caja de cambios | Obroty przekładni | Gearbox rotation speed generator shaft | rpm | RPM | Live Value | Double | Live Value
WTRM.RotSpd_10m_Avg | #N/A | WTRM. | RotSpd_10m_Avg | Gearbox RPM (avg) | Getriebedrehzahl (avg) | RPM de la caja de cambios (avg) | Obroty przekładni (avg) | Gearbox rotation speed generator shaft | rpm | RPM | Average | Double | 10 minute tag
WTRM.RotSpd_10m_Max | #N/A | WTRM. | RotSpd_10m_Max | Gearbox RPM (max) | Getriebedrehzahl (max) | RPM de la caja de cambios (max) | Obroty przekładni (max) | Gearbox rotation speed generator shaft | rpm | RPM | Maximum | Double | 10 minute tag
WTRM.RotSpd_10m_Min | #N/A | WTRM. | RotSpd_10m_Min | Gearbox RPM (min) | Getriebedrehzahl (min) | RPM de la caja de cambios (min) | Obroty przekładni (min) | Gearbox rotation speed generator shaft | rpm | RPM | Minimum | Double | 10 minute tag
WTRM.RotSpd_10m_Std | #N/A | WTRM. | RotSpd_10m_Std | Gearbox RPM (std) | Getriebedrehzahl (std) | RPM de la caja de cambios (std) | Obroty przekładni (std) | Gearbox rotation speed generator shaft | rpm | RPM | Standard Deviation | Double | 10 minute tag
WTRM.ShftBrkPmpCnt | #N/A | WTRM. | ShftBrkPmpCnt | Number of activations of the shaft brake pump | Anzahl der Aktivierungen der Wellenbremspumpe | Número de activaciones de la bomba de freno del eje | Liczba aktywacji pompy hamulca wału | Number of activations of the shaft brake pump | count | Count | Total Counter | Long | Live Value
WTRM.ShftBrkPmpCnt_10m_End | #N/A | WTRM. | ShftBrkPmpCnt_10m_End | Number of activations of the shaft brake pump (end) | Anzahl der Aktivierungen der Wellenbremspumpe (end) | Número de activaciones de la bomba de freno del eje (end) | Liczba aktywacji pompy hamulca wału (end) | Number of activations of the shaft brake pump | count | Count | Endvalue | Long | 10 minute tag
WTRM.ShftBrkPmpTms | #N/A | WTRM. | ShftBrkPmpTms | Time the shaft brake pump has been activated | Zeit, in der die Wellenbremspumpe aktiviert wurde | Tiempo que la bomba de freno del eje ha estado activada | Czas aktywacji pompy hamulca wału | Time the shaft brake pump has been activated | s | seconds | Total Counter | Long | Live Value
WTRM.ShftBrkPmpTms_10m_End | #N/A | WTRM. | ShftBrkPmpTms_10m_End | Time the shaft brake pump has been activated (end) | Zeit, in der die Wellenbremspumpe aktiviert wurde. (end) | Tiempo que la bomba de freno del eje ha estado activada (end) | Czas aktywacji pompy hamulca wału (end) | Time the shaft brake pump has been activated | s | seconds | Endvalue | Long | 10 minute tag
WTRM.ShftBrkTmp | WTRM.ShftBrkTmp | WTRM. | ShftBrkTmp | Generator Shaft Brake Temp | Generator-Wellenbremse Temperatur | Temperatura del freno del eje del generador | Temp hamulca wału generatora | Generator Shaft brake temperature | deg_c | °C | Live Value | Double | Live Value
WTRM.ShftBrkTmp_10m_Avg | #N/A | WTRM. | ShftBrkTmp_10m_Avg | Generator Shaft Brake Temp (avg) | Generator-Wellenbremse Temperatur (avg) | Temperatura del freno del eje del generador (avg) | Temp hamulca wału generatora (avg) | Generator Shaft brake temperature | deg_c | °C | Average | Double | 10 minute tag | Rare tags for analysis
WTRM.ShftBrkTmp_10m_Max | #N/A | WTRM. | ShftBrkTmp_10m_Max | Generator Shaft Brake Temp (max) | Generator-Wellenbremse Temperatur (max) | Temperatura del freno del eje del generador (max) | Temp hamulca wału generatora (max) | Generator Shaft brake temperature | deg_c | °C | Maximum | Double | 10 minute tag | Rare tags for analysis
WTRM.ShftBrkTmp_10m_Min | #N/A | WTRM. | ShftBrkTmp_10m_Min | Generator Shaft Brake Temp (min) | Generator-Wellenbremse Temperatur (min) | Temperatura del freno del eje del generador (min) | Temp hamulca wału generatora (min) | Generator Shaft brake temperature | deg_c | °C | Minimum | Double | 10 minute tag | Rare tags for analysis
WTRM.ShftBrkTmp_10m_Std | #N/A | WTRM. | ShftBrkTmp_10m_Std | Generator Shaft Brake Temp (std) | Generator-Wellenbremse Temperatur (std) | Temperatura del freno del eje del generador (std) | Temp hamulca wału generatora (std) | Generator Shaft brake temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag | Rare tags for analysis
WTRM.ShftBrkTnkPres | #N/A | WTRM. | ShftBrkTnkPres | Hydraulic pressure in accumulation tank for shaft brake | Hydraulikdruck im Akkumulationsbehälter für die Wellenbremse | Presión hidráulica en el tanque de acumulación para el freno del eje | Ciśnienie hydrauliczne w zbiorniku akumulacyjnym hamulca wału | Hydraulic pressure in accumulation tank for shaft brake | bar | bar | Live Value | Double | Live Value
WTRM.ShftBrkTnkPres_10m_Avg | #N/A | WTRM. | ShftBrkTnkPres_10m_Avg | Hydraulic pressure in accumulation tank for shaft brake (avg) | Hydraulikdruck im Akkumulationsbehälterfür die Wellenbremse (avg) | Presión hidráulica en el tanque de acumulación para el freno del eje (avg) | Ciśnienie hydrauliczne w zbiorniku akumulacyjnym hamulca wału (avg) | Hydraulic pressure in accumulation tank for shaft brake | bar | bar | Average | Double | 10 minute tag
WTRM.ShftBrkTnkPres_10m_Max | #N/A | WTRM. | ShftBrkTnkPres_10m_Max | Hydraulic pressure in accumulation tank for shaft brake (max) | Hydraulikdruck im Akkumulationsbehälter für die Wellenbremse (max) | Presión hidráulica en el tanque de acumulación para el freno del eje (max) | Ciśnienie hydrauliczne w zbiorniku akumulacyjnym hamulca wału (max) | Hydraulic pressure in accumulation tank for shaft brake | bar | bar | Maximum | Double | 10 minute tag
WTRM.ShftBrkTnkPres_10m_Min | #N/A | WTRM. | ShftBrkTnkPres_10m_Min | Hydraulic pressure in accumulation tank for shaft brake (min) | Hydraulikdruck im Akkumulationsbehälter für die Wellenbremse (min) | Presión hidráulica en el tanque de acumulación para el freno del eje (min) | Ciśnienie hydrauliczne w zbiorniku akumulacyjnym hamulca wału (min) | Hydraulic pressure in accumulation tank for shaft brake | bar | bar | Minimum | Double | 10 minute tag
WTRM.ShftBrkTnkPres_10m_Std | #N/A | WTRM. | ShftBrkTnkPres_10m_Std | Hydraulic pressure in accumulation tank for shaft brake (std) | Hydraulikdruck im Akkumulationsbehälter für die Wellenbremse (std) | Presión hidráulica en el tanque de acumulación para el freno del eje (std) | Ciśnienie hydrauliczne w zbiorniku akumulacyjnym hamulca wału (std) | Hydraulic pressure in accumulation tank for shaft brake | bar | bar | Standard Deviation | Double | 10 minute tag
WTRM.WtrPmpCnt_10m_End | #N/A | WTRM. | WtrPmpCnt_10m_End | Number of activations of cooling water pump (end) | Anzahl der Aktivierungen der Kühlwasserpumpe (end) | Número de activaciones de la bomba de agua de refrigeración (end) | Liczba aktywacji pompy wody chłodzącej (end) | Number of activations of cooling water pump | count | Count | Endvalue | Long | 10 minute tag
WTRM.WtrPmpTms_10m_End | #N/A | WTRM. | WtrPmpTms_10m_End | Time cooling water pump has been activated (end) | Zeit, in der die Kühlwasserpumpe aktiviert wurde (end) | Tiempo que la bomba de agua de refrigeración ha estado activada (end) | Pompa wody chłodzącej czas została aktywowana (end) | Time cooling water pump has been activated | s | seconds | Endvalue | Long | 10 minute tag
WTUR.AlmTms | #N/A | WTUR. | AlmTms | Time with an alarm | Zeit mit einem Alarm | Tiempo con una alarma | Czas z alarmem | Time with an alarm | s | seconds | Total Counter | Long | Live Value
WTUR.AlmTms_10m_End | #N/A | WTUR. | AlmTms_10m_End | Time with an alarm (end) | Zeit mit einem Alarm (end) | Tiempo con una alarma (end) | Czas z alarmem (end) | Time with an alarm | s | seconds | Endvalue | Long | 10 minute tag
WTUR.AlmTms_10m_Sum | #N/A | WTUR. | AlmTms_10m_Sum | Time with an alarm (sum) | Zeit mit einem Alarm (sum) | Tiempo con una alarma (sum) | Czas z alarmem (sum) | Time with an alarm | s | seconds | Summation | Long | 10 minute tag
WTUR.AlmTms_Dly_Sum | #N/A | WTUR. | AlmTms_Dly_Sum | Time with an alarm (sum) | Zeit mit einem Alarm (sum) | Tiempo con una alarma (sum) | Czas z alarmem (sum) | Time with an alarm in each Daily period i.e. 0-86400 seconds | s | seconds | Summation | Long | Daily tag
WTUR.AlmTms_Mly_Sum | #N/A | WTUR. | AlmTms_Mly_Sum | Time with an alarm (sum) | Zeit mit einem Alarm (sum) | Tiempo con una alarma (sum) | Czas z alarmem (sum) | Time with an alarm in each Monthly period i.e. 0-86400 seconds | s | seconds | Summation | Long | Monthly tag
WTUR.AvlTms_10m_End | #N/A | WTUR. | AvlTms_10m_End | Time that turbine is available to produce (end) | Zeit, die die Turbine für die Produktion zur Verfügung steht (end) | Tiempo que la turbina está disponible para producir (end) | Czas, w którym turbina jest dostępna do produkcji (end) | Time that turbine is available to produce | s | seconds | Endvalue | Long | 10 minute tag
WTUR.BstAct | #N/A | WTUR. | BstAct | Utilized power boost | Genutzter Leistungsschub | Aumento de potencia utilizado | Wykorzystanie zwiększenia mocy | Utilized power boost | Enum | Enum | Live Value | Long | Live Value
WTUR.BstAvl | #N/A | WTUR. | BstAvl | Power boost available | Verfügbarer Leistungsboost | Aumento de potencia disponible | Dostępne zwiększenie mocy | Power boost available | Enum | Enum | Live Value | Long | Live Value
WTUR.BstSt | #N/A | WTUR. | BstSt | Boost status | Boost-Status | Estado del aumento | Status Boost | Boost status | Enum | Enum | Live Value | Long | Live Value
WTUR.BstWh | #N/A | WTUR. | BstWh | Total accumulated boost energy | Gesamte akkumulierte Boost-Energie | Aumento de energía total acumulada | Całkowita zgromadzona energia doładowania | Accumulated boost energy, total | Wh | Wh | Live Value | Double | Live Value
WTUR.CapFact | #N/A | WTUR. | CapFact | Capacity factor | Kapazitätsfaktor | Factor de capacidad | Współczynnik wydajności | Capacity factor | percent | percent | Live Value | Double | Live Value
WTUR.CapFact_Dly_Sum | #N/A | WTUR. | CapFact_Dly_Sum | Capactity factor Daily (sum) | Kapazitätsfaktor Täglich (sum) | Factor de capacidad diario (sum) | Współczynnik wydajności Dziennie (sum) | Capactity factor in each Daily period | percent | percent | Summation | Double | Daily tag
WTUR.CapFact_Mly_Sum | #N/A | WTUR. | CapFact_Mly_Sum | Capactity factor Monthly (sum) | Kapazitätsfaktor Monatlich (sum) | Factor de capacidad mensual (sum) | Współczynnik wydajności miesięcznie (sum) | Capactity factor in each Monthly period | percent | percent | Summation | Double | Monthly tag
WTUR.CapFact_Yly_Sum | #N/A | WTUR. | CapFact_Yly_Sum | Capactity factor Yearly (sum) | Kapazitätsfaktor Jährlich (sum) | Factor de capacidad anual (sum) | Współczynnik wydajności rocznie (sum) | Capactity factor in each Yearly period | percent | percent | Summation | Double | Yearly tag
WTUR.CommErrTms | #N/A | WTUR. | CommErrTms | Time with communication SCADA lost | Zeit mit Ausfall der SCADA-Kommunikation | Tiempo con comunicación SCADA perdida | Czas bez komunikacji SCADA | Time during which the remote monitoring system has failed or computed data have been lost | s | seconds | Total Counter | Long | Live Value
WTUR.CommErrTms_Dly_Sum | #N/A | WTUR. | CommErrTms_Dly_Sum | Time with communication SCADA lost (sum) | Zeit mit Ausfall der SCADA-Kommunikation (sum) | Tiempo con comunicación SCADA perdida (sum) | Czas bez komunikacji SCADA (sum) | Time during which the remote monitoring system has failed or computed data have been lost | s | seconds | Summation | Long | Daily tag
WTUR.CstmStopSt | #N/A | WTUR. | CstmStopSt | Status for TDI-command | Status für TDI-Befehl | Estado para comando TDI | Stan polecenia TDI | Status for TDI-command Manual Stop Owner Coding:1= 1021(WTC3)/123003(STC1) is reset, 2= 1021(WTC3)/123003(STC1) is set where 1021(WTC3)/123003(STC1) is Manual Stop Owner | Enum | Enum | Live Value | Long | Live Value
WTUR.CstmStopTms | #N/A | WTUR. | CstmStopTms | Downtime due to customer stop | Ausfallzeit aufgrund von Kundenstopp | Tiempo de inactividad debido a parada del cliente | Przestój przez zatrzymanie Klienta | Downtime due to customer stop | s | seconds | Total Counter | Long | Live Value
WTUR.CstmStopTms_10m_End | #N/A | WTUR. | CstmStopTms_10m_End | Downtime due to customer stop (end) | Ausfallzeit aufgrund von Kundenstopp (end) | Tiempo de inactividad debido a parada del cliente (end) | Przestój przez zatrzymanie Klienta (end) | Downtime due to customer stop | s | seconds | Endvalue | Long | 10 minute tag
WTUR.CtlSt | #N/A | WTUR. | CtlSt | Remote control state | Status der remoten Regelung | Estado del control remoto | Stan zdalnego sterowania | remote control state. Whether turbine can be controlled from remote | Enum | Enum | Live Value | Long | Live Value
WTUR.CtlVer | #N/A | WTUR. | CtlVer | Turbine Controller Version | Version des Turbinenreglers | Versión del controlador de la turbina | Wersja sterownika turbiny | Turbine Controller Version | String | String | Live Value | String | Live Value
WTUR.DateTime | #N/A | WTUR. | DateTime | Turbine controller Date and Time | Turbinenregler Datum und Uhrzeit | Fecha y hora del controlador de la turbina | Data i godzina sterownika turbiny | Date and timestamp of the turbine controller | DateTime | DateTime | Live Value | DateTime | Live Value
WTUR.DateTimeDay | #N/A | WTUR. | DateTimeDay | Day | Tag | Día | Dzień | Turbine time Day | Enum | Enum | Live Value | Double | Live Value
WTUR.DateTimeHour | #N/A | WTUR. | DateTimeHour | Hour | Stunde | Hora | Godzina | Turbine time Hour | Enum | Enum | Live Value | Double | Live Value
WTUR.DateTimeMin | #N/A | WTUR. | DateTimeMin | Minute | Minute | Minuto | Minuta | Turbine time Minute | Enum | Enum | Live Value | Double | Live Value
WTUR.DateTimeMonth | #N/A | WTUR. | DateTimeMonth | Month | Monant | Mes | Miesiąc | Turbine time Month | Enum | Enum | Live Value | Double | Live Value
WTUR.DateTimeSec | #N/A | WTUR. | DateTimeSec | Second | Sekunde | Segundo | Sekunda | Turbine time Second | s | seconds | Live Value | Double | Live Value
WTUR.DateTimeYear | #N/A | WTUR. | DateTimeYear | Year | Jahr | Año | Rok | Turbine time Year | Enum | Enum | Live Value | Double | Live Value
WTUR.DmdIntWSpt | #N/A | WTUR. | DmdIntWSpt | Internal Active power setpoint | Interner Wirkleistungssollwert | Punto de ajuste de potencia activa interna | Wewnętrzna nastawa mocy czynnej | Internal Turbine active power generation setpoint | W | W | Setpoint | Double | Live Value
WTUR.DmdPFSpt | WTUR.DmdPFSpt | WTUR. | DmdPFSpt | Turbine Power factor setpoint | Turbinenleistungsfaktor Sollwert | Punto de ajuste del factor de potencia de turbina | Zadany współczynnik mocy turbiny | Turbine power factor setpoint | pf | Pf | Setpoint | Double | Live Value
WTUR.DmdPFSpt_10m_Avg | #N/A | WTUR. | DmdPFSpt_10m_Avg | Turbine Power factor setpoint (avg) | Turbinenleistungsfaktor Sollwert (avg) | Punto de ajuste del factor de potencia de turbina (avg) | Zadany współczynnik mocy turbiny (avg) | Turbine power factor setpoint | pf | Pf | Average | Double | 10 minute tag
WTUR.DmdPFSt | #N/A | WTUR. | DmdPFSt | Turbine power factor mode | Turbinenleistungsfaktor Modus | Modo del factor de potencia de turbina | Tryb współczynnika mocy turbiny | Turbine power factor mode | Enum | Enum | Live Value | Long | Live Value |  |  | New Vestas UA TAG
WTUR.DmdQPSpt | #N/A | WTUR. | DmdQPSpt | Turbine Q/P setpoint |  |  |  | Turbine Q/P setpoint | Enum | Enum | Setpoint | Double | Live Value
WTUR.DmdSpdSpt | #N/A | WTUR. | DmdSpdSpt | Turbine speed setpoint | Turbinendrehzahl Sollwert | Punto de ajuste de velocidad de turbina | Zadana prędkość obrotowa turbiny | Turbine speed set-point | rpm | RPM | Setpoint | Double | Live Value
WTUR.DmdSpdSpt_10m_Avg | #N/A | WTUR. | DmdSpdSpt_10m_Avg | Turbine speed setpoint (avg) | Turbinendrehzahl Sollwert (avg) | Punto de ajuste de velocidad de turbina (avg) | Zadana prędkość obrotowa turbiny (avg) | Turbine speed set-point | rpm | RPM | Average | Double | 10 minute tag
WTUR.DmdSpdSpt_10m_Max | #N/A | WTUR. | DmdSpdSpt_10m_Max | Turbine speed setpoint (max) | Turbinendrehzahl Sollwert (max) | Punto de ajuste de velocidad de turbina (max) | Zadana prędkość obrotowa turbiny (max) | Turbine speed set-point | rpm | RPM | Maximum | Double | 10 minute tag
WTUR.DmdSpdSpt_10m_Min | #N/A | WTUR. | DmdSpdSpt_10m_Min | Turbine speed setpoint (min) | Turbinendrehzahl Sollwert (min) | Punto de ajuste de velocidad de turbina (min) | Zadana prędkość obrotowa turbiny (min) | Turbine speed set-point | rpm | RPM | Minimum | Double | 10 minute tag
WTUR.DmdSpdSpt_10m_Std | #N/A | WTUR. | DmdSpdSpt_10m_Std | Turbine speed setpoint (std) | Turbinendrehzahl Sollwert (std) | Punto de ajuste de velocidad de turbina (std) | Zadana prędkość obrotowa turbiny (std) | Turbine speed set-point | rpm | RPM | Standard Deviation | Double | 10 minute tag
WTUR.DmdVArh | WTUR.DmdVArh | WTUR. | DmdVArh | Reactive energy demand | Blindenergiebedarf | Demanda de energía reactiva | Zapotrzebowanie na energię bierną | Reactive energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine) | VArh | VArh | Total Counter | Double | Live Value
WTUR.DmdVArh_10m_End | #N/A | WTUR. | DmdVArh_10m_End | Reactive energy demand (end) | Blindenergiebedarf (end) | Demanda de energía reactiva (end) | Zapotrzebowanie na energię bierną (end) | Reactive energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine) | VArh | VArh | Endvalue | Double | 10 minute tag | Needed for reports
WTUR.DmdVArh_10m_Sum | #N/A | WTUR. | DmdVArh_10m_Sum | Reactive energy demand (sum) | Blindenergiebedarf (sum) | Demanda de energía reactiva (sum) | Zapotrzebowanie na energię bierną (sum) | Reactive energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine) | VArh | VArh | Summation | Double | 10 minute tag | Needed for reports
WTUR.DmdVArh_Dly_End | #N/A | WTUR. | DmdVArh_Dly_End | Reactive energy demand (end) | Blindenergiebedarf (end) | Demanda de energía reactiva (end) | Zapotrzebowanie na energię bierną (end) | Reactive energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine) | VArh | VArh | Endvalue | Double | Daily tag
WTUR.DmdVArh_Dly_Sum | #N/A | WTUR. | DmdVArh_Dly_Sum | Reactive energy demand (sum) | Blindenergiebedarf (sum) | Demanda de energía reactiva (sum) | Zapotrzebowanie na energię bierną (sum) | Reactive energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine) | VArh | VArh | Summation | Double | Daily tag
WTUR.DmdVArh_Mly_Sum | #N/A | WTUR. | DmdVArh_Mly_Sum | Reactive energy demand (sum) | Blindenergiebedarf (sum) | Demanda de energía reactiva (sum) | Zapotrzebowanie na energię bierną (sum) | Reactive energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine) | VArh | VArh | Summation | Double | Monthly tag
WTUR.DmdVArh_Yly_Sum | #N/A | WTUR. | DmdVArh_Yly_Sum | Reactive energy demand (sum) | Blindenergiebedarf (sum) | Demanda de energía reactiva (sum) | Zapotrzebowanie na energię bierną (sum) | Reactive energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine) | VArh | VArh | Summation | Double | Yearly tag
WTUR.DmdVArSpt | WTUR.DmdVArSpt | WTUR. | DmdVArSpt | Turbine reactive power setpoint | Turbinenblindleistungssollwert | Punto de ajuste de potencia reactiva de turbina | Zadana moc bierna turbiny | Turbine reactive power generation setpoint | VAr | VAr | Setpoint | Double | Live Value
WTUR.DmdVArSpt_10m_Avg | #N/A | WTUR. | DmdVArSpt_10m_Avg | Turbine reactive power setpoint (avg) | Turbinenblindleistungssollwert (avg) | Punto de ajuste de potencia reactiva de turbina (avg) | Zadana moc bierna turbiny (avg) | Turbine reactive power generation setpoint | VAr | VAr | Average | Double | 10 minute tag
WTUR.DmdVArSpt_10m_Max | #N/A | WTUR. | DmdVArSpt_10m_Max | Turbine reactive power setpoint (max) | Turbinenblindleistungssollwert (max) | Punto de ajuste de potencia reactiva de turbina (max) | Zadana moc bierna turbiny (max) | Turbine reactive power generation setpoint | VAr | VAr | Maximum | Double | 10 minute tag
WTUR.DmdVArSpt_10m_Min | #N/A | WTUR. | DmdVArSpt_10m_Min | Turbine reactive power setpoint (min) | Turbinenblindleistungssollwert (min) | Punto de ajuste de potencia reactiva de turbina (min) | Zadana moc bierna turbiny (min) | Turbine reactive power generation setpoint | VAr | VAr | Minimum | Double | 10 minute tag
WTUR.DmdVArSpt_10m_Std | #N/A | WTUR. | DmdVArSpt_10m_Std | Turbine reactive power setpoint (std) | Turbinenblindleistungssollwert (std) | Punto de ajuste de potencia reactiva de turbina (std) | Zadana moc bierna turbiny (std) | Turbine reactive power generation setpoint | VAr | VAr | Standard Deviation | Double | 10 minute tag
WTUR.DmdVArSptSrc_10m_Avg | #N/A | WTUR. | DmdVArSptSrc_10m_Avg | Turbine reactive power setpoint soucre (avg) | Turbinenblindleistungssollwert Quelle (avg) | Fuente de punto de ajuste de potencia reactiva de turbina (avg) | Źródło zadanej mocy biernej turbiny (avg) | Turbine reactive power generation setpoint source | VAr | VAr | Average | Double | 10 minute tag
WTUR.DmdVArSrc | #N/A | WTUR. | DmdVArSrc | Turbine reactive power generation setpoint source | Quelle des Blindleistungserzeugungssollwerts der Turbine | Fuente del punto de ajuste de generación de potencia reactiva de la turbina | Źródło zadanej mocy biernej turbiny | Turbine reactive power generation setpoint source | Enum | Enum | Live Value | Long | Live Value |  |  | New Vestas UA TAG
WTUR.DmdVSpt | WTUR.DmdVSpt | WTUR. | DmdVSpt | Turbine Voltage setpoint | Turbinenspannung Sollwert | Punto de ajuste de tensión de turbina | Zadana Napięcie turbiny | Turbine voltage output setpoint | V | V | Setpoint | Double | Live Value
WTUR.DmdWh | WTUR.DmdWh | WTUR. | DmdWh | Active energy demand | Bedarf an Wirkenergie | Demanda de energía activa | Zapotrzebowanie na energię czynną | Active (real) energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine) | Wh | Wh | Total Counter | Double | Live Value
WTUR.DmdWh_10m_End | #N/A | WTUR. | DmdWh_10m_End | Active energy demand (end) | Bedarf an Wirkenergie (end) | Demanda de energía activa (end) | Zapotrzebowanie na energię czynną (end) | Active (real) energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine) | Wh | Wh | Endvalue | Double | 10 minute tag | Needed for reports
WTUR.DmdWh_10m_Sum | #N/A | WTUR. | DmdWh_10m_Sum | Active energy demand (sum) | Bedarf an Wirkenergie (sum) | Demanda de energía activa (sum) | Zapotrzebowanie na energię czynną (sum) | Active (real) energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine) | Wh | Wh | Summation | Double | 10 minute tag | Needed for reports
WTUR.DmdWh_Dly_End | #N/A | WTUR. | DmdWh_Dly_End | Active energy demand (end) | Bedarf an Wirkenergie (end) | Demanda de energía activa (end) | Zapotrzebowanie na energię czynną (end) | Active (real) energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine) | Wh | Wh | Endvalue | Double | 10 minute tag
WTUR.DmdWh_Dly_Sum | #N/A | WTUR. | DmdWh_Dly_Sum | Active energy demand (sum) | Bedarf an Wirkenergie (sum) | Demanda de energía activa (sum) | Zapotrzebowanie na energię czynną (sum) | Active (real) energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine) | Wh | Wh | Summation | Double | Daily tag
WTUR.DmdWh_Mly_End | #N/A | WTUR. | DmdWh_Mly_End | Active energy demand (end) | Bedarf an Wirkenergie (end) | Demanda de energía activa (end) | Zapotrzebowanie na energię czynną (end) | Active (real) energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine) | Wh | Wh | Endvalue | Double | 10 minute tag
WTUR.DmdWh_Mly_Sum | #N/A | WTUR. | DmdWh_Mly_Sum | Active energy demand (sum) | Bedarf an Wirkenergie (sum) | Demanda de energía activa (sum) | Zapotrzebowanie na energię czynną (sum) | Active (real) energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine) | Wh | Wh | Summation | Double | Monthly tag
WTUR.DmdWh_Yly_End | #N/A | WTUR. | DmdWh_Yly_End | Active energy demand (end) | Bedarf an Wirkenergie (end) | Demanda de energía activa (end) | Zapotrzebowanie na energię czynną (end) | Active (real) energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine) | Wh | Wh | Endvalue | Double | 10 minute tag
WTUR.DmdWh_Yly_Sum | #N/A | WTUR. | DmdWh_Yly_Sum | Active energy demand (sum) | Bedarf an Wirkenergie (sum) | Demanda de energía activa (sum) | Zapotrzebowanie na energię czynną (sum) | Active (real) energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine) | Wh | Wh | Summation | Double | Yearly tag
WTUR.DmdWSpt | WTUR.DmdWSpt | WTUR. | DmdWSpt | Active power setpoint | Wirkleistungssollwert | Punto de ajuste de potencia activa | Nastawa mocy czynnej | Turbine active power generation setpoint | W | W | Setpoint | Double | Live Value
WTUR.DmdWSpt_10m_Avg | #N/A | WTUR. | DmdWSpt_10m_Avg | Active power setpoint | Wirkleistungssollwert | Punto de ajuste de potencia activa | Nastawa mocy czynnej | Turbine active power generation setpoint, 10 min Avg | W | W | Setpoint | Double | 10 minute tag
WTUR.DmdWSpt_10m_End | #N/A | WTUR. | DmdWSpt_10m_End | Active power setpoint (end) | Wirkleistungssollwert (end) | Punto de ajuste de potencia activa (end) | Nastawa mocy czynnej (end) | Turbine active power generation setpoint, at end of 10 min period | W | W | Endvalue | Double | 10 minute tag
WTUR.DmdWSpt_10m_Max | #N/A | WTUR. | DmdWSpt_10m_Max | Active power setpoint | Wirkleistungssollwert | Punto de ajuste de potencia activa | Nastawa mocy czynnej | Turbine active power generation setpoint, 10 min Max | W | W | Setpoint | Double | 10 minute tag
WTUR.DmdWSpt_10m_Min | #N/A | WTUR. | DmdWSpt_10m_Min | Active power setpoint | Wirkleistungssollwert | Punto de ajuste de potencia activa | Nastawa mocy czynnej | Turbine active power generation setpoint, 10 min Min | W | W | Setpoint | Double | 10 minute tag
WTUR.DmdWSpt_10m_Std | #N/A | WTUR. | DmdWSpt_10m_Std | Active power setpoint | Wirkleistungssollwert | Punto de ajuste de potencia activa | Nastawa mocy czynnej | Turbine active power generation setpoint, 10 min Std | W | W | Setpoint | Double | 10 minute tag
WTUR.DmdWSptSrc_10m_Avg | #N/A | WTUR. | DmdWSptSrc_10m_Avg | Active power setpoint source (avg) | Quelle des Wirkleistungssollwerts (avg) | Fuente del punto de ajuste de potencia activa (avg) | Źródło zadanej mocy czynnej (avg) | Turbine active power generation setpoint source | W | W | Average | Double | 10 minute tag
WTUR.DmdWSrc | #N/A | WTUR. | DmdWSrc | Turbine active power generation setpoint source | Quelle des Wirkleistungssollwerts der Turbine | Fuente del punto de ajuste de generación de potencia activa de la turbina | Źródło zadanej mocy czynnej turbiny | Turbine active power generation setpoint source | Enum | Enum | Live Value | Long | Live Value |  |  | New Vestas UA TAG
WTUR.DnTms | #N/A | WTUR. | DnTms | Total downtime | Gesamtstillstandszeit | Inactividad total | Całkowity czas przestoju | Total downtime | s | seconds | Total Counter | Long | Live Value
WTUR.DnTms_10m_End | #N/A | WTUR. | DnTms_10m_End | Total downtime (end) | Gesamtstillstandszeit (end) | Inactividad total (end) | Całkowity czas przestoju (end) | Total downtime | s | seconds | Endvalue | Long | 10 minute tag
WTUR.DnTms_10m_Sum | #N/A | WTUR. | DnTms_10m_Sum | Total downtime (sum) | Gesamtstillstandszeit (sum) | Inactividad total (sum) | Całkowity czas przestoju (sum) | Total downtime in each 10 minute period i.e. 0-600 seconds | s | seconds | Summation | Long | 10 minute tag
WTUR.DnTms_Dly_Sum | #N/A | WTUR. | DnTms_Dly_Sum | Total downtime (sum) | Gesamtstillstandszeit (sum) | Inactividad total (sum) | Całkowity czas przestoju (sum) | Downtime in each Daily period i.e. 0-86400 seconds | s | seconds | Summation | Long | Daily tag
WTUR.DnTms_Mly_Sum | #N/A | WTUR. | DnTms_Mly_Sum | Total downtime (sum) | Gesamtstillstandszeit (sum) | Inactividad total (sum) | Całkowity czas przestoju (sum) | Downtime in each Monthly period | s | seconds | Summation | Long | Monthly tag
WTUR.DnTms_Yly_Sum | #N/A | WTUR. | DnTms_Yly_Sum | Total downtime (sum) | Gesamtstillstandszeit (sum) | Inactividad total (sum) | Całkowity czas przestoju (sum) | Downtime in each Yearly period | s | seconds | Summation | Long | Yearly tag
WTUR.EnvDnTms | #N/A | WTUR. | EnvDnTms | Downtime due to Ambient/Environment | Ausfallzeit aufgrund von Umgebung/Umwelt | Inactividad debido a ambiente/entorno | Przestoje spowodowane otoczeniem/środowiskiem | Downtime due to Ambient/Environment factors(e.g. high wind) | s | seconds | Total Counter | Long | Live Value
WTUR.EnvDnTms_10m_End | #N/A | WTUR. | EnvDnTms_10m_End | Downtime due to Ambient/Environment (end) | Ausfallzeit aufgrund von Umgebung/Umwelt (end) | Inactividad debido a ambiente/entorno (end) | Przestoje spowodowane otoczeniem/środowiskiem (end) | Downtime due to Ambient/Environment factors(e.g. high wind) | s | seconds | Endvalue | Long | 10 minute tag
WTUR.EnvDnTms_10m_Sum | #N/A | WTUR. | EnvDnTms_10m_Sum | Downtime due to Ambient/Environment (sum) | Ausfallzeit aufgrund von Umgebung/Umwelt (sum) | Inactividad debido a ambiente/entorno (sum) | Przestoje spowodowane otoczeniem/środowiskiem (sum) | Downtime due to Ambient/Environment factors(e.g. high wind) in each 10 minute period i.e. 0-600 seconds | s | seconds | Summation | Long | 10 minute tag | Needed for reports
WTUR.EnvDnTms_Dly_Sum | #N/A | WTUR. | EnvDnTms_Dly_Sum | Downtime due to Ambient/Environment (sum) | Ausfallzeit aufgrund von Umgebung/Umwelt (sum) | Inactividad debido a ambiente/entorno (sum) | Przestoje spowodowane otoczeniem/środowiskiem (sum) | Downtime due to Ambient/Environment factors(e.g. high wind) in each Daily period i.e. 0-86400 seconds | s | seconds | Summation | Long | Daily tag
WTUR.EnvDnTms_Mly_Sum | #N/A | WTUR. | EnvDnTms_Mly_Sum | Downtime due to Ambient/Environment (sum) | Ausfallzeit aufgrund von Umgebung/Umwelt (sum) | Inactividad debido a ambiente/entorno (sum) | Przestoje spowodowane otoczeniem/środowiskiem (sum) | Downtime due to Ambient/Environment factors(e.g. high wind) in each Monthly period | s | seconds | Summation | Long | Monthly tag
WTUR.EnvDnTms_Yly_Sum | #N/A | WTUR. | EnvDnTms_Yly_Sum | Downtime due to Ambient/Environment (sum) | Ausfallzeit aufgrund von Umgebung/Umwelt (sum) | Inactividad debido a ambiente/entorno (sum) | Przestoje spowodowane otoczeniem/środowiskiem (sum) | Downtime due to Ambient/Environment factors(e.g. high wind) in each Yearly period | s | seconds | Summation | Long | Yearly tag
WTUR.EnvOkTms | #N/A | WTUR. | EnvOkTms | Environment/Ambient Ok time | Umwelt/Umgebung Ok-Zeit | Tiempo de entorno/ambiente ok | Środowisko/Otoczenie Ok czas | Environment/Ambient Ok time | s | seconds | Total Counter | Long | Live Value
WTUR.EnvOkTms_10m_End | #N/A | WTUR. | EnvOkTms_10m_End | Environment/Ambient Ok time | Umwelt/Umgebung Ok-Zeit | Tiempo de entorno/ambiente ok | Środowisko/Otoczenie Ok czas | Environment/Ambient Ok time | s | seconds | Total Counter | Long | 10 minute tag
WTUR.EnvOkTms_10m_Sum | #N/A | WTUR. | EnvOkTms_10m_Sum | Environment/Ambient Ok time (sum) | Umwelt/Umgebung Ok-Zeit (sum) | Tiempo de entorno/ambiente ok (sum) | Środowisko/Otoczenie Ok czas (sum) | Environment/Ambient Ok time | s | seconds | Summation | Long | 10 minute tag
WTUR.EnvOkTms_Mly_Sum | #N/A | WTUR. | EnvOkTms_Mly_Sum | Environment/Ambient Ok time (sum) | Umwelt/Umgebung Ok-Zeit (sum) | Tiempo de entorno/ambiente ok (sum) | Środowisko/Otoczenie Ok czas (sum) | Environment/Ambient Ok time | s | seconds | Summation | Long | Monthly tag
WTUR.ExpW | #N/A | WTUR. | ExpW | ActivePowerOutPWC_kW | WirkleistungAusPWC_kW | ActivePowerOutPWC_kW | ActivePowerOutPWC_kW | Expected average power using 10-min average wind speed, based upon the WTG-processed 30 s power curve | W | W | Live Value | Double | Live Value
WTUR.ExpWh | #N/A | WTUR. | ExpWh | Expected active energy production | Erwartete Wirkenergieproduktion | Producción de energía activa esperada | Oczekiwana produkcja energii czynnej | Expected (net) active energy production i.e. produced-consumed energy | Wh | Wh | Total Counter | Double | Live Value
WTUR.ExpWh_10m_End | #N/A | WTUR. | ExpWh_10m_End | Expected active energy production (end) | Erwartete Wirkenergieproduktion (end) | Producción de energía activa esperada (end) | Oczekiwana produkcja energii czynnej (end) | Expected (net) active energy production i.e. produced-consumed energy | Wh | Wh | Endvalue | Double | 10 minute tag
WTUR.ExpWh_Dly_Sum | #N/A | WTUR. | ExpWh_Dly_Sum | Expected active energy production (sum) | Erwartete Wirkenergieproduktion (sum) | Producción de energía activa esperada (sum) | Oczekiwana produkcja energii czynnej (sum) | Expected (net) active energy production i.e. produced-consumed energy | Wh | Wh | Summation | Double | Daily tag
WTUR.ExpWh_Hly_Sum | #N/A | WTUR. | ExpWh_Hly_Sum | Expected active energy production (sum) | Erwartete Wirkenergieproduktion (sum) | Producción de energía activa esperada (sum) | Oczekiwana produkcja energii czynnej (sum) | Expected (net) active energy production i.e. produced-consumed energy | Wh | Wh | Summation | Double | Live Value
WTUR.ExpWh_Mly_Sum | #N/A | WTUR. | ExpWh_Mly_Sum | Expected active energy production (sum) | Erwartete Wirkenergieproduktion (sum) | Producción de energía activa esperada (sum) | Oczekiwana produkcja energii czynnej (sum) | Expected (net) active energy production i.e. produced-consumed energy | Wh | Wh | Summation | Double | Monthly tag
WTUR.ExpWh_Yly_Sum | #N/A | WTUR. | ExpWh_Yly_Sum | Expected active energy production (sum) | Erwartete Wirkenergieproduktion (sum) | Producción de energía activa esperada (sum) | Oczekiwana produkcja energii czynnej (sum) | Expected (net) active energy production i.e. produced-consumed energy | Wh | Wh | Summation | Double | Yearly tag
WTUR.ExpWRef | #N/A | WTUR. | ExpWRef | ActivePowerOutPWCSell_kW | WirkleistungAusPWCSell_kW | ActivePowerOutPWCSell_kW | ActivePowerOutPWCSell_kW | Expected average power using 10-min average wind speed, based upon the WTG-entered reference power curve | W | W | Live Value | Double | Live Value
WTUR.ExStopDnTms | #N/A | WTUR. | ExStopDnTms | Downtime due external stop | Ausfallzeit durch externen Stopp | Inactividad debido a parada externa | Przestój spowod. zatrzymaniem zewnętrznym | Downtime due external stop | s | seconds | Total Counter | Long | Live Value
WTUR.ExStopDnTms_10m_End | #N/A | WTUR. | ExStopDnTms_10m_End | Downtime due external stop (end) | Ausfallzeit durch externen Stopp (end) | Inactividad debido a parada externa (end) | Przestój spowod. zatrzymaniem zewnętrznym (end) | Downtime due external stop | s | seconds | Endvalue | Long | 10 minute tag
WTUR.ExStopDnTms_10m_Sum | #N/A | WTUR. | ExStopDnTms_10m_Sum | Downtime due external stop (sum) | Ausfallzeit durch externen Stopp (sum) | Inactividad debido a parada externa (sum) | Przestój spowod. zatrzymaniem zewnętrznym (sum) | Downtime due external stop in each 10 minute period i.e. 0-600 seconds | s | seconds | Summation | Long | 10 minute tag
WTUR.ExStopDnTms_Dly_Sum | #N/A | WTUR. | ExStopDnTms_Dly_Sum | Downtime due external stop (sum) | Ausfallzeit durch externen Stopp (sum) | Inactividad debido a parada externa (sum) | Przestój spowod. zatrzymaniem zewnętrznym (sum) | Downtime due external stop in each Daily period i.e. 0-86400 seconds | s | seconds | Summation | Long | Daily tag
WTUR.ExStopDnTms_Mly_Sum | #N/A | WTUR. | ExStopDnTms_Mly_Sum | Downtime due external stop (sum) | Ausfallzeit durch externen Stopp (sum) | Inactividad debido a parada externa (sum) | Przestój spowod. zatrzymaniem zewnętrznym (sum) | Downtime due external stop in each Monthly period | s | seconds | Summation | Long | Monthly tag
WTUR.ExStopDnTms_Yly_Sum | #N/A | WTUR. | ExStopDnTms_Yly_Sum | Downtime due external stop (sum) | Ausfallzeit durch externen Stopp (sum) | Inactividad debido a parada externa (sum) | Przestój spowod. zatrzymaniem zewnętrznym (sum) | Downtime due external stop in each Yearly period | s | seconds | Summation | Long | Yearly tag
WTUR.ExtPwrDnTms | #N/A | WTUR. | ExtPwrDnTms | Downtime due to external curtailment | Ausfallzeit durch externe Einschränkung | Inactividad debido a restricción externa | Przestój spowod. zewnętrznym ograniczeniem | Downtime due to external energy/power curtailment | s | seconds | Total Counter | Long | Live Value
WTUR.ExtPwrDnTms_10m_End | #N/A | WTUR. | ExtPwrDnTms_10m_End | Downtime due to external curtailment (end) | Ausfallzeit durch externe Einschränkung (end) | Inactividad debido a restricción externa (end) | Przestój spowod. zewnętrznym ograniczeniem (end) | Downtime due to external energy/power curtailment | s | seconds | Endvalue | Long | 10 minute tag
WTUR.GriErrDnTms | #N/A | WTUR. | GriErrDnTms | Downtime due to grid fault | Ausfallzeit aufgrund von Netzstörungen | Inactividad debido a fallo de la red eléctrica | Przestój spowod. awarią sieci | Downtime due to grid faults | s | seconds | Total Counter | Long | Live Value
WTUR.GriErrDnTms_10m_End | #N/A | WTUR. | GriErrDnTms_10m_End | Downtime due to grid fault (end) | Ausfallzeit aufgrund von Netzstörungen (end) | Inactividad debido a fallo de la red eléctrica (end) | Przestój spowod. awarią sieci (end) | Downtime due to grid faults | s | seconds | Endvalue | Long | 10 minute tag | Needed for reports
WTUR.GriErrDnTms_10m_Sum | #N/A | WTUR. | GriErrDnTms_10m_Sum | Downtime due to grid fault (sum) | Ausfallzeit aufgrund von Netzstörungen (sum) | Inactividad debido a fallo de la red eléctrica (sum) | Przestój spowod. awarią sieci (sum) | Downtime due to grid faults in each 10 minute period i.e. 0-600 seconds | s | seconds | Summation | Long | 10 minute tag | Needed for reports
WTUR.GriErrDnTms_Dly_Sum | #N/A | WTUR. | GriErrDnTms_Dly_Sum | Downtime due to grid fault (sum) | Ausfallzeit aufgrund von Netzstörungen (sum) | Inactividad debido a fallo de la red eléctrica (sum) | Przestój spowod. awarią sieci (sum) | Downtime due to grid faults in each Daily period i.e. 0-86400 seconds | s | seconds | Summation | Long | Daily tag
WTUR.GriErrDnTms_Mly_Sum | #N/A | WTUR. | GriErrDnTms_Mly_Sum | Downtime due to grid fault (sum) | Ausfallzeit aufgrund von Netzstörungen (sum) | Inactividad debido a fallo de la red eléctrica (sum) | Przestój spowod. awarią sieci (sum) | Downtime due to grid faults in each Monthly period | s | seconds | Summation | Long | Monthly tag
WTUR.GriErrDnTms_Yly_Sum | #N/A | WTUR. | GriErrDnTms_Yly_Sum | Downtime due to grid fault (sum) | Ausfallzeit aufgrund von Netzstörungen (sum) | Inactividad debido a fallo de la red eléctrica (sum) | Przestój spowod. awarią sieci (sum) | Downtime due to grid faults in each Yearly period | s | seconds | Summation | Long | Yearly tag
WTUR.GriOfTms | #N/A | WTUR. | GriOfTms | Time with no grid | Zeit ohne Netz | Tiempo sin la red eléctrica | Czas bez sieci | Time with no grid (missing grid) T3 | s | seconds | Total Counter | Long | Live Value
WTUR.GriOfTms_10m_End | #N/A | WTUR. | GriOfTms_10m_End | Time with no grid (end) | Zeit ohne Netz (end) | Tiempo sin la red eléctrica (end) | Czas bez sieci (end) | Time with no grid (missing grid) T3 | s | seconds | Endvalue | Long | 10 minute tag
WTUR.GriOkTms | #N/A | WTUR. | GriOkTms | Time grid Ok | Zeitnetz Ok | Tiempo de la red eléctrica ok | Czas sieć Ok | Time grid Ok | s | seconds | Total Counter | Long | Live Value
WTUR.GriOkTms_10m_End | #N/A | WTUR. | GriOkTms_10m_End | Time grid Ok (end) | Zeitnetz Ok (end) | Tiempo de la red eléctrica ok (end) | Czas sieć Ok (end) | Time grid Ok | s | seconds | Endvalue | Long | 10 minute tag
WTUR.GriOkTms_10m_Sum | #N/A | WTUR. | GriOkTms_10m_Sum | Time grid Ok (sum) | Zeitnetz Ok (sum) | Tiempo de la red eléctrica ok (sum) | Czas sieć Ok (sum) | Time grid Ok | s | seconds | Summation | Long | 10 minute tag
WTUR.GriOkTms_Dly_Sum | #N/A | WTUR. | GriOkTms_Dly_Sum | Time grid Ok (sum) | Zeitnetz Ok (sum) | Tiempo de la red eléctrica ok (sum) | Czas sieć Ok (sum) | Time grid Ok | s | seconds | Summation | Long | Daily tag
WTUR.GriOkTms_Mly_Sum | #N/A | WTUR. | GriOkTms_Mly_Sum | Time grid Ok (sum) | Zeitnetz Ok (sum) | Tiempo de la red eléctrica ok (sum) | Czas sieć Ok (sum) | Time grid Ok | s | seconds | Summation | Long | Monthly tag
WTUR.GriOnCnt_10m_End | #N/A | WTUR. | GriOnCnt_10m_End | Number of times power on (end) | Anzahl der Einschaltvorgänge (end) | Número de encendidos (end) | Liczba włączeń (end) | Number of times power on | count | Count | Endvalue | Long | 10 minute tag
WTUR.GriOnTms | #N/A | WTUR. | GriOnTms | Power On Time | Einschaltzeit | Tiempo de encendido | Czas włączenia | Time turbine (controller) has been connected to grid (Power on time) | s | seconds | Total Counter | Long | Live Value
WTUR.GriOnTms_10m_End | #N/A | WTUR. | GriOnTms_10m_End | Power On Time (end) | Einschaltzeit (end) | Tiempo de encendido (end) | Czas włączenia (end) | Time turbine (controller) has been connected to grid (Power on time) | s | seconds | Endvalue | Long | 10 minute tag
WTUR.GriOnTms_10m_Sum | #N/A | WTUR. | GriOnTms_10m_Sum | Power On Time (sum) | Einschaltzeit (sum) | Tiempo de encendido (sum) | Czas włączenia (sum) | Time turbine (controller) has been connected to grid (Power on time) | s | seconds | Summation | Long | 10 minute tag
WTUR.IceDnTms_10m_End | #N/A | WTUR. | IceDnTms_10m_End | Downtime due to Ice (end) | Ausfallzeit aufgrund von Eis (end) | Inactividad debido a hielo (end) | Przestój spowodowany lodem (end) | Downtime due to Ice | s | seconds | Endvalue | Long | 10 minute tag
WTUR.Id | #N/A | WTUR. | Id | Turbine node id | Turbinenknoten-ID | Id de nodo de turbina | Identyfikator węzła turbiny | Turbine node id | Enum | Enum | Live Value | Long | Live Value
WTUR.IntnW | #N/A | WTUR. | IntnW | Internal Active power | Interne Wirkleistung | Potencia activa interna | Wewnętrzna moc czynna | Internal power | W | W | Live Value | Double | Live Value
WTUR.IntnW_10m_Avg | #N/A | WTUR. | IntnW_10m_Avg | Internal Active power (avg) | Interne Wirkleistung (avg) | Potencia activa interna (avg) | Wewnętrzna moc czynna (avg) | Internal power | W | W | Average | Double | 10 minute tag
WTUR.IntnW_10m_Max | #N/A | WTUR. | IntnW_10m_Max | Internal Active power (max) | Interne Wirkleistung (max) | Potencia activa interna (max) | Wewnętrzna moc czynna (max) | Internal power | W | W | Maximum | Double | 10 minute tag
WTUR.IntnW_10m_Min | #N/A | WTUR. | IntnW_10m_Min | Internal Active power (min) | Interne Wirkleistung (min) | Potencia activa interna (min) | Wewnętrzna moc czynna (min) | Internal power | W | W | Minimum | Double | 10 minute tag
WTUR.IntnW_10m_Std | #N/A | WTUR. | IntnW_10m_Std | Internal Active power (std) | Interne Wirkleistung (std) | Potencia activa interna (std) | Wewnętrzna moc czynna (std) | Internal power | W | W | Standard Deviation | Double | 10 minute tag
WTUR.LsW | #N/A | WTUR. | LsW | Lost active power | Verlorene Wirkleistung | Pérdida de potencia activa | Utrata mocy czynnej | Lost active power | W | W | Live Value | Double | Live Value
WTUR.LsWh_Dly_Sum | #N/A | WTUR. | LsWh_Dly_Sum | Lost energy production (sum) | Verlorene Energieerzeugung (sum) | Pérdida de producción de energía (sum) | Utracona produkcja energii (sum) | Lost active energy in each Daily period | Wh | Wh | Summation | Double | Daily tag
WTUR.MainCBSt | #N/A | WTUR. | MainCBSt | Main circuit breaker position feedback | Rückmeldung der Stellung des Hauptleistungsschalters | Retroalimentación de posición de interruptor principal | Sprzężenie zwrotne położenia wyłącznika głównego | Main circuit breaker position feedback (open/closed) | Enum | Enum | Live Value | Long | Live Value
WTUR.MaxAvlExtW | #N/A | WTUR. | MaxAvlExtW | Maximum power external setpoints | Maximale Leistung externe Sollwerte | Puntos de ajuste externos de potencia máxima | Maksymalna moc zewnętrznych wartości zadanych | Maximum available active power, limited by external setpoints | W | W | Live Value | Double | Live Value |  |  | Enercon
WTUR.MaxAvlFmW | #N/A | WTUR. | MaxAvlFmW | Maximum power force majeure | Maximale Leistung Höhere Gewalt | Fuerza mayor potencia máxima | Maksymalna moc siła wyższa | Maximum available active power, limited by force majeure | W | W | Live Value | Double | Live Value |  |  | Enercon
WTUR.NoAlmTms | #N/A | WTUR. | NoAlmTms | Time with no active alarms | Zeit ohne aktive Alarme | Tiempo sin alarmas activas | Czas bez aktywnych alarmów | Time with no active alarms | s | seconds | Total Counter | Long | Live Value
WTUR.OpTms | #N/A | WTUR. | OpTms | Time in state Run | Zeit im Betriebsstatus | Tiempo con estado de funcionamiento | Czas w stanie Uruchom | Time in state Run (Operational) | s | seconds | Live Value | Long
WTUR.OpTms_10m_End | #N/A | WTUR. | OpTms_10m_End | Time in state Run (end) | Zeit im Betriebsstatus (end) | Tiempo con estado de funcionamiento (end) | Czas w stanie Uruchom (end) | Time in state Run (Operational) | s | seconds | Endvalue | Long | 10 minute tag
WTUR.OpTms_10m_Sum | #N/A | WTUR. | OpTms_10m_Sum | Time in state Run (sum) | Zeit im Betriebsstatus (sum) | Tiempo con estado de funcionamiento (sum) | Czas w stanie Uruchom (sum) | Time in state Run (Operational) | s | seconds | Summation | Long | 10 minute tag
WTUR.OpTms_Dly_Sum | #N/A | WTUR. | OpTms_Dly_Sum | Time in state Run (sum) | Zeit im Betriebsstatus (sum) | Tiempo con estado de funcionamiento (sum) | Czas w stanie Uruchom (sum) | Time in state Run (Operational) | s | seconds | Summation | Long | Daily tag
WTUR.OpTms_Mly_Sum | #N/A | WTUR. | OpTms_Mly_Sum | Time in state Run (sum) | Zeit im Betriebsstatus (sum) | Tiempo con estado de funcionamiento (sum) | Czas w stanie Uruchom (sum) | Time in state Run (Operational) | s | seconds | Summation | Long | Monthly tag
WTUR.PsblPFCap | #N/A | WTUR. | PsblPFCap | Possible capacity power factor | Möglicher kapazitiver Leistungsfaktor | Posible factor de potencia de capacidad | Możliwy współczynnik mocy pojemności | Possible capacity power factor | pf | pf | Live Value | Double | Live Value
WTUR.PsblPFInd | #N/A | WTUR. | PsblPFInd | Possible inductive power factor | Möglicher induktiver Leistungsfaktor | Posible factor de potencia inductiva | Możliwy współczynnik mocy indukcyjnej | Possible inductive power factor | pf | pf | Live Value | Double | Live Value
WTUR.PsblVArCap | #N/A | WTUR. | PsblVArCap | Possible capacity reactive power | Mögliche kapazitive Blindleistung | Posible potencia reactiva de capacidad | Możliwa pojemn. moc bierna | Possible capacity reactive power | VAr | VAr | Live Value | Double | Live Value
WTUR.PsblVArCap_10m_Avg | #N/A | WTUR. | PsblVArCap_10m_Avg | Possible capacity reactive power (avg) | Mögliche kapazitive Blindleistung (avg) | Posible potencia reactiva de capacidad (avg) | Możliwa pojemn. moc bierna (avg) | Possible capacity reactive power | VAr | VAr | Average | Double | 10 minute tag
WTUR.PsblVArCap_10m_Max | #N/A | WTUR. | PsblVArCap_10m_Max | Possible capacity reactive power (max) | Mögliche kapazitive Blindleistung (max) | Posible potencia reactiva de capacidad (max) | Możliwa pojemn. moc bierna (max) | Possible capacity reactive power | VAr | VAr | Maximum | Double | 10 minute tag
WTUR.PsblVArCap_10m_Min | #N/A | WTUR. | PsblVArCap_10m_Min | Possible capacity reactive power (min) | Mögliche kapazitive Blindleistung (min) | Posible potencia reactiva de capacidad (min) | Możliwa pojemn. moc bierna (min) | Possible capacity reactive power | VAr | VAr | Minimum | Double | 10 minute tag
WTUR.PsblVArCap_10m_Std | #N/A | WTUR. | PsblVArCap_10m_Std | Possible capacity reactive power (std) | Mögliche kapazitive Blindleistung (std) | Posible potencia reactiva de capacidad (std) | Możliwa pojemn. moc bierna (std) | Possible capacity reactive power | VAr | VAr | Standard Deviation | Double | 10 minute tag
WTUR.PsblVArInd | #N/A | WTUR. | PsblVArInd | Possible inductive reactive power | Mögliche induktive Blindleistung | Posible potencia reactiva inductiva | Możliwa indukc. moc bierna | Possible inductive reactive power | VAr | VAr | Live Value | Double | Live Value
WTUR.PsblVArInd_10m_Avg | #N/A | WTUR. | PsblVArInd_10m_Avg | Possible inductive reactive power (avg) | Mögliche induktive Blindleistung (avg) | Posible potencia reactiva inductiva (avg) | Możliwa indukc. moc bierna (avg) | Possible inductive reactive power | VAr | VAr | Average | Double | 10 minute tag
WTUR.PsblVArInd_10m_Max | #N/A | WTUR. | PsblVArInd_10m_Max | Possible inductive reactive power (max) | Mögliche induktive Blindleistung (max) | Posible potencia reactiva inductiva (max) | Możliwa indukc. moc bierna (max) | Possible inductive reactive power | VAr | VAr | Maximum | Double | 10 minute tag
WTUR.PsblVArInd_10m_Min | #N/A | WTUR. | PsblVArInd_10m_Min | Possible inductive reactive power (min) | Mögliche induktive Blindleistung (min) | Posible potencia reactiva inductiva (min) | Możliwa indukc. moc bierna (min) | Possible inductive reactive power | VAr | VAr | Minimum | Double | 10 minute tag
WTUR.PsblVArInd_10m_Std | #N/A | WTUR. | PsblVArInd_10m_Std | Possible inductive reactive power (std) | Mögliche induktive Blindleistung (std) | Posible potencia reactiva inductiva (std) | Możliwa indukc. moc bierna (std) | Possible inductive reactive power | VAr | VAr | Standard Deviation | Double | 10 minute tag
WTUR.PsblW | #N/A | WTUR. | PsblW | Possibly Active power | Möglicherweise Wirkleistung | Posible potencia activa | Możliwa Moc czynna | Possibly active power at grid connection | W | W | Live Value | Double | Live Value
WTUR.PsblW_10m_Avg | #N/A | WTUR. | PsblW_10m_Avg | Possibly Active power (avg) | Möglicherweise Wirkleistung (avg) | Posible potencia activa (avg) | Możliwa Moc czynna (avg) | Possibly active power at grid connection | W | W | Average | Double | 10 minute tag
WTUR.PsblW_10m_Max | #N/A | WTUR. | PsblW_10m_Max | Possibly Active power (max) | Möglicherweise Wirkleistung (max) | Posible potencia activa (max) | Możliwa Moc czynna (max) | Possibly active power at grid connection | W | W | Maximum | Double | 10 minute tag
WTUR.PsblW_10m_Min | #N/A | WTUR. | PsblW_10m_Min | Possibly Active power (min) | Möglicherweise Wirkleistung (min) | Posible potencia activa (min) | Możliwa Moc czynna (min) | Possibly active power at grid connection | W | W | Minimum | Double | 10 minute tag
WTUR.PsblW_10m_Std | #N/A | WTUR. | PsblW_10m_Std | Possibly Active power (std) | Möglicherweise Wirkleistung (std) | Posible potencia activa (std) | Możliwa Moc czynna (std) | Possibly active power at grid connection | W | W | Standard Deviation | Double | 10 minute tag
WTUR.PsblWLoc | #N/A | WTUR. | PsblWLoc | Possibly Active power | Möglicherweise Wirkleistung | Posible potencia activa | Możliwa Moc czynna | Available power based in local wind measurement | W | W | Live Value | Double | Live Value
WTUR.PsblWRaw | #N/A | WTUR. | PsblWRaw | Possibly Active power | Möglicherweise Wirkleistung | Posible potencia activa | Możliwa Moc czynna | Estimation of possible power production assuming no operational limitations | W | W | Live Value | Double | Live Value
WTUR.Q7CBSt | #N/A | WTUR. | Q7CBSt | Circuit breaker Q7 | Leitungsschutzschalter Q7 | Interruptor Q7 | Wyłącznik Q7 | Circuit breaker Q7 Open/Closed | Enum | Enum | Live Value | Long | Live Value
WTUR.Q8CBSt | #N/A | WTUR. | Q8CBSt | Main circuit breaker Q8 | Hauptstromkreisunterbrecher Q8 | Interruptor principal Q8 | Wyłącznik główny Q8 | Main circuit breaker Q8 Open/Closed | Enum | Enum | Live Value | Long | Live Value
WTUR.RdyTms | #N/A | WTUR. | RdyTms | Time turbine ready | Zeit, in der Turbine bereit ist | Tiempo de turbina lista | Czas Turbina gotowa do pracy | Time with turbine ready i.e. time turbine has been fault free, used for technical availability | s | seconds | Total Counter | Long | Live Value
WTUR.RdyTms_10m_End | #N/A | WTUR. | RdyTms_10m_End | Time turbine ready (end) | Zeit, in der Turbine bereit ist (end) | Tiempo de turbina lista (end) | Czas Turbina gotowa do pracy (end) | Time with turbine ready i.e. time turbine has been fault free, used for technical availability | s | seconds | Endvalue | Long | 10 minute tag | Needed for reports
WTUR.RdyTms_10m_Sum | #N/A | WTUR. | RdyTms_10m_Sum | Time turbine ready (sum) | Zeit, in der Turbine bereit ist (sum) | Tiempo de turbina lista (sum) | Czas Turbina gotowa do pracy (sum) | Time with turbine ready each 10 minute period i.e. time turbine has been fault free, used for technical availability i.e. 0-600 seconds | s | seconds | Summation | Long | 10 minute tag | Needed for reports
WTUR.RdyTms_Dly_Sum | #N/A | WTUR. | RdyTms_Dly_Sum | Time turbine ready (sum) | Zeit, in der Turbine bereit ist (sum) | Tiempo de turbina lista (sum) | Czas Turbina gotowa do pracy (sum) | Time with turbine ready each Daily period i.e. time turbine has been fault free, used for technical availability i.e. 0-86400 seconds | s | seconds | Summation | Long | Daily tag
WTUR.RdyTms_Mly_Sum | #N/A | WTUR. | RdyTms_Mly_Sum | Time turbine ready (sum) | Zeit, in der Turbine bereit ist (sum) | Tiempo de turbina lista (sum) | Czas Turbina gotowa do pracy (sum) | Time with turbine ready each Monthly period i.e. time turbine has been fault free, used for technical availability | s | seconds | Summation | Long | Monthly tag
WTUR.RefTms | #N/A | WTUR. | RefTms | Reference Time | Referenzzeit | Tiempo de referencia | Czas odniesienia | Time as measured by turbine. Should be Time since WTG controller was installed. (Power on time) | s | seconds | Total Counter | Long | Live Value
WTUR.RefTms_10m_End | #N/A | WTUR. | RefTms_10m_End | Reference Time (end) | Referenzzeit (end) | Tiempo de referencia (end) | Czas odniesienia (end) | Time as measured by turbine. Should be Time since WTG controller was installed. (Power on time) | s | seconds | Endvalue | Long | 10 minute tag
WTUR.RefTms_10m_Sum | #N/A | WTUR. | RefTms_10m_Sum | Reference Time (sum) | Referenzzeit (sum) | Tiempo de referencia (sum) | Czas odniesienia (sum) | Time as measured by turbine. Should be Time since WTG controller was installed. (Power on time) | s | seconds | Summation | Long | 10 minute tag
WTUR.RefTms_Dly_Sum | #N/A | WTUR. | RefTms_Dly_Sum | Reference Time (sum) | Referenzzeit (sum) | Tiempo de referencia (sum) | Czas odniesienia (sum) | Time as measured by turbine. Should be Time since WTG controller was installed. (Power on time) | s | seconds | Summation | Long | Daily tag
WTUR.RefTms_Mly_Sum | #N/A | WTUR. | RefTms_Mly_Sum | Reference Time (sum) | Referenzzeit (sum) | Tiempo de referencia (sum) | Czas odniesienia (sum) | Time as measured by turbine. Should be Time since WTG controller was installed. (Power on time) | s | seconds | Summation | Long | Monthly tag
WTUR.SmokAct | #N/A | WTUR. | SmokAct | Active Smoke alarm | Aktiv Rauchmelder | Alarma de incendios activa | Aktywny czujnik dymu | Active smoke alarm in turbine. 0 = No active smoke detector alarms, 1 = Active smoke detector alarms | Enum | Enum | Live Value | Long | Live Value
WTUR.SrvDnTms | #N/A | WTUR. | SrvDnTms | Downtime due to service | Ausfallzeit aufgrund von Wartungsarbeiten | Inactividad debido a servicio | Przestój spowodowany serwisem | Downtime due to service, i.e. scheduled maintenance | s | seconds | Total Counter | Long | Live Value
WTUR.SrvDnTms_10m_End | #N/A | WTUR. | SrvDnTms_10m_End | Downtime due to service (end) | Ausfallzeit aufgrund von Wartungsarbeiten (end) | Inactividad debido a servicio (end) | Przestój spowodowany serwisem (end) | Downtime due to service, i.e. scheduled maintenance | s | seconds | Endvalue | Long | 10 minute tag | Needed for reports
WTUR.SrvDnTms_10m_Sum | #N/A | WTUR. | SrvDnTms_10m_Sum | Downtime due to service (sum) | Ausfallzeit aufgrund von Wartungsarbeiten (sum) | Inactividad debido a servicio (sum) | Przestój spowodowany serwisem (sum) | Downtime due to due to service, i.e. scheduled maintenance in each 10 minute period i.e. 0-600 seconds | s | seconds | Summation | Long | 10 minute tag | Needed for reports
WTUR.SrvDnTms_Dly_Sum | #N/A | WTUR. | SrvDnTms_Dly_Sum | Downtime due to service (sum) | Ausfallzeit aufgrund von Wartungsarbeiten (sum) | Inactividad debido a servicio (sum) | Przestój spowodowany serwisem (sum) | Downtime due to due to service, i.e. scheduled maintenance in each Daily period i.e. 0-86400 seconds | s | seconds | Summation | Long | Daily tag
WTUR.SrvDnTms_Mly_Sum | #N/A | WTUR. | SrvDnTms_Mly_Sum | Downtime due to service (sum) | Ausfallzeit aufgrund von Wartungsarbeiten (sum) | Inactividad debido a servicio (sum) | Przestój spowodowany serwisem (sum) | Downtime due to due to service, i.e. scheduled maintenance in each Monthly period | s | seconds | Summation | Long | Monthly tag
WTUR.SrvDnTms_Yly_Sum | #N/A | WTUR. | SrvDnTms_Yly_Sum | Downtime due to service (sum) | Ausfallzeit aufgrund von Wartungsarbeiten (sum) | Inactividad debido a servicio (sum) | Przestój spowodowany serwisem (sum) | Downtime due to due to service, i.e. scheduled maintenance in each Yearly period | s | seconds | Summation | Long | Yearly tag
WTUR.SrvRpDnTms | #N/A | WTUR. | SrvRpDnTms | Downtime due to service repair jobs | Ausfallzeiten aufgrund von Reparaturarbeiten | Inactividad debido a labores de reparación | Przestój spowodowany naprawami serwisowymi | Downtime due to service repair jobs, i.e. unscheduled maintenance | s | seconds | Total Counter | Long | Live Value
WTUR.SrvRpDnTms_10m_End | #N/A | WTUR. | SrvRpDnTms_10m_End | Downtime due to service repair jobs (end) | Ausfallzeiten aufgrund von Reparaturarbeiten (end) | Inactividad debido a labores de reparación (end) | Przestój spowodowany naprawami serwisowymi (end) | Downtime due to service repair jobs, i.e. unscheduled maintenance | s | seconds | Endvalue | Long | 10 minute tag | Needed for reports
WTUR.SrvRpDnTms_10m_Sum | #N/A | WTUR. | SrvRpDnTms_10m_Sum | Downtime due to service repair jobs (sum) | Ausfallzeiten aufgrund von Reparaturarbeiten (sum) | Inactividad debido a labores de reparación (sum) | Przestój spowodowany naprawami serwisowymi (sum) | Downtime due to due to service repair jobs, i.e. unscheduled maintenance in each 10 minute period i.e. 0-600 seconds | s | seconds | Summation | Long | 10 minute tag | Needed for reports
WTUR.StopCnt | WTUR.StopCnt | WTUR. | StopCnt | Number of turbine stops (vendor-specific) | Anzahl der Turbinenstopps (herstellerspezifisch) | Número de paradas de la turbina (específica del proveedor) | Liczba zatrzymań turbiny (zależna od dostawcy) | Number of turbine stops (vendor-specific) | count | Count | Live Value | Long | Live Value
WTUR.StrCnt | WTUR.StrCnt | WTUR. | StrCnt | Number of turbine starts (vendor-specific) | Anzahl der Turbinenstarts (herstellerspezifisch) | Número de arranques de la turbina (específica del proveedor) | Liczba uruchomień turbiny (zależna od dostawcy) | Number of turbine starts (vendor-specific) | count | Count | Live Value | Long | Live Value
WTUR.SupVArh | WTUR.SupVArh | WTUR. | SupVArh | Reactive energy supply | Blindenergieversorgung | Suministro de energía reactiva | Energia bierna dostarczana | Reactive energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar) | VArh | VArh | Total Counter | Double | Live Value
WTUR.SupVArh_10m_End | #N/A | WTUR. | SupVArh_10m_End | Reactive energy supply (end) | Blindenergieversorgung (end) | Suministro de energía reactiva (end) | Energia bierna dostarczana (end) | Reactive energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar) | VArh | VArh | Endvalue | Double | 10 minute tag | Needed for reports
WTUR.SupVArh_10m_Sum | #N/A | WTUR. | SupVArh_10m_Sum | Reactive energy supply (sum) | Blindenergieversorgung (sum) | Suministro de energía reactiva (sum) | Energia bierna dostarczana (sum) | Reactive energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar) | VArh | VArh | Summation | Double | 10 minute tag | Needed for reports
WTUR.SupVArh_Dly_End | #N/A | WTUR. | SupVArh_Dly_End | Reactive energy supply (end) | Blindenergieversorgung (end) | Suministro de energía reactiva (end) | Energia bierna dostarczana (end) | Reactive energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar) | VArh | VArh | Endvalue | Double | Daily tag
WTUR.SupVArh_Dly_Sum | #N/A | WTUR. | SupVArh_Dly_Sum | Reactive energy supply (sum) | Blindenergieversorgung (sum) | Suministro de energía reactiva (sum) | Energia bierna dostarczana (sum) | Reactive energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar) | VArh | VArh | Summation | Double | Daily tag
WTUR.SupVArh_Mly_Sum | #N/A | WTUR. | SupVArh_Mly_Sum | Reactive energy supply (sum) | Blindenergieversorgung (sum) | Suministro de energía reactiva (sum) | Energia bierna dostarczana (sum) | Reactive energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar) | VArh | VArh | Summation | Double | Monthly tag
WTUR.SupVArh_Yly_Sum | #N/A | WTUR. | SupVArh_Yly_Sum | Reactive energy supply (sum) | Blindenergieversorgung (sum) | Suministro de energía reactiva (sum) | Energia bierna dostarczana (sum) | Reactive energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar) | VArh | VArh | Summation | Double | Yearly tag
WTUR.SupWh | WTUR.SupWh | WTUR. | SupWh | Active energy supplied | gelieferte Wirkenergie | Energía activa suministrada | Energia aktywna dostarczana | Active (real) energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar) | Wh | Wh | Total Counter | Double | Live Value
WTUR.SupWh_10m_End | #N/A | WTUR. | SupWh_10m_End | Active energy supplied (end) | gelieferte Wirkenergie (end) | Energía activa suministrada (end) | Energia aktywna dostarczana (end) | Active (real) energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar) | Wh | Wh | Endvalue | Double | 10 minute tag | Needed for reports | Used in standard Monitor presentation
WTUR.SupWh_10m_Sum | #N/A | WTUR. | SupWh_10m_Sum | Active energy supplied (sum) | gelieferte Wirkenergie (sum) | Energía activa suministrada (sum) | Energia aktywna dostarczana (sum) | Active (real) energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar) | Wh | Wh | Summation | Double | 10 minute tag | Needed for reports | Used in standard Monitor presentation
WTUR.SupWh_Dly_End | #N/A | WTUR. | SupWh_Dly_End | Active energy supplied (end) | gelieferte Wirkenergie (end) | Energía activa suministrada (end) | Energia aktywna dostarczana (end) | Active (real) energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar) | Wh | Wh | Endvalue | Double | 10 minute tag
WTUR.SupWh_Dly_Sum | #N/A | WTUR. | SupWh_Dly_Sum | Active energy supplied (sum) | gelieferte Wirkenergie (sum) | Energía activa suministrada (sum) | Energia aktywna dostarczana (sum) | Active (real) energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar) | Wh | Wh | Summation | Double | Daily tag
WTUR.SupWh_Mly_End | #N/A | WTUR. | SupWh_Mly_End | Active energy supplied (end) | gelieferte Wirkenergie (end) | Energía activa suministrada (end) | Energia aktywna dostarczana (end) | Active (real) energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar) | Wh | Wh | Endvalue | Double | 10 minute tag
WTUR.SupWh_Mly_Sum | #N/A | WTUR. | SupWh_Mly_Sum | Active energy supplied (sum) | gelieferte Wirkenergie (sum) | Energía activa suministrada (sum) | Energia aktywna dostarczana (sum) | Active (real) energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar) | Wh | Wh | Summation | Double | Monthly tag
WTUR.SupWh_Yly_End | #N/A | WTUR. | SupWh_Yly_End | Active energy supplied (end) | gelieferte Wirkenergie (end) | Energía activa suministrada (end) | Energia aktywna dostarczana (end) | Active (real) energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar) | Wh | Wh | Endvalue | Double | 10 minute tag
WTUR.SupWh_Yly_Sum | #N/A | WTUR. | SupWh_Yly_Sum | Active energy supplied (sum) | gelieferte Wirkenergie (sum) | Energía activa suministrada (sum) | Energia aktywna dostarczana (sum) | Active (real) energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar) | Wh | Wh | Summation | Double | Yearly tag
WTUR.SvcSt | #N/A | WTUR. | SvcSt | Service State | Service Status | Estado de servicio | Stan usługi | Service state value (0= Service not active 1 = Normal Service active, 2 = Extended Service active) | Enum | Enum | Live Value | Long | Live Value |  |  | New Vestas UA TAG
WTUR.TechAvlW | #N/A | WTUR. | TechAvlW | Technically power | Technische Leistung | Potencia técnica | Moc techniczna | Technically available active power | W | W | Live Value | Double | Live Value |  |  | Enercon
WTUR.TheoAvlW | #N/A | WTUR. | TheoAvlW | Theoretically power | Theoretische Leistung | Potencia teórica | Moc teoretyczna | Theoretically available active power | W | W | Live Value | Double | Live Value |  |  | Enercon
WTUR.TmZnOfs | #N/A | WTUR. | TmZnOfs | Offset from UTC | Abweichung von UTC | Compensación a partir de UTC | Przesunięcie od UTC | Offset from UTC time in minutes | s | seconds | Live Value | Double | Live Value
WTUR.TotTmsRsTms | #N/A | WTUR. | TotTmsRsTms | Reset time of total hour counters | Rückstellzeit der Gesamtstundenzähler | Restablecer el tiempo de los contadores de horas totales | Resetowanie liczników czasu całkowitej liczby godzin | Reset time of total hour counters | DateTime | DateTime | Live Value | DateTime | Live Value
WTUR.TotVArh | WTUR.TotVArh | WTUR. | TotVArh | Total reactive energy production | Gesamte Blindenergieerzeugung | Producción total de energía reactiva | Całkowita produkcja energii biernej | Total (net) reactive energy production i.e. produced-consumed reactive energy | VArh | VArh | Total Counter | Double | Live Value
WTUR.TotVArh_10m_End | #N/A | WTUR. | TotVArh_10m_End | Total reactive energy production (end) | Gesamte Blindenergieerzeugung (end) | Producción total de energía reactiva (end) | Całkowita produkcja energii biernej (end) | Total (net) reactive energy production i.e. produced-consumed reactive energy | VArh | VArh | Endvalue | Double | 10 minute tag
WTUR.TotVArh_10m_Sum | #N/A | WTUR. | TotVArh_10m_Sum | Total reactive energy production (sum) | Gesamte Blindenergieerzeugung (sum) | Producción total de energía reactiva (sum) | Całkowita produkcja energii biernej (sum) | Total (net) reactive energy production i.e. produced-consumed reactive energy | VArh | VArh | Summation | Double | 10 minute tag
WTUR.TotVArh_Dly_Sum | #N/A | WTUR. | TotVArh_Dly_Sum | Total reactive energy production (sum) | Gesamte Blindenergieerzeugung (sum) | Producción total de energía reactiva (sum) | Całkowita produkcja energii biernej (sum) | Total (net) reactive energy production i.e. produced-consumed reactive energy | VArh | VArh | Summation | Double | 10 minute tag
WTUR.TotVArh_Mly_Sum | #N/A | WTUR. | TotVArh_Mly_Sum | Total reactive energy production (sum) | Gesamte Blindenergieerzeugung (sum) | Producción total de energía reactiva (sum) | Całkowita produkcja energii biernej (sum) | Total (net) reactive energy production i.e. produced-consumed reactive energy | VArh | VArh | Summation | Double | Monthly tag
WTUR.TotVArh_Yly_Sum | #N/A | WTUR. | TotVArh_Yly_Sum | Total reactive energy production (sum) | Gesamte Blindenergieerzeugung (sum) | Producción total de energía reactiva (sum) | Całkowita produkcja energii biernej (sum) | Total (net) reactive energy production i.e. produced-consumed reactive energy | VArh | VArh | Summation | Double | Yearly tag
WTUR.TotWh | WTUR.TotWh | WTUR. | TotWh | Total active energy production | Gesamte Wirkenergieerzeugung | Producción total de energía activa | Całkowita produkcja energii czynnej | Total (net) active energy production i.e. produced-consumed energy | Wh | Wh | Total Counter | Double | Live Value | Used in standard monitor Presentation
WTUR.TotWh_10m_End | #N/A | WTUR. | TotWh_10m_End | Total active energy production (end) | Gesamte Wirkenergieerzeugung (end) | Producción total de energía activa (end) | Całkowita produkcja energii czynnej (end) | Total (net) active energy production i.e. produced-consumed energy | Wh | Wh | Endvalue | Double | 10 minute tag | Needed for reports
WTUR.TotWh_10m_Sum | #N/A | WTUR. | TotWh_10m_Sum | Total active energy production (sum) | Gesamte Wirkenergieerzeugung (sum) | Producción total de energía activa (sum) | Całkowita produkcja energii czynnej (sum) | Total (net) active energy production i.e. produced-consumed energy | Wh | Wh | Summation | Double | 10 minute tag | Needed for reports
WTUR.TotWh_Dly_End | #N/A | WTUR. | TotWh_Dly_End | Total active energy production (end) | Gesamte Wirkenergieerzeugung (end) | Producción total de energía activa (end) | Całkowita produkcja energii czynnej (end) | Total (net) active energy production i.e. produced-consumed energy | Wh | Wh | Endvalue | Double | 10 minute tag
WTUR.TotWh_Dly_Sum | #N/A | WTUR. | TotWh_Dly_Sum | Total active energy production (sum) | Gesamte Wirkenergieerzeugung (sum) | Producción total de energía activa (sum) | Całkowita produkcja energii czynnej (sum) | Total (net) active energy production i.e. produced-consumed energy | Wh | Wh | Summation | Double | Daily tag
WTUR.TotWh_Hly_Sum | #N/A | WTUR. | TotWh_Hly_Sum | Total active energy production (sum) | Gesamte Wirkenergieerzeugung (sum) | Producción total de energía activa (sum) | Całkowita produkcja energii czynnej (sum) | Total (net) active energy production i.e. produced-consumed energy | Wh | Wh | Summation | Double | Live Value
WTUR.TotWh_Mly_End | #N/A | WTUR. | TotWh_Mly_End | Total active energy production (end) | Gesamte Wirkenergieerzeugung (end) | Producción total de energía activa (end) | Całkowita produkcja energii czynnej (end) | Total (net) active energy production i.e. produced-consumed energy | Wh | Wh | Endvalue | Double | 10 minute tag
WTUR.TotWh_Mly_Sum | #N/A | WTUR. | TotWh_Mly_Sum | Total active energy production (sum) | Gesamte Wirkenergieerzeugung (sum) | Producción total de energía activa (sum) | Całkowita produkcja energii czynnej (sum) | Total (net) active energy production i.e. produced-consumed energy | Wh | Wh | Summation | Double | Monthly tag
WTUR.TotWh_Mly_Sum_Current | #N/A | WTUR. | TotWh_Mly_Sum_Current | Total active energy production | Gesamte Wirkenergieerzeugung | Producción total de energía activa | Całkowita produkcja energii czynnej | Total (net) active energy production i.e. produced-consumed energy | Wh | Wh | Live Value | Double | Live Value
WTUR.TotWh_Yly_End | #N/A | WTUR. | TotWh_Yly_End | Total active energy production (end) | Gesamte Wirkenergieerzeugung (end) | Producción total de energía activa (end) | Całkowita produkcja energii czynnej (end) | Total (net) active energy production i.e. produced-consumed energy | Wh | Wh | Endvalue | Double | 10 minute tag
WTUR.TotWh_Yly_Sum | #N/A | WTUR. | TotWh_Yly_Sum | Total active energy production (sum) | Gesamte Wirkenergieerzeugung (sum) | Producción total de energía activa (sum) | Całkowita produkcja energii czynnej (sum) | Total (net) active energy production i.e. produced-consumed energy | Wh | Wh | Summation | Double | Yearly tag
WTUR.TotWh_Yly_Sum_Current | #N/A | WTUR. | TotWh_Yly_Sum_Current | Total active energy production | Gesamte Wirkenergieerzeugung | Producción total de energía activa | Całkowita produkcja energii czynnej | Total (net) active energy production i.e. produced-consumed energy | Wh | Wh | Live Value | Double | Live Value
WTUR.TotWhRsTms | #N/A | WTUR. | TotWhRsTms | Reset time of total production counter | Rückstellzeit des Zählers der Gesamtproduktion | Restablecer el contador de producción total | Resetowanie czasu całkowitego licznika produkcji | Reset time of total production counter | DateTime | DateTime | Live Value | DateTime | Live Value
WTUR.TurNam | #N/A | WTUR. | TurNam | Turbine name | Turbinenname | Nombre de turbina | Nazwa turbiny | Turbine name | String | String | Live Value | String | Live Value
WTUR.TurOp | WTUR.TurOp | WTUR. | TurOp | Operation Command | Betrieb Befehl | Comando de operación | Polecenie operacji | Wind turbine operation command 1:Start 2:Stop | cmd | Enum | Command | Long | Command
WTUR.TurOp_10m_Avg | #N/A | WTUR. | TurOp_10m_Avg | Operation Command (avg) | Betrieb Befehl (avg) | Comando de operación (avg) | Polecenie operacji (avg) | Wind turbine operation command 1:Start 2:Stop | cmd | Enum | Average | Long | 10 minute tag
WTUR.TurOp_10m_Max | #N/A | WTUR. | TurOp_10m_Max | Operation Command (max) | Betrieb Befehl (max) | Comando de operación (max) | Polecenie operacji (max) | Wind turbine operation command 1:Start 2:Stop | cmd | Enum | Maximum | Long | 10 minute tag
WTUR.TurOp_10m_Min | #N/A | WTUR. | TurOp_10m_Min | Operation Command (min) | Betrieb Befehl (min) | Comando de operación (min) | Polecenie operacji (min) | Wind turbine operation command 1:Start 2:Stop | cmd | Enum | Minimum | Long | 10 minute tag
WTUR.TurOp_10m_Std | #N/A | WTUR. | TurOp_10m_Std | Operation Command (std) | Betrieb Befehl (std) | Comando de operación (std) | Polecenie operacji (std) | Wind turbine operation command 1:Start 2:Stop | cmd | Enum | Standard Deviation | Long | 10 minute tag
WTUR.TurOpEmgStop | #N/A | WTUR. | TurOpEmgStop | Emergency stop | Not-Aus | Parada de emergencia | Wyłącznik awaryjny | Emergency stop | cmd | Enum | Command | Long | Command
WTUR.TurOpRs | #N/A | WTUR. | TurOpRs | Reset command | Reset-Befehl | Restablecer comando | Polecenie Resetuj | Reset command | cmd | Enum | Command | Long | Command
WTUR.TurOpStop | #N/A | WTUR. | TurOpStop | Stop command | Stopp-Befehl | Detener comando | Polecenie Zatrzymaj | Stop command | cmd | Enum | Command | Long | Command
WTUR.TurOpStr | #N/A | WTUR. | TurOpStr | Start command | Start-Befehl | Iniciar comando | Polecenie Uruchom | Start command | cmd | Enum | Command | Long | Command
WTUR.TurSt | WTUR.TurSt | WTUR. | TurSt | Turbine Status | Turbine Status | Estado de la turbina | Stan turbiny | 1:Turbine stopped/alarm 2:Turbine in standby/warning 3:Turbine is starting 4:Turbine is running en normal operation 5:Turbine is in freerun with the generator disconnected 6:Turbine is braking -10:No communication -11:Turbine in Service -12:Manual stop -14:Unknown | Enum | Enum | Live Value | Long | Live Value | Used in standard monitor Presentation
WTUR.TurSt_10m_End | #N/A | WTUR. | TurSt_10m_End | Turbine Status (end) | Turbine Status (end) | Estado de la turbina (end) | Stan turbiny (end) | 1:Turbine stopped/alarm 2:Turbine in standby/warning 3:Turbine is starting 4:Turbine is running en normal operation 5:Turbine is in freerun with the generator disconnected 6:Turbine is braking 10:No communication 11:Turbine in Service | Enum | Enum | Endvalue | Long | 10 minute tag
WTUR.TurStAlm | #N/A | WTUR. | TurStAlm | Turbine Alarm Status | Turbinen-Alarmstatus | Estado de alarma de la turbina | Stan alarmu turbiny | Turbine Alarm Status: 0 : No Alarm 1 : Active Alarm | Enum | Enum | Live Value | Long | Live Value | Used in standard monitor Presentation | Used in standard Park monitor presentation
WTUR.TurStComm | #N/A | WTUR. | TurStComm | Turbine Communication Status | Turbine Kommunikationsstatus | Estado de comunicación de la turbina | Stan komunikacji turbiny | Turbine Communication Status: 0 : Communication Error 1 : Communication OK | Enum | Enum | Live Value | Long | Live Value | Used in standard monitor Presentation | Used in standard Park monitor presentation
WTUR.TurStEmgStop | #N/A | WTUR. | TurStEmgStop | Turbine Emergency Stop Status | Turbinen-Not-Aus-Status | Estado de parada de emergencia de la turbina | Stan zatrzymania awaryjnego turbiny | Turbine Emergency Stop status: 1 : stopped | Enum | Enum | Live Value | Long | Live Value
WTUR.TurStErr | #N/A | WTUR. | TurStErr | Number of turbines with error | Anzahl der Turbinen mit Störung | Número de turbinas con error | Liczba turbin z błędem | Number of turbines with error | Enum | Enum | Live Value | Long | Live Value
WTUR.TurStManu | #N/A | WTUR. | TurStManu | Turbine state manufacturer code | Turbinenstatus Herstellercode | Código del fabricante del estado de la turbina | Kod producenta stanu turbiny | Turbine state manufacturer code | Enum | Enum | Live Value | Long | Live Value | Used in standard monitor Presentation
WTUR.TurStManu_10m_Avg | #N/A | WTUR. | TurStManu_10m_Avg | Turbine state manufacturer code (avg) | Turbinenstatus Herstellercode (avg) | Código del fabricante del estado de la turbina (avg) | Kod producenta stanu turbiny (avg) | Turbine state manufacturer code | Enum | Enum | Average | Double | 10 minute tag | Used in standard monitor Presentation
WTUR.TurStManu_10m_End | #N/A | WTUR. | TurStManu_10m_End | Turbine state manufacturer code (end) | Turbinenstatus Herstellercode (end) | Código del fabricante del estado de la turbina (end) | Kod producenta stanu turbiny (end) | Turbine state manufacturer code | Enum | Enum | Endvalue | Long | 10 minute tag
WTUR.TurStManu_10m_Max | #N/A | WTUR. | TurStManu_10m_Max | Turbine state manufacturer code (max) | Turbinenstatus Herstellercode (max) | Código del fabricante del estado de la turbina (max) | Kod producenta stanu turbiny (max) | Turbine state manufacturer code | Enum | Enum | Maximum | Double | 10 minute tag | Used in standard monitor Presentation
WTUR.TurStManu_10m_Min | #N/A | WTUR. | TurStManu_10m_Min | Turbine state manufacturer code (min) | Turbinenstatus Herstellercode (min) | Código del fabricante del estado de la turbina (min) | Kod producenta stanu turbiny (min) | Turbine state manufacturer code | Enum | Enum | Minimum | Double | 10 minute tag | Used in standard monitor Presentation
WTUR.TurStManu_10m_Std | #N/A | WTUR. | TurStManu_10m_Std | Turbine state manufacturer code (std) | Turbinenstatus Herstellercode (std) | Código del fabricante del estado de la turbina (std) | Kod producenta stanu turbiny (std) | Turbine state manufacturer code | Enum | Enum | Standard Deviation | Double | 10 minute tag | Used in standard monitor Presentation
WTUR.TurStManuStop1 | #N/A | WTUR. | TurStManuStop1 | Commanded Stop Status | Status des befohlenen Stopps | Estado de parada comandada | Stan polecenia zatrzymania | Commanded stop status (bitset representing 16 specific errors) | Enum | Enum | Live Value | Long | Live Value
WTUR.TurStManuStop2 | #N/A | WTUR. | TurStManuStop2 | Commanded Stop Status | Status des befohlenen Stopps | Estado de parada comandada | Stan polecenia zatrzymania | Commanded stop status (bitset representing 16 specific errors) | Enum | Enum | Live Value | Long | Live Value
WTUR.TurStManuStr | #N/A | WTUR. | TurStManuStr | Turbine state manufacturer text | Turbinenstatus Herstellertext | Texto del fabricante del estado de la turbina | Tekst producenta stanu turbiny | Turbine state manufacturer text | String | String | Live Value | String | Live Value | Used in standard monitor Presentation
WTUR.TurStOk | #N/A | WTUR. | TurStOk | Turbine in Ok/Ready problem Status | Turbine im ok/bereit Problemstatus | Estado de problema de turbina en ok/lista | Turbina w stanie OK/Ready problem | Turbine in Ok/Ready problem status: 0:Not Ok/Ready 1:Ok/ready | Enum | Enum | Live Value | Long | Live Value | Used in standard monitor Presentation | Used in standard Park monitor presentation
WTUR.TurStPend | #N/A | WTUR. | TurStPend | Pending turbine state | Ausstehender Turbinenstatus | Estado pendiente de la turbina | Oczekujący stan turbiny | Pending turbine state | Enum | Enum | Live Value | Long | Live Value
WTUR.TurStPsblW | #N/A | WTUR. | TurStPsblW | Possibly Active power | Möglicherweise Wirkleistung | Posiblemente potencia activa | Możliwa Moc czynna | Available power production based on turbine status | W | W | Live Value | Double | Live Value
WTUR.TurStSrv | #N/A | WTUR. | TurStSrv | Turbine Service Status | Turbinen Service Status | Estado de servicio de turbina | Stan turbiny Serwis | Turbine Service status: 0 : not in service 1 : Service | Enum | Enum | Live Value | Long | Live Value | Used in standard monitor Presentation | Used in standard Park monitor presentation
WTUR.TurStStdby | #N/A | WTUR. | TurStStdby | Turbine Standby Status | Turbinen Standby-Status | Estado de espera de la turbina | Stan gotowości turbiny | Turbine Standby status: 1 : Standby | Enum | Enum | Live Value | Long | Live Value
WTUR.TurStStop | #N/A | WTUR. | TurStStop | Turbine Stop Status | Turbinen Stop Status | Estado de parada en la turbina | Stan zatrzymania turbiny | Turbine Stop status: 1 : stopped | Enum | Enum | Live Value | Long | Live Value
WTUR.TurStStr | #N/A | WTUR. | TurStStr | Turbine Status Text | Statustext der Turbine | Texto de estado de la turbina | Tekst stanu turbiny | 1:Turbine stopped/alarm 2:Turbine in standby/warning 3:Turbine is starting 4:Turbine is running en normal operation 5:Turbine is in freerun with the generator disconnected 6:Turbine is braking -10:No communication -11:Turbine in Service -12:Manual stop -14:Unknown | String | String | Function | String | Live Value | Used in standard monitor Presentation
WTUR.TurStSubManu | #N/A | WTUR. | TurStSubManu | Turbine substate manufacturer code | Turbine Unterzustand Herstellercode | Código del fabricante del subestado de la turbina | Kod producenta podstanu turbiny | Turbine substate manufacturer code | Enum | Enum | Live Value | Long | Live Value | Used in some specialised presentations
WTUR.TurStSubManu_10m_Avg | #N/A | WTUR. | TurStSubManu_10m_Avg | Turbine substate manufacturer code (avg) | Turbine Unterzustand Herstellercode (avg) | Código del fabricante del subestado de la turbina (avg) | Kod producenta podstanu turbiny (avg) | Turbine substate manufacturer code | Enum | Enum | Average | Long | 10 minute tag
WTUR.TurStSubManu_10m_End | #N/A | WTUR. | TurStSubManu_10m_End | Turbine substate manufacturer code (end) | Turbine Unterzustand Herstellercode (end) | Código del fabricante del subestado de la turbina (end) | Kod producenta podstanu turbiny (end) | Turbine substate manufacturer code | Enum | Enum | Endvalue | Long | 10 minute tag
WTUR.TurStSubManu_10m_Max | #N/A | WTUR. | TurStSubManu_10m_Max | Turbine substate manufacturer code (max) | Turbine Unterzustand Herstellercode (max) | Código del fabricante del subestado de la turbina (max) | Kod producenta podstanu turbiny (max) | Turbine substate manufacturer code | Enum | Enum | Maximum | Long | 10 minute tag
WTUR.TurStSubManu_10m_Min | #N/A | WTUR. | TurStSubManu_10m_Min | Turbine substate manufacturer code (min) | Turbine Unterzustand Herstellercode (min) | Código del fabricante del subestado de la turbina (min) | Kod producenta podstanu turbiny (min) | Turbine substate manufacturer code | Enum | Enum | Minimum | Long | 10 minute tag
WTUR.TurStSubManu_10m_Std | #N/A | WTUR. | TurStSubManu_10m_Std | Turbine substate manufacturer code (std) | Turbine Unterzustand Herstellercode (std) | Código del fabricante del subestado de la turbina (std) | Kod producenta podstanu turbiny (std) | Turbine substate manufacturer code | Enum | Enum | Standard Deviation | Long | 10 minute tag
WTUR.TurStSubManuStr | #N/A | WTUR. | TurStSubManuStr | Turbine substate manufacturer text | Turbine Unterzustand Herstellertext | Código del fabricante del subestado de la turbina | Tekst producenta podstanu turbiny | Turbine substate manufacturer text | String | String | Live Value | String | Live Value | Used in some specialised presentations
WTUR.TurStWar | #N/A | WTUR. | TurStWar | Turbine warning Status | Turbinenwarnstatus | Estado del aviso de la turbina | Stan ostrzeżenia turbiny | Turbine warning status: 0 : no warning 1 : active warning | Enum | Enum | Live Value | Long | Live Value | Used in standard monitor Presentation | Used in standard Park monitor presentation
WTUR.UntId | #N/A | WTUR. | UntId | Unit Identification Number | Identifikationsnummer der Einheit | Número de identificación de unidad | Numer identyfikacyjny jednostki | Unit Identification Number | Enum | Enum | Live Value | Long | Live Value |  |  | New Vestas UA TAG
WTUR.UntTyp | #N/A | WTUR. | UntTyp | Unit Type | Gerätetyp | Tipo de unidad | Typ jednostki | Unit Type (e.g. V126) | Enum | Enum | Live Value | Long | Live Value |  |  | New Vestas UA TAG
WTUR.VAr | WTUR.VAr | WTUR. | VAr | Reactive power | Blindleistung | Potencia reactiva | Moc bierna | Reactive power at grid connection | VAr | VAr | Live Value | Double | Live Value | Used in some specialised presentations
WTUR.VAr_10m_Avg | #N/A | WTUR. | VAr_10m_Avg | Reactive power (avg) | Blindleistung (avg) | Potencia reactiva (avg) | Moc bierna (avg) | Reactive power at grid connection | VAr | VAr | Average | Double | 10 minute tag | Common tags for analysis
WTUR.VAr_10m_Max | #N/A | WTUR. | VAr_10m_Max | Reactive power (max) | Blindleistung (max) | Potencia reactiva (max) | Moc bierna (max) | Reactive power at grid connection | VAr | VAr | Maximum | Double | 10 minute tag | Common tags for analysis
WTUR.VAr_10m_Min | #N/A | WTUR. | VAr_10m_Min | Reactive power (min) | Blindleistung (min) | Potencia reactiva (min) | Moc bierna (min) | Reactive power at grid connection | VAr | VAr | Minimum | Double | 10 minute tag | Common tags for analysis
WTUR.VAr_10m_Std | #N/A | WTUR. | VAr_10m_Std | Reactive power (std) | Blindleistung (std) | Potencia reactiva (std) | Moc bierna (std) | Reactive power at grid connection | VAr | VAr | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WTUR.VArOvW | WTUR.VArOvW | WTUR. | VArOvW | Activate reactive power priority | Aktivieren der Blindleistungspriorität | Activar prioridad de potencia reactiva | Aktywuj priorytet mocy biernej | Activate wind turbine reactive power priority over active power | Enum | Enum | Live Value | Long
WTUR.W | WTUR.W | WTUR. | W | Active Power | Wirkleistung | Potencia activa | Moc czynna | Active power at grid connection | W | W | Live Value | Double | Live Value | Used in standard monitor Presentation
WTUR.W_10m_Avg | #N/A | WTUR. | W_10m_Avg | Active Power (avg) | Wirkleistung (avg) | Potencia activa (avg) | Moc czynna (avg) | Active power at grid connection | W | W | Average | Double | 10 minute tag | Needed for reports | Used in standard Park monitor presentation
WTUR.W_10m_Max | #N/A | WTUR. | W_10m_Max | Active Power (max) | Wirkleistung (max) | Potencia activa (max) | Moc czynna (max) | Active power at grid connection | W | W | Maximum | Double | 10 minute tag | Common tags for analysis
WTUR.W_10m_Min | #N/A | WTUR. | W_10m_Min | Active Power (min) | Wirkleistung (min) | Potencia activa (min) | Moc czynna (min) | Active power at grid connection | W | W | Minimum | Double | 10 minute tag | Common tags for analysis
WTUR.W_10m_Std | #N/A | WTUR. | W_10m_Std | Active Power (std) | Wirkleistung (std) | Potencia activa (std) | Moc czynna (std) | Active power at grid connection | W | W | Standard Deviation | Double | 10 minute tag | Common tags for analysis
WTUR.W_Dly_Avg | #N/A | WTUR. | W_Dly_Avg | Active Power (avg) | Wirkleistung (avg) | Potencia activa (avg) | Moc czynna (avg) | Daily average power | W | W | Average | Double | Daily tag
WTUR.W_Mly_Avg | #N/A | WTUR. | W_Mly_Avg | Active Power (avg) | Wirkleistung (avg) | Potencia activa (avg) | Moc czynna (avg) | Monthly average power | W | W | Average | Double | Monthly tag
WTUR.WarTms | #N/A | WTUR. | WarTms | Time with a warning | Zeit mit Warnung | Tiempo con un aviso | Czas z ostrzeżeniem | Time with a warning | s | seconds | Total Counter | Long | Live Value
WTUR.WarTms_10m_End | #N/A | WTUR. | WarTms_10m_End | Time with a warning (end) | Zeit mit Warnung (end) | Tiempo con un aviso (end) | Czas z ostrzeżeniem (end) | Time with a warning | s | seconds | Endvalue | Long | 10 minute tag
WTUR.WdDirDnTms | #N/A | WTUR. | WdDirDnTms | Downtime due to wind direction stop time | Ausfallzeit aufgrund der Windrichtung Stoppzeit | Inactividad debido al tiempo de parada de la dirección del viento | Przestój spowodowany czasem zatrzymania kierunku wiatru | Downtime due to wind direction stop time | s | seconds | Total Counter | Long | Live Value
WTUR.WdDirDnTms_10m_End | #N/A | WTUR. | WdDirDnTms_10m_End | Downtime due to wind direction stop time (end) | Ausfallzeit aufgrund der Windrichtung Stoppzeit (end) | Inactividad debido al tiempo de parada de la dirección del viento (end) | Przestój spowodowany czasem zatrzymania kierunku wiatru (end) | Downtime due to wind direction stop time | s | seconds | Endvalue | Long | 10 minute tag
WTUR.WdOkTms | #N/A | WTUR. | WdOkTms | Time wind OK time | Zeit Wind OK Zeit | Tiempo de viento OK | Czas wiatr OK | Time wind ok time, i.e. wind above cut-in value and below cut-out value | s | seconds | Total Counter | Long | Live Value
WTUR.WdOkTms_10m_End | #N/A | WTUR. | WdOkTms_10m_End | Time wind OK time (end) | Zeit Wind OK Zeit (end) | Tiempo de viento OK (end) | Czas wiatr OK (end) | Time wind ok time, i.e. wind above cut-in value and below cut-out value | s | seconds | Endvalue | Long | 10 minute tag
WTUR.WdOkTms_10m_Sum | #N/A | WTUR. | WdOkTms_10m_Sum | Time wind OK time (sum) | Zeit Wind OK Zeit (sum) | Tiempo de viento OK (sum) | Czas wiatr OK (sum) | Time wind ok time, i.e. wind above cut-in and below high wind cut-out in each 10 minute period i.e. 0-600 seconds | s | seconds | Summation | Long | 10 minute tag
WTUR.WdOkTms_Dly_Sum | #N/A | WTUR. | WdOkTms_Dly_Sum | Time wind OK time (sum) | Zeit Wind OK Zeit (sum) | Tiempo de viento OK (sum) | Czas wiatr OK (sum) | Time wind ok time, i.e. wind above cut-in and below high wind cut-out in each Daily period i.e. 0-86400 seconds | s | seconds | Summation | Long | Daily tag
WTUR.WdOkTms_Mly_Sum | #N/A | WTUR. | WdOkTms_Mly_Sum | Time wind OK time (sum) | Zeit Wind OK Zeit (sum) | Tiempo de viento OK (sum) | Czas wiatr OK (sum) | Time wind ok time, i.e. wind above cut-in and below high wind cut-out in each Monthly Period | s | seconds | Summation | Long | Monthly tag
WYAW.BrkPmpCnt_10m_End | #N/A | WYAW. | BrkPmpCnt_10m_End | Number of activations of the yaw brake pump (end) | Anzahl der Aktivierungen der Yawbremspumpe (end) | Número de activaciones de la bomba de freno de desplazamiento (end) | Liczba aktywacji pompy hamulca yaw (end) | Number of activations of the yaw brake pump | count | Count | Endvalue | Long | 10 minute tag
WYAW.BrkPmpTms_10m_End | #N/A | WYAW. | BrkPmpTms_10m_End | Time yaw brake pump has been activated (end) | Zeit, in der die Yawbremspumpe aktiviert wurde (end) | Tiempo que la bomba de freno del desplazamiento ha estado activada (end) | Czsa aktywacji pompy hamulca yaw (end) | Time yaw brake pump has been activated | s | seconds | Endvalue | Long | 10 minute tag
WYAW.BrkPres | WYAW.BrkPres | WYAW. | BrkPres | Yaw system brake pressure | Bremsdruck des Yawsystems | Presión del freno del sistema de desplazamiento | Ciśnienie hamulca w układzie yaw | Yaw system brake pressure | bar | bar | Live Value | Double | Live Value
WYAW.BrkPres_10m_Avg | #N/A | WYAW. | BrkPres_10m_Avg | Yaw system brake pressure (avg) | Bremsdruck des Yawsystems (avg) | Presión del freno del sistema de desplazamiento (avg) | Ciśnienie hamulca w układzie yaw (avg) | Yaw system brake pressure | bar | bar | Average | Double | 10 minute tag
WYAW.BrkPres_10m_Max | #N/A | WYAW. | BrkPres_10m_Max | Yaw system brake pressure (max) | Bremsdruck des Yawsystems (max) | Presión del freno del sistema de desplazamiento (max) | Ciśnienie hamulca w układzie yaw (max) | Yaw system brake pressure | bar | bar | Maximum | Double | 10 minute tag
WYAW.BrkPres_10m_Min | #N/A | WYAW. | BrkPres_10m_Min | Yaw system brake pressure (min) | Bremsdruck des Yawsystems (min) | Presión del freno del sistema de desplazamiento (min) | Ciśnienie hamulca w układzie yaw (min) | Yaw system brake pressure | bar | bar | Minimum | Double | 10 minute tag
WYAW.BrkPres_10m_Std | #N/A | WYAW. | BrkPres_10m_Std | Yaw system brake pressure (std) | Bremsdruck des Yawsystems (std) | Presión del freno del sistema de desplazamiento (std) | Ciśnienie hamulca w układzie yaw (std) | Yaw system brake pressure | bar | bar | Standard Deviation | Double | 10 minute tag
WYAW.BrkSt | WYAW.BrkSt | WYAW. | BrkSt | Yaw brake Status | Status der Yawbremse | Estado del freno de desplazamiento | Stan hamulca yaw | Status of the yaw brake | Enum | Enum | Live Value | Long | Live Value
WYAW.CabWup | WYAW.CabWup | WYAW. | CabWup | Cable windup. Number of windings from calibration point | Kabelaufwicklung. Anzahl der Wicklungen vom Kalibrierungspunkt | Cable enrollado. Número de bobinados desde el punto de calibración | Skęcenie kabla. Liczba skręceń od punktu kalibracji | Cable windup. Number of windings from calibration point | count | Count | Live Value | Double | Live Value
WYAW.CabWup_10m_Avg | #N/A | WYAW. | CabWup_10m_Avg | Cable windup. Number of windings from calibration point (avg) | Kabelaufwicklung. Anzahl der Wicklungen vom Kalibrierungspunkt (avg) | Cable enrollado. Número de bobinados desde el punto de calibración (avg) | Skęcenie kabla. Liczba skręceń od punktu kalibracji (avg) | Cable windup. Number of windings from calibration point | count | Count | Average | Double | 10 minute tag
WYAW.CabWup_10m_Max | #N/A | WYAW. | CabWup_10m_Max | Cable windup. Number of windings from calibration point (max) | Kabelaufwicklung. Anzahl der Wicklungen vom Kalibrierungspunkt (max) | Cable enrollado. Número de bobinados desde el punto de calibración (max) | Skęcenie kabla. Liczba skręceń od punktu kalibracji (max) | Cable windup. Number of windings from calibration point | count | Count | Maximum | Double | 10 minute tag
WYAW.CabWup_10m_Min | #N/A | WYAW. | CabWup_10m_Min | Cable windup. Number of windings from calibration point (min) | Kabelaufwicklung. Anzahl der Wicklungen vom Kalibrierungspunkt (min) | Cable enrollado. Número de bobinados desde el punto de calibración (min) | Skęcenie kabla. Liczba skręceń od punktu kalibracji (min) | Cable windup. Number of windings from calibration point | count | Count | Minimum | Double | 10 minute tag
WYAW.CabWup_10m_Std | #N/A | WYAW. | CabWup_10m_Std | Cable windup. Number of windings from calibration point (std) | Kabelaufwicklung. Anzahl der Wicklungen vom Kalibrierungspunkt (std) | Cable enrollado. Número de bobinados desde el punto de calibración (std) | Skęcenie kabla. Liczba skręceń od punktu kalibracji (std) | Cable windup. Number of windings from calibration point | count | Count | Standard Deviation | Double | 10 minute tag
WYAW.CcwCnt | #N/A | WYAW. | CcwCnt | Number of activations of yaw Counter clockwise | Anzahl der Aktivierungen des Yaw Gegen den Uhrzeigersinn | Número de activaciones del contador de desplazamiento en el sentido de las agujas del reloj | Liczba aktywacji yaw Licznik zgodnie ze wskazówkami zegara | Number of activations of yaw Counter clockwise | count | Count | Live Value | Long | Live Value
WYAW.CcwCnt_10m_End | #N/A | WYAW. | CcwCnt_10m_End | Number of activations of yaw Counter clockwise (end) | Anzahl der Aktivierungen des Yaw Gegen den Uhrzeigersinn (end) | Número de activaciones del contador de desplazamiento en el sentido de las agujas del reloj (end) | Liczba aktywacji yaw Licznik zgodnie ze wskazówkami zegara (end) | Number of activations of yaw Counter clockwise | count | Count | Endvalue | Long | 10 minute tag
WYAW.CcwOpTms | WYAW.CcwOpTms | WYAW. | CcwOpTms | Time yaw Counter clockwise has been activated | Yawzeit Gegen den Uhrzeigersinn wurde aktiviert | Tiempo que el contador de desplazamiento en el sentido de las agujas del reloj ha estado activado | Czas aktywacji yaw Licznik zgodnie ze wskazówkami zegara | Time yaw Counter clockwise has been activated | s | seconds | Total Counter | Long | Live Value
WYAW.CcwOpTms_10m_End | #N/A | WYAW. | CcwOpTms_10m_End | Time yaw Counter clockwise has been activated (end) | Yawzeit Gegen den Uhrzeigersinn wurde aktiviert (end) | Tiempo que el contador de desplazamiento en el sentido de las agujas del reloj ha estado activado (end) | Czas aktywacji yaw Licznik zgodnie ze wskazówkami zegara (end) | Time yaw Counter clockwise has been activated | s | seconds | Endvalue | Long | 10 minute tag
WYAW.Cnt | #N/A | WYAW. | Cnt | Yaw counter | Yawzähler | Contador de desplazamiento | Licznik Yaw | Yaw counter | deg | Degrees | Live Value | Double | Live Value
WYAW.CwCnt | #N/A | WYAW. | CwCnt | Number of activations of yaw clockwise | Anzahl der Aktivierungen des Yaw im Uhrzeigersinn | Número de activaciones de desplazamiento en el sentido de las agujas del reloj | Liczba aktywacji yaw zgodnie z wskazówkami zegara | Number of activations of yaw clockwise | count | Count | Live Value | Long | Live Value
WYAW.CwCnt_10m_End | #N/A | WYAW. | CwCnt_10m_End | Number of activations of yaw clockwise (end) | Anzahl der Aktivierungen des Yaw im Uhrzeigersinn (end) | Número de activaciones de desplazamiento en el sentido de las agujas del reloj (end) | Liczba aktywacji Yaw zgodnie z ruchem wskazówek zegara (end) | Number of activations of yaw clockwise | count | Count | Endvalue | Long | 10 minute tag
WYAW.CwOpTms | WYAW.CwOpTms | WYAW. | CwOpTms | Time yaw Clockwise has been activated | Yawzeit im Uhrzeigersinn wurde aktiviert | Tiempo que el desplazamiento en el sentido de las agujas del reloj ha estado activado | Czas aktywacji yaw zgodnie ze wskazówkami zegara | Time yaw Clockwise has been activated | s | seconds | Total Counter | Long | Live Value
WYAW.CwOpTms_10m_End | #N/A | WYAW. | CwOpTms_10m_End | Time yaw Clockwise has been activated (end) | Yawzeit im Uhrzeigersinn wurde aktiviert (end) | Tiempo que el desplazamiento en el sentido de las agujas del reloj ha estado activado (end) | Czas aktywacji yaw zgodnie ze wskazówkami zegara (end) | Time yaw Clockwise has been activated | s | seconds | Endvalue | Long | 10 minute tag
WYAW.HyOilTmp | #N/A | WYAW. | HyOilTmp | Yaw Hydraulic Oil Temp | Yaw Hydrauliköltemperatur | Temperatura de aceite hidráulico de desplazamiento | Temp oleju hydr. Yaw | Yaw hydraulic Oil Temperature | deg_c | °C | Live Value | Double | Live Value
WYAW.HyOilTmp_10m_Avg | #N/A | WYAW. | HyOilTmp_10m_Avg | Yaw Hydraulic Oil Temp (avg) | Yaw Hydrauliköltemperatur (avg) | Temperatura de aceite hidráulico de desplazamiento (avg) | Temp oleju hydr. Yaw (avg) | Yaw hydraulic Oil Temperature | deg_c | °C | Average | Double | 10 minute tag
WYAW.HyOilTmp_10m_Max | #N/A | WYAW. | HyOilTmp_10m_Max | Yaw Hydraulic Oil Temp (max) | Yaw Hydrauliköltemperatur (max) | Temperatura de aceite hidráulico de desplazamiento (max) | Temp oleju hydr. Yaw (max) | Yaw hydraulic Oil Temperature | deg_c | °C | Maximum | Double | 10 minute tag
WYAW.HyOilTmp_10m_Min | #N/A | WYAW. | HyOilTmp_10m_Min | Yaw Hydraulic Oil Temp (min) | Yaw Hydrauliköltemperatur (min) | Temperatura de aceite hidráulico de desplazamiento (min) | Temp oleju hydr. Yaw (min) | Yaw hydraulic Oil Temperature | deg_c | °C | Minimum | Double | 10 minute tag
WYAW.HyOilTmp_10m_Std | #N/A | WYAW. | HyOilTmp_10m_Std | Yaw Hydraulic Oil Temp (std) | Yaw Hydrauliköltemperatur (std) | Temperatura de aceite hidráulico de desplazamiento (std) | Temp oleju hydr. Yaw (std) | Yaw hydraulic Oil Temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WYAW.HyPres | #N/A | WYAW. | HyPres | Yaw system hydraulic pressure | Hydraulikdruck des Yawsystems | Presión hidráulica del sistema de desplazamiento | Ciśnienie hydr. układu Yaw | Yaw system hydraulic pressure | bar | bar | Live Value | Double | Live Value
WYAW.HyPres_10m_Avg | #N/A | WYAW. | HyPres_10m_Avg | Yaw system hydraulic pressure (avg) | Hydraulikdruck des Yawsystems (avg) | Presión hidráulica del sistema de desplazamiento (avg) | Ciśnienie hydr. układu Yaw (avg) | Yaw system hydraulic pressure | bar | bar | Average | Double | 10 minute tag
WYAW.HyPres_10m_Max | #N/A | WYAW. | HyPres_10m_Max | Yaw system hydraulic pressure (max) | Hydraulikdruck des Yawsystems (max) | Presión hidráulica del sistema de desplazamiento (max) | Ciśnienie hydr. układu Yaw (max) | Yaw system hydraulic pressure | bar | bar | Maximum | Double | 10 minute tag
WYAW.HyPres_10m_Min | #N/A | WYAW. | HyPres_10m_Min | Yaw system hydraulic pressure (min) | Hydraulikdruck des Yawsystems (min) | Presión hidráulica del sistema de desplazamiento (min) | Ciśnienie hydr. układu Yaw (min) | Yaw system hydraulic pressure | bar | bar | Minimum | Double | 10 minute tag
WYAW.HyPres_10m_Std | #N/A | WYAW. | HyPres_10m_Std | Yaw system hydraulic pressure (std) | Hydraulikdruck des Yawsystems (std) | Presión hidráulica del sistema de desplazamiento (std) | Ciśnienie hydr. układu Yaw (std) | Yaw system hydraulic pressure | bar | bar | Standard Deviation | Double | 10 minute tag
WYAW.HyTnkPres | #N/A | WYAW. | HyTnkPres | Yaw system hydraulic accumulation tank pressure | Druck des Hydraulikspeichers des Yawsystems | Presión del tanque de acumulación hidráulica del sistema de desplazamiento | Ciśnienie w hydr. zbiorniku akumulacyjnym układu Yaw | Yaw system hydraulic accumulation tank pressure | bar | bar | Live Value | Double | Live Value
WYAW.HyTnkPres_10m_Avg | #N/A | WYAW. | HyTnkPres_10m_Avg | Yaw system hydraulic accumulation tank pressure (avg) | Druck des Hydraulikspeichers des Yawsystems (avg) | Presión del tanque de acumulación hidráulica del sistema de desplazamiento (avg) | Ciśnienie w hydr. zbiorniku akumulacyjnym układu Yaw (avg) | Yaw system hydraulic accumulation tank pressure | bar | bar | Average | Double | 10 minute tag
WYAW.HyTnkPres_10m_Max | #N/A | WYAW. | HyTnkPres_10m_Max | Yaw system hydraulic accumulation tank pressure (max) | Druck des Hydraulikspeichers des Yawsystems (max) | Presión del tanque de acumulación hidráulica del sistema de desplazamiento (max) | Ciśnienie w hydr. zbiorniku akumulacyjnym układu Yaw (max) | Yaw system hydraulic accumulation tank pressure | bar | bar | Maximum | Double | 10 minute tag
WYAW.HyTnkPres_10m_Min | #N/A | WYAW. | HyTnkPres_10m_Min | Yaw system hydraulic accumulation tank pressure (min) | Druck des Hydraulikspeichers des Yawsystems (min) | Presión del tanque de acumulación hidráulica del sistema de desplazamiento (min) | Ciśnienie w hydr. zbiorniku akumulacyjnym układu Yaw (min) | Yaw system hydraulic accumulation tank pressure | bar | bar | Minimum | Double | 10 minute tag
WYAW.HyTnkPres_10m_Std | #N/A | WYAW. | HyTnkPres_10m_Std | Yaw system hydraulic accumulation tank pressure (std) | Druck des Hydraulikspeichers des Yawsystems (std) | Presión del tanque de acumulación hidráulica del sistema de desplazamiento (std) | Ciśnienie w hydr. zbiorniku akumulacyjnym układu Yaw (std) | Yaw system hydraulic accumulation tank pressure | bar | bar | Standard Deviation | Double | 10 minute tag
WYAW.OpTms | #N/A | WYAW. | OpTms | Time the yaw system has been activated | Zeit, in der das Yawsystem aktiviert wurde | Tiempo que el sistema de desplazamiento ha estado activado | Czas aktywacji systemu Yaw | Time the yaw system has been activated | s | seconds | Total Counter | Long | Live Value
WYAW.OpTms_10m_End | #N/A | WYAW. | OpTms_10m_End | Time the yaw system has been activated (end) | Zeit, in der das Yawsystem aktiviert wurde (end) | Tiempo que el sistema de desplazamiento ha estado activado (end) | Czas aktywacji systemu Yaw (end) | Time the yaw system has been activated | s | seconds | Endvalue | Long | 10 minute tag
WYAW.OpTms_10m_Sum | #N/A | WYAW. | OpTms_10m_Sum | Time the yaw system has been activated (sum) | Zeit, in der das Yawsystem aktiviert wurde (sum) | Tiempo que el sistema de desplazamiento ha estado activado (sum) | Czas aktywacji systemu Yaw (sum) | Time the yaw system has been activated in each 10 minute period i.e. 0-600 seconds | s | seconds | Summation | Long | 10 minute tag
WYAW.OpTms_Dly_Sum | #N/A | WYAW. | OpTms_Dly_Sum | Time the yaw system has been activated (sum) | Zeit, in der das Yawsystem aktiviert wurde (sum) | Tiempo que el sistema de desplazamiento ha estado activado (sum) | Czas aktywacji systemu Yaw (sum) | Time the yaw system has been activated in each Daily period i.e. 0-86400 seconds | s | seconds | Summation | Long | Daily tag
WYAW.OpTms_Mly_Sum | #N/A | WYAW. | OpTms_Mly_Sum | Time the yaw system has been activated (sum) | Zeit, in der das Yawsystem aktiviert wurde (sum) | Tiempo que el sistema de desplazamiento ha estado activado (sum) | Czas aktywacji systemu Yaw (sum) | Time the yaw system has been activated in each Monthly period | s | seconds | Summation | Long | Monthly tag
WYAW.PinGsLev | #N/A | WYAW. | PinGsLev | Grease level in the yaw pinion lubrication tank | Fettstand im Schmiermittelbehälter des Yawzahnrades | Nivel de grasa del depósito de lubricación del piñón de desplazamiento | Poziom smaru w zbiorniku smarowania zębatki Yaw | Grease level in the yaw pinion lubrication tank | percent | percent | Live Value | Double | Live Value
WYAW.PinGsLev_10m_Avg | #N/A | WYAW. | PinGsLev_10m_Avg | Grease level in the yaw pinion lubrication tank (avg) | Fettstand im Schmiermittelbehälter des Yawzahnrades (avg) | Nivel de grasa del depósito de lubricación del piñón de desplazamiento (avg) | Poziom smaru w zbiorniku smarowania zębatki Yaw (avg) | Grease level in the yaw pinion lubrication tank | percent | percent | Average | Double | 10 minute tag
WYAW.PinGsLev_10m_Max | #N/A | WYAW. | PinGsLev_10m_Max | Grease level in the yaw pinion lubrication tank (max) | Fettstand im Schmiermittelbehälter des Yawzahnrades (max) | Nivel de grasa del depósito de lubricación del piñón de desplazamiento (max) | Poziom smaru w zbiorniku smarowania zębatki Yaw (max) | Grease level in the yaw pinion lubrication tank | percent | percent | Maximum | Double | 10 minute tag
WYAW.PinGsLev_10m_Min | #N/A | WYAW. | PinGsLev_10m_Min | Grease level in the yaw pinion lubrication tank (min) | Fettstand im Schmiermittelbehälter des Yawzahnrades (min) | Nivel de grasa del depósito de lubricación del piñón de desplazamiento (min) | Poziom smaru w zbiorniku smarowania zębatki Yaw (min) | Grease level in the yaw pinion lubrication tank | percent | percent | Minimum | Double | 10 minute tag
WYAW.PinGsLev_10m_Std | #N/A | WYAW. | PinGsLev_10m_Std | Grease level in the yaw pinion lubrication tank (std) | Fettstand im Schmiermittelbehälter des Yawzahnrades (std) | Nivel de grasa del depósito de lubricación del piñón de desplazamiento (std) | Poziom smaru w zbiorniku smarowania zębatki Yaw (std) | Grease level in the yaw pinion lubrication tank | percent | percent | Standard Deviation | Double | 10 minute tag
WYAW.PltGsLev | #N/A | WYAW. | PltGsLev | Grease level in the yaw plate lubrication tank | Fettstand im Schmierstoffbehälter der Yawplatte | Nivel de grasa del depósito de lubricación de la placa de desplazamiento | Poziom smaru w zbiorniku smarowania płyty Yaw | Grease level in the yaw plate lubrication tank | percent | percent | Live Value | Double | Live Value
WYAW.PltGsLev_10m_Avg | #N/A | WYAW. | PltGsLev_10m_Avg | Grease level in the yaw plate lubrication tank (avg) | Fettstand im Schmierstoffbehälter der Yawplatte (avg) | Nivel de grasa del depósito de lubricación de la placa de desplazamiento (avg) | Poziom smaru w zbiorniku smarowania płyty Yaw (avg) | Grease level in the yaw plate lubrication tank | percent | percent | Average | Double | 10 minute tag
WYAW.PltGsLev_10m_Max | #N/A | WYAW. | PltGsLev_10m_Max | Grease level in the yaw plate lubrication tank (max) | Fettstand im Schmierstoffbehälter der Yawplatte (max) | Nivel de grasa del depósito de lubricación de la placa de desplazamiento (max) | Poziom smaru w zbiorniku smarowania płyty Yaw (max) | Grease level in the yaw plate lubrication tank | percent | percent | Maximum | Double | 10 minute tag
WYAW.PltGsLev_10m_Min | #N/A | WYAW. | PltGsLev_10m_Min | Grease level in the yaw plate lubrication tank (min) | Fettstand im Schmierstoffbehälter der Yawplatte (min) | Nivel de grasa del depósito de lubricación de la placa de desplazamiento (min) | Poziom smaru w zbiorniku smarowania płyty Yaw (min) | Grease level in the yaw plate lubrication tank | percent | percent | Minimum | Double | 10 minute tag
WYAW.PltGsLev_10m_Std | #N/A | WYAW. | PltGsLev_10m_Std | Grease level in the yaw plate lubrication tank (std) | Fettstand im Schmierstoffbehälter der Yawplatte (std) | Nivel de grasa del depósito de lubricación de la placa de desplazamiento (std) | Poziom smaru w zbiorniku smarowania płyty Yaw (std) | Grease level in the yaw plate lubrication tank | percent | percent | Standard Deviation | Double | 10 minute tag
WYAW.PnlTmp | #N/A | WYAW. | PnlTmp | Yaw Inverter Control Cabinet Temp | Yawwechselrichter Schaltschrank Temperatur | Temperatura del armario eléctrico del convertidor de desplazamiento | Temp szafy sterowniczej falownika odchyleń | Temperature yaw inverter control cabinet | deg_c | °C | Live Value | Double | Live Value
WYAW.PnlTmp_10m_Avg | #N/A | WYAW. | PnlTmp_10m_Avg | Yaw Inverter Control Cabinet Temp (avg) | Yawwechselrichter Schaltschrank Temperatur (avg) | Temperatura del armario eléctrico del convertidor de desplazamiento (avg) | Temp szafy sterowniczej falownika odchyleń (avg) | Temperature yaw inverter control cabinet | deg_c | °C | Average | Double | 10 minute tag
WYAW.RngTmp | #N/A | WYAW. | RngTmp | Yaw Rim Temp | Yaw Randtemperatur | Temperatura del borde de desplazamiento | Yaw Rim Temp | Yaw rim temperature | deg_c | °C | Live Value | Double | Live Value
WYAW.RngTmp_10m_Avg | #N/A | WYAW. | RngTmp_10m_Avg | Yaw Rim Temp (avg) | Yaw Randtemperatur (avg) | Temperatura del borde de desplazamiento (avg) | Yaw Rim Temp (avg) | Yaw rim temperature | deg_c | °C | Average | Double | 10 minute tag
WYAW.RngTmp_10m_Max | #N/A | WYAW. | RngTmp_10m_Max | Yaw Rim Temp (max) | Yaw Randtemperatur (max) | Temperatura del borde de desplazamiento (max) | Yaw Rim Temp (max) | Yaw rim temperature | deg_c | °C | Maximum | Double | 10 minute tag
WYAW.RngTmp_10m_Min | #N/A | WYAW. | RngTmp_10m_Min | Yaw Rim Temp (min) | Yaw Randtemperatur (min) | Temperatura del borde de desplazamiento (min) | Yaw Rim Temp (min) | Yaw rim temperature | deg_c | °C | Minimum | Double | 10 minute tag
WYAW.RngTmp_10m_Std | #N/A | WYAW. | RngTmp_10m_Std | Yaw Rim Temp (std) | Yaw Randtemperatur (std) | Temperatura del borde de desplazamiento (std) | Yaw Rim Temp (std) | Yaw rim temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WYAW.RotSpd | WYAW.RotSpd | WYAW. | RotSpd | Yaw RPM | Yawdrehzahl | RPM de desplazamiento | Odchylanie RPM | Yaw Rotational speed | rpm | RPM | Live Value | Double | Live Value
WYAW.SysGsLev | WYAW.SysGsLev | WYAW. | SysGsLev | Grease level for lubrication of yaw system | Fettstand für die Schmierung des Yawsystems | Nivel de grasa para la lubricación del sistema de desplazamiento | Poziom smaru do smarowania układu Yaw | Grease level for lubrication of yaw system | Enum | Enum | Live Value | Double
WYAW.Tmp | WYAW.Tmp | WYAW. | Tmp | Yawing Motor Temp | Temperatur des Yawmotors | Temperatura del motor de desplazamiento | Temp silnika ziewania | Yawing motor/gear temperature | deg_c | °C | Live Value | Double | Live Value
WYAW.YwAng | WYAW.YwAng | WYAW. | YwAng | Yaw Angle | Yawwinkel | Ángulo de desplazamiento | Kąt Yaw | Yaw bearing rotational angle relative to nominal true North, 0-360 degrees 0 is north | deg | Degrees | Live Value | Double | Live Value
WYAW.YwAng_10m_Avg | #N/A | WYAW. | YwAng_10m_Avg | Yaw Angle (avg) | Yawwinkel (avg) | Ángulo de desplazamiento (avg) | Kąt Yaw (avg) | Yaw bearing rotational angle relative to nominal true North, 0-360 degrees 0 is north | deg | Degrees | Average | Double | 10 minute tag
WYAW.YwAng_10m_Max | #N/A | WYAW. | YwAng_10m_Max | Yaw Angle (max) | Yawwinkel (max) | Ángulo de desplazamiento (max) | Kąt Yaw (max) | Yaw bearing rotational angle relative to nominal true North, 0-360 degrees 0 is north | deg | Degrees | Maximum | Double | 10 minute tag
WYAW.YwAng_10m_Min | #N/A | WYAW. | YwAng_10m_Min | Yaw Angle (min) | Yawwinkel (min) | Ángulo de desplazamiento (min) | Kąt Yaw (min) | Yaw bearing rotational angle relative to nominal true North, 0-360 degrees 0 is north | deg | Degrees | Minimum | Double | 10 minute tag
WYAW.YwAng_10m_Std | #N/A | WYAW. | YwAng_10m_Std | Yaw Angle (std) | Yawwinkel (std) | Ángulo de desplazamiento (std) | Kąt Yaw (std) | Yaw bearing rotational angle relative to nominal true North, 0-360 degrees 0 is north | deg | Degrees | Standard Deviation | Double | 10 minute tag
WYAW.YwAng2 | #N/A | WYAW. | YwAng2 | Yaw Angle 2 | Yawwinkel 2 | Ángulo de desplazamiento 2 | Kąt Yaw 2 | Yaw bearing rotational angle relative to nominal true North, 0-360 degrees 0 is north | deg | Degrees | Live Value | Double | Live Value
WYAW.YwAng2_10m_Avg | #N/A | WYAW. | YwAng2_10m_Avg | Yaw Angle 2 (avg) | Yawwinkel 2 (avg) | Ángulo de desplazamiento 2 (avg) | Kąt Yaw 2 (avg) | Yaw bearing rotational angle relative to nominal true North, 0-360 degrees 0 is north | deg | Degrees | Average | Double | 10 minute tag
WYAW.YwAng2_10m_Max | #N/A | WYAW. | YwAng2_10m_Max | Yaw Angle 2 (max) | Yawwinkel 2 (max) | Ángulo de desplazamiento 2 (max) | Kąt Yaw 2 (max) | Yaw bearing rotational angle relative to nominal true North, 0-360 degrees 0 is north | deg | Degrees | Maximum | Double | 10 minute tag
WYAW.YwAng2_10m_Min | #N/A | WYAW. | YwAng2_10m_Min | Yaw Angle 2 (min) | Yawwinkel 2 (min) | Ángulo de desplazamiento 2 (min) | Kąt Yaw 2 (min) | Yaw bearing rotational angle relative to nominal true North, 0-360 degrees 0 is north | deg | Degrees | Minimum | Double | 10 minute tag
WYAW.YwAng2_10m_Std | #N/A | WYAW. | YwAng2_10m_Std | Yaw Angle 2 (std) | Yawwinkel 2 (std) | Ángulo de desplazamiento 2 (std) | Kąt Yaw 2 (std) | Yaw bearing rotational angle relative to nominal true North, 0-360 degrees 0 is north | deg | Degrees | Standard Deviation | Double | 10 minute tag
WYAW.YwErr_10m_Avg | #N/A | WYAW. | YwErr_10m_Avg | Yaw error (avg) | Yawfehler (avg) | Error de desplazamiento (avg) | Błąd Yaw (avg) | Yaw error | deg | Degrees | Average | Double | 10 minute tag
WYAW.YwErr_10m_Max | #N/A | WYAW. | YwErr_10m_Max | Yaw error (max) | Yawfehler (max) | Error de desplazamiento (max) | Błąd Yaw (max) | Yaw error | deg | Degrees | Maximum | Double | 10 minute tag
WYAW.YwErr_10m_Min | #N/A | WYAW. | YwErr_10m_Min | Yaw error (min) | Yawfehler (min) | Error de desplazamiento (min) | Błąd Yaw (min) | Yaw error | deg | Degrees | Minimum | Double | 10 minute tag
WYAW.YwErr_10m_Std | #N/A | WYAW. | YwErr_10m_Std | Yaw error (std) | Yawfehler (std) | Error de desplazamiento (std) | Błąd Yaw (std) | Yaw error | deg | Degrees | Standard Deviation | Double | 10 minute tag
WYAW.YwOp | WYAW.YwOp | WYAW. | YwOp | Yaw system command | Yaw-Systembefehl | Comando del sistema de desplazamiento | Polecenie systemu odchylnia | Yaw system command | Enum | Enum | Live Value | Long
WYAW.YwSt | WYAW.YwSt | WYAW. | YwSt | Yaw system Status | Status des Yawsystems | Estado del sistema de desplazamiento | Status systemu odchylnia | Yaw system Status: 1 : Auto operation 2 : Clockwise operation 3 : Yaw blocked 4: Counter clock wise operation 5 : yaw fault | Enum | Enum | Live Value | Long | Live Value
WYAW.YwStCcw | #N/A | WYAW. | YwStCcw | Yaw State Counter Clockwise active | Yaw Status gegen den Uhrzeigersinn aktiv | Contador de estado de desplazamiento en el sentido de las agujas del reloj activo | Yaw Stan zgodnie ze wskazówkami zegara aktywny | Yaw State Counter Clockwise active | Enum | Enum | Live Value | Long | Live Value
WYAW.YwStCw | #N/A | WYAW. | YwStCw | Yaw State Clockwise active | Yaw Status im Uhrzeigersinn aktiv | Estado de desplazamiento en el sentido de las agujas del reloj activo | Yaw Stan licznika zgodnie ze wskazówkami zegara aktywny | Yaw State Clockwise active | Enum | Enum | Live Value | Long | Live Value
WYAW.YwStManu | #N/A | WYAW. | YwStManu | Yaw Manual Status | Manueller Yaw Status | Estado manual de desplazamiento | Ręczny status Yaw | Up in wind status | Enum | Enum | Live Value | Long | Live Value
WYAW.YwStStr | #N/A | WYAW. | YwStStr | Yaw system Status | Yaw Status | Estado del sistema de desplazamiento | Status systemu Yaw | Yaw system Status as string | String | String | Live Value | String | Live Value
WROT.BlPthHyTnkPres1 | #N/A | WROT. | BlPthHyTnkPres1 | Hydraulic Oil Pitch accumulation tank Pressure blade1 | Translate | Translate | Translate | Hydraulic Oil Pitch accumulation tank Pressure blade1 | bar | bar | Live Value | Double | Live Value
WROT.BlPthHyTnkPres1_10m_Avg | #N/A | WROT. | BlPthHyTnkPres1_10m_Avg | Hydraulic Oil Pitch accumulation tank Pressure blade1 (avg) | Translate | Translate | Translate | Hydraulic Oil Pitch accumulation tank Pressure blade1 (avg) | bar | bar | Average | Double | 10 minute tag
WROT.BlPthHyTnkPres1_10m_Max | #N/A | WROT. | BlPthHyTnkPres1_10m_Max | Hydraulic Oil Pitch accumulation tank Pressure blade1 (max) | Translate | Translate | Translate | Hydraulic Oil Pitch accumulation tank Pressure blade1 (max) | bar | bar | Maximum | Double | 10 minute tag
WROT.BlPthHyTnkPres1_10m_Min | #N/A | WROT. | BlPthHyTnkPres1_10m_Min | Hydraulic Oil Pitch accumulation tank Pressure blade1 (min) | Translate | Translate | Translate | Hydraulic Oil Pitch accumulation tank Pressure blade1 (min) | bar | bar | Minimum | Double | 10 minute tag
WROT.BlPthHyTnkPres1_10m_Std | #N/A | WROT. | BlPthHyTnkPres1_10m_Std | Hydraulic Oil Pitch accumulation tank Pressure blade1 (std) | Translate | Translate | Translate | Hydraulic Oil Pitch accumulation tank Pressure blade1 (std) | bar | bar | Standard Deviation | Double | 10 minute tag
WROT.BlPthHyTnkPres2 | #N/A | WROT. | BlPthHyTnkPres2 | Hydraulic Oil Pitch accumulation tank Pressure blade2 | Translate | Translate | Translate | Hydraulic Oil Pitch accumulation tank Pressure blade2 | bar | bar | Live Value | Double | Live Value
WROT.BlPthHyTnkPres2_10m_Avg | #N/A | WROT. | BlPthHyTnkPres2_10m_Avg | Hydraulic Oil Pitch accumulation tank Pressure blade2 (avg) | Translate | Translate | Translate | Hydraulic Oil Pitch accumulation tank Pressure blade2 (avg) | bar | bar | Average | Double | 10 minute tag
WROT.BlPthHyTnkPres2_10m_Max | #N/A | WROT. | BlPthHyTnkPres2_10m_Max | Hydraulic Oil Pitch accumulation tank Pressure blade2 (max) | Translate | Translate | Translate | Hydraulic Oil Pitch accumulation tank Pressure blade2 (max) | bar | bar | Maximum | Double | 10 minute tag
WROT.BlPthHyTnkPres2_10m_Min | #N/A | WROT. | BlPthHyTnkPres2_10m_Min | Hydraulic Oil Pitch accumulation tank Pressure blade2 (min) | Translate | Translate | Translate | Hydraulic Oil Pitch accumulation tank Pressure blade2 (min) | bar | bar | Minimum | Double | 10 minute tag
WROT.BlPthHyTnkPres2_10m_Std | #N/A | WROT. | BlPthHyTnkPres2_10m_Std | Hydraulic Oil Pitch accumulation tank Pressure blade2 (std) | Translate | Translate | Translate | Hydraulic Oil Pitch accumulation tank Pressure blade2 (std) | bar | bar | Standard Deviation | Double | 10 minute tag
WROT.BlPthHyTnkPres3 | #N/A | WROT. | BlPthHyTnkPres3 | Hydraulic Oil Pitch accumulation tank Pressure blade3 | Translate | Translate | Translate | Hydraulic Oil Pitch accumulation tank Pressure blade3 | bar | bar | Live Value | Double | Live Value
WROT.BlPthHyTnkPres3_10m_Avg | #N/A | WROT. | BlPthHyTnkPres3_10m_Avg | Hydraulic Oil Pitch accumulation tank Pressure blade3 (avg) | Translate | Translate | Translate | Hydraulic Oil Pitch accumulation tank Pressure blade3 (avg) | bar | bar | Average | Double | 10 minute tag
WROT.BlPthHyTnkPres3_10m_Max | #N/A | WROT. | BlPthHyTnkPres3_10m_Max | Hydraulic Oil Pitch accumulation tank Pressure blade3 (max) | Translate | Translate | Translate | Hydraulic Oil Pitch accumulation tank Pressure blade3 (max) | bar | bar | Maximum | Double | 10 minute tag
WROT.BlPthHyTnkPres3_10m_Min | #N/A | WROT. | BlPthHyTnkPres3_10m_Min | Hydraulic Oil Pitch accumulation tank Pressure blade3 (min) | Translate | Translate | Translate | Hydraulic Oil Pitch accumulation tank Pressure blade3 (min) | bar | bar | Minimum | Double | 10 minute tag
WROT.BlPthHyTnkPres3_10m_Std | #N/A | WROT. | BlPthHyTnkPres3_10m_Std | Hydraulic Oil Pitch accumulation tank Pressure blade3 (std) | Translate | Translate | Translate | Hydraulic Oil Pitch accumulation tank Pressure blade3 (std) | bar | bar | Standard Deviation | Double | 10 minute tag
WTRM.BrkAccuPres1 | #N/A | WTRM. | BrkAccuPres1 | Hydraulic pressure for brake accumulator 1 | Translate | Translate | Translate | Hydraulic pressure for brake accumulator 1 | bar | bar | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WTRM.BrkAccuPres1_10m_Avg | #N/A | WTRM. | BrkAccuPres1_10m_Avg | Hydraulic pressure for brake accumulator 1 (avg) | Translate | Translate | Translate | Hydraulic pressure for brake accumulator 1 | bar | bar | Average | Double | 10 minute tag
WTRM.BrkAccuPres1_10m_Max | #N/A | WTRM. | BrkAccuPres1_10m_Max | Hydraulic pressure for brake accumulator 1(max) | Translate | Translate | Translate | Hydraulic pressure for brake accumulator 1 | bar | bar | Maximum | Double | 10 minute tag
WTRM.BrkAccuPres1_10m_Min | #N/A | WTRM. | BrkAccuPres1_10m_Min | Hydraulic pressure for brake accumulator 1 (min) | Translate | Translate | Translate | Hydraulic pressure for brake accumulator 1 | bar | bar | Minimum | Double | 10 minute tag
WTRM.BrkAccuPres1_10m_Std | #N/A | WTRM. | BrkAccuPres1_10m_Std | Hydraulic pressure for brake accumulator 1 (std) | Translate | Translate | Translate | Hydraulic pressure for brake accumulator 1 | bar | bar | Standard Deviation | Double | 10 minute tag
WTRM.BrkAccuPres2 | #N/A | WTRM. | BrkAccuPres2 | Hydraulic pressure for brake accumulator 1 | Translate | Translate | Translate | Hydraulic pressure for brake accumulator 1 | bar | bar | Live Value | Double | Live Value |  |  | New Vestas UA TAG
WTRM.BrkAccuPres2_10m_Avg | #N/A | WTRM. | BrkAccuPres2_10m_Avg | Hydraulic pressure for brake accumulator 1 (avg) | Translate | Translate | Translate | Hydraulic pressure for brake accumulator 1 | bar | bar | Average | Double | 10 minute tag
WTRM.BrkAccuPres2_10m_Max | #N/A | WTRM. | BrkAccuPres2_10m_Max | Hydraulic pressure for brake accumulator 1(max) | Translate | Translate | Translate | Hydraulic pressure for brake accumulator 1 | bar | bar | Maximum | Double | 10 minute tag
WTRM.BrkAccuPres2_10m_Min | #N/A | WTRM. | BrkAccuPres2_10m_Min | Hydraulic pressure for brake accumulator 1 (min) | Translate | Translate | Translate | Hydraulic pressure for brake accumulator 1 | bar | bar | Minimum | Double | 10 minute tag
WTRM.BrkAccuPres2_10m_Std | #N/A | WTRM. | BrkAccuPres2_10m_Std | Hydraulic pressure for brake accumulator 1 (std) | Translate | Translate | Translate | Hydraulic pressure for brake accumulator 1 | bar | bar | Standard Deviation | Double | 10 minute tag
WCNV.AuxVAr | #N/A | WCNV. | AuxVAr | Auxiliary Reactive power | Translate | Translate | Translate | Auxiliary Reactive power | VAr | VAr | Live Value | Double | Live Value
WCNV.AuxVAr_10m_Avg | #N/A | WCNV. | AuxVAr_10m_Avg | Auxiliary Reactive power (avg) | Translate | Translate | Translate | Auxiliary Reactive power | VAr | VAr | Average | Double | 10 minute tag
WCNV.AuxVAr_10m_Max | #N/A | WCNV. | AuxVAr_10m_Max | Auxiliary Reactive power (max) | Translate | Translate | Translate | Auxiliary Reactive power | VAr | VAr | Maximum | Double | 10 minute tag
WCNV.AuxVAr_10m_Min | #N/A | WCNV. | AuxVAr_10m_Min | Auxiliary Reactive power (min) | Translate | Translate | Translate | Auxiliary Reactive power | VAr | VAr | Minimum | Double | 10 minute tag
WCNV.AuxVAr_10m_Std | #N/A | WCNV. | AuxVAr_10m_Std | Auxiliary Reactive power (std) | Translate | Translate | Translate | Auxiliary Reactive power | VAr | VAr | Standard Deviation | Double | 10 minute tag
WCNV.UpcInPNV | #N/A | WCNV. | UpcInPNV | UPC input P-N Voltage | Translate | Translate | Translate | UPC input P-N Voltage | V | V | Live Value | Double | Live Value
WCNV.UpcInPNV_10m_Avg | #N/A | WCNV. | UpcInPNV_10m_Avg | UPC input P-N Voltage (avg) | Translate | Translate | Translate | UPC input P-N Voltage | V | V | Average | Double | 10 minute tag
WCNV.UpcInPNV_10m_Max | #N/A | WCNV. | UpcInPNV_10m_Max | UPC input P-N Voltage (max) | Translate | Translate | Translate | UPC input P-N Voltage | V | V | Maximum | Double | 10 minute tag
WCNV.UpcInPNV_10m_Min | #N/A | WCNV. | UpcInPNV_10m_Min | UPC input P-N Voltage (min) | Translate | Translate | Translate | UPC input P-N Voltage | V | V | Minimum | Double | 10 minute tag
WCNV.UpcInPNV_10m_Std | #N/A | WCNV. | UpcInPNV_10m_Std | UPC input P-N Voltage (std) | Translate | Translate | Translate | UPC input P-N Voltage | V | V | Standard Deviation | Double | 10 minute tag
WCNV.UpcOutPNV | #N/A | WCNV. | UpcOutPNV | UPC Output P-N Voltage | Translate | Translate | Translate | UPC Output P-N Voltage | V | V | Live Value | Double | Live Value
WCNV.UpcOutPNV_10m_Avg | #N/A | WCNV. | UpcOutPNV_10m_Avg | UPC Output P-N Voltage (avg) | Translate | Translate | Translate | UPC Output P-N Voltage | V | V | Average | Double | 10 minute tag
WCNV.UpcOutPNV_10m_Max | #N/A | WCNV. | UpcOutPNV_10m_Max | UPC Output P-N Voltage (max) | Translate | Translate | Translate | UPC Output P-N Voltage | V | V | Maximum | Double | 10 minute tag
WCNV.UpcOutPNV_10m_Min | #N/A | WCNV. | UpcOutPNV_10m_Min | UPC Output P-N Voltage (min) | Translate | Translate | Translate | UPC Output P-N Voltage | V | V | Minimum | Double | 10 minute tag
WCNV.UpcOutPNV_10m_Std | #N/A | WCNV. | UpcOutPNV_10m_Std | UPC Output P-N Voltage (std) | Translate | Translate | Translate | UPC Output P-N Voltage | V | V | Standard Deviation | Double | 10 minute tag
WCNV.GenCnt | #N/A | WCNV. | GenCnt | Number of activations of the Generator contactor | Translate | Translate | Translate | Number of activations of the Generator contactor | count | Count | Total Counter | Long | Live Value
WCNV.GenCnt_10m_End | #N/A | WCNV. | GenCnt_10m_End | Number of activations of the Generator contactor (end) | Translate | Translate | Translate | Number of activations of the Generator contactor | count | Count | Endvalue | Long | 10 minute tag
WTRM.MainBrgLubOilTmp | #N/A | WTRM. | MainBrgLubOilTmp | Main Bearing Lubricant Oil Tank Temp | Translate | Translate | Translate | Main Bearing Lubricant Oil Tank Temp | deg_c | °C | Live Value | Double | Live Value
WTRM.MainBrgLubOilTmp_10m_Avg | #N/A | WTRM. | MainBrgLubOilTmp_10m_Avg | Main Bearing Lubricant Oil Tank Temp (avg) | Translate | Translate | Translate | Main Bearing Lubricant Oil Tank Temp | deg_c | °C | Average | Double | 10 minute tag
WTRM.MainBrgLubOilTmp_10m_Max | #N/A | WTRM. | MainBrgLubOilTmp_10m_Max | Main Bearing Lubricant Oil Tank Temp (max) | Translate | Translate | Translate | Main Bearing Lubricant Oil Tank Temp | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.MainBrgLubOilTmp_10m_Min | #N/A | WTRM. | MainBrgLubOilTmp_10m_Min | Main Bearing Lubricant Oil Tank Temp (min) | Translate | Translate | Translate | Main Bearing Lubricant Oil Tank Temp | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.MainBrgLubOilTmp_10m_Std | #N/A | WTRM. | MainBrgLubOilTmp_10m_Std | Main Bearing Lubricant Oil Tank Temp (std) | Translate | Translate | Translate | Main Bearing Lubricant Oil Tank Temp | deg_c | °C | Standard Deviation | Double | 10 minute tag
WTRM.GbxOilLubOilTnkTmp | #N/A | WTRM. | GbxOilLubOilTnkTmp | Gear Box Lubricant Oil Tank Temp | Translate | Translate | Translate | Gear Box Lubricant Oil Tank Temp | deg_c | °C | Live Value | Double | Live Value
WTRM.GbxOilLubOilTnkTmp_10m_Avg | #N/A | WTRM. | GbxOilLubOilTnkTmp_10m_Avg | Gear Box Lubricant Oil Tank Temp (avg) | Translate | Translate | Translate | Gear Box Lubricant Oil Tank Temp | deg_c | °C | Average | Double | 10 minute tag
WTRM.GbxOilLubOilTnkTmp_10m_Max | #N/A | WTRM. | GbxOilLubOilTnkTmp_10m_Max | Gear Box Lubricant Oil Tank Temp (max) | Translate | Translate | Translate | Gear Box Lubricant Oil Tank Temp | deg_c | °C | Maximum | Double | 10 minute tag
WTRM.GbxOilLubOilTnkTmp_10m_Min | #N/A | WTRM. | GbxOilLubOilTnkTmp_10m_Min | Gear Box Lubricant Oil Tank Temp (min) | Translate | Translate | Translate | Gear Box Lubricant Oil Tank Temp | deg_c | °C | Minimum | Double | 10 minute tag
WTRM.GbxOilLubOilTnkTmp_10m_Std | #N/A | WTRM. | GbxOilLubOilTnkTmp_10m_Std | Gear Box Lubricant Oil Tank Temp (std) | Translate | Translate | Translate | Gear Box Lubricant Oil Tank Temp | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.HtexTmp1 | #N/A | WCNV. | HtexTmp1 | Lower Heat Exchanger Temp | Translate | Translate | Translate | Temperature of heat exchanger (lower) | deg_c | °C | Live Value | Double | Live Value
WCNV.HtexTmp1_10m_Avg | #N/A | WCNV. | HtexTmp1_10m_Avg | Lower Heat Exchanger Temp (avg) | Translate | Translate | Translate | Temperature of heat exchanger (lower) | deg_c | °C | Average | Double | 10 minute tag
WCNV.HtexTmp1_10m_Max | #N/A | WCNV. | HtexTmp1_10m_Max | Lower Heat Exchanger Temp (max) | Translate | Translate | Translate | Temperature of heat exchanger (lower) | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.HtexTmp1_10m_Min | #N/A | WCNV. | HtexTmp1_10m_Min | Lower Heat Exchanger Temp (min) | Translate | Translate | Translate | Temperature of heat exchanger (lower) | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.HtexTmp1_10m_Std | #N/A | WCNV. | HtexTmp1_10m_Std | Lower Heat Exchanger Temp (std) | Translate | Translate | Translate | Temperature of heat exchanger (lower) | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.HtexTmp2 | #N/A | WCNV. | HtexTmp2 | Upper Heat Exchanger Temp | Translate | Translate | Translate | Temperature of heat exchanger (Upper) | deg_c | °C | Live Value | Double | Live Value
WCNV.HtexTmp2_10m_Avg | #N/A | WCNV. | HtexTmp2_10m_Avg | Upper Heat Exchanger Temp (avg) | Translate | Translate | Translate | Temperature of heat exchanger (Upper) | deg_c | °C | Average | Double | 10 minute tag
WCNV.HtexTmp2_10m_Max | #N/A | WCNV. | HtexTmp2_10m_Max | Upper Heat Exchanger Temp (max) | Translate | Translate | Translate | Temperature of heat exchanger (Upper) | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.HtexTmp2_10m_Min | #N/A | WCNV. | HtexTmp2_10m_Min | Upper Heat Exchanger Temp (min) | Translate | Translate | Translate | Temperature of heat exchanger (Upper) | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.HtexTmp2_10m_Std | #N/A | WCNV. | HtexTmp2_10m_Std | Upper Heat Exchanger Temp (std) | Translate | Translate | Translate | Temperature of heat exchanger (Upper) | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.ClWtrInletTmp | #N/A | WCNV. | ClWtrInletTmp | Converter Cooling Water Inlet Temp | Translate | Translate | Translate | Converter Cooling Water Inlet Temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.ClWtrInletTmp_10m_Avg | #N/A | WCNV. | ClWtrInletTmp_10m_Avg | Converter Cooling Water Inlet Temp (avg) | Translate | Translate | Translate | Converter Cooling Water Inlet Temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.ClWtrInletTmp_10m_Max | #N/A | WCNV. | ClWtrInletTmp_10m_Max | Converter Cooling Water Inlet Temp (max) | Translate | Translate | Translate | Converter Cooling Water Inlet Temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.ClWtrInletTmp_10m_Min | #N/A | WCNV. | ClWtrInletTmp_10m_Min | Converter Cooling Water Inlet Temp (min) | Translate | Translate | Translate | Converter Cooling Water Inlet Temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.ClWtrInletTmp_10m_Std | #N/A | WCNV. | ClWtrInletTmp_10m_Std | Converter Cooling Water Inlet Temp (std) | Translate | Translate | Translate | Converter Cooling Water Inlet Temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.ClWtrOutletTmp | #N/A | WCNV. | ClWtrOutletTmp | Converter Cooling Water Outlet Temp | Translate | Translate | Translate | Converter Cooling Water Outlet Temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.ClWtrOutletTmp_10m_Avg | #N/A | WCNV. | ClWtrOutletTmp_10m_Avg | Converter Cooling Water Outlet Temp (avg) | Translate | Translate | Translate | Converter Cooling Water Outlet Temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.ClWtrOutletTmp_10m_Max | #N/A | WCNV. | ClWtrOutletTmp_10m_Max | Converter Cooling Water Outlet Temp (max) | Translate | Translate | Translate | Converter Cooling Water Outlet Temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.ClWtrOutletTmp_10m_Min | #N/A | WCNV. | ClWtrOutletTmp_10m_Min | Converter Cooling Water Outlet Temp (min) | Translate | Translate | Translate | Converter Cooling Water Outlet Temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.ClWtrOutletTmp_10m_Std | #N/A | WCNV. | ClWtrOutletTmp_10m_Std | Converter Cooling Water Outlet Temp (std) | Translate | Translate | Translate | Converter Cooling Water Outlet Temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.RectInductTmp | #N/A | WCNV. | RectInductTmp | Rectifier Side Inductance Temp | Translate | Translate | Translate | Rectifier Side Inductance Temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.RectInductTmp_10m_Avg | #N/A | WCNV. | RectInductTmp_10m_Avg | Rectifier Side Inductance Temp (avg) | Translate | Translate | Translate | Rectifier Side Inductance Temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.RectInductTmp_10m_Max | #N/A | WCNV. | RectInductTmp_10m_Max | Rectifier Side Inductance Temp (max) | Translate | Translate | Translate | Rectifier Side Inductance Temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.RectInductTmp_10m_Min | #N/A | WCNV. | RectInductTmp_10m_Min | Rectifier Side Inductance Temp (min) | Translate | Translate | Translate | Rectifier Side Inductance Temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.RectInductTmp_10m_Std | #N/A | WCNV. | RectInductTmp_10m_Std | Rectifier Side Inductance Temp (std) | Translate | Translate | Translate | Rectifier Side Inductance Temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.RotInductTmp | #N/A | WCNV. | RotInductTmp | Rotor Side Inductance Temp | Translate | Translate | Translate | Rotor Side Inductance Temperature | deg_c | °C | Live Value | Double | Live Value
WCNV.RotInductTmp_10m_Avg | #N/A | WCNV. | RotInductTmp_10m_Avg | Rotor Side Inductance Temp (avg) | Translate | Translate | Translate | Rotor Side Inductance Temperature | deg_c | °C | Average | Double | 10 minute tag
WCNV.RotInductTmp_10m_Max | #N/A | WCNV. | RotInductTmp_10m_Max | Rotor Side Inductance Temp (max) | Translate | Translate | Translate | Rotor Side Inductance Temperature | deg_c | °C | Maximum | Double | 10 minute tag
WCNV.RotInductTmp_10m_Min | #N/A | WCNV. | RotInductTmp_10m_Min | Rotor Side Inductance Temp (min) | Translate | Translate | Translate | Rotor Side Inductance Temperature | deg_c | °C | Minimum | Double | 10 minute tag
WCNV.RotInductTmp_10m_Std | #N/A | WCNV. | RotInductTmp_10m_Std | Rotor Side Inductance Temp (std) | Translate | Translate | Translate | Rotor Side Inductance Temperature | deg_c | °C | Standard Deviation | Double | 10 minute tag
WCNV.AuxW | #N/A | WCNV. | AuxW | Auxiliary Active power | Translate | Translate | Translate | Auxiliary Active power | W | W | Live Value | Double | Live Value
WCNV.AuxW_10m_Avg | #N/A | WCNV. | AuxW_10m_Avg | Auxiliary Active power (avg) | Translate | Translate | Translate | Auxiliary Active power | W | W | Average | Double | 10 minute tag
WCNV.AuxW_10m_Max | #N/A | WCNV. | AuxW_10m_Max | Auxiliary Active power (max) | Translate | Translate | Translate | Auxiliary Active power | W | W | Maximum | Double | 10 minute tag
WCNV.AuxW_10m_Min | #N/A | WCNV. | AuxW_10m_Min | Auxiliary Active power (min) | Translate | Translate | Translate | Auxiliary Active power | W | W | Minimum | Double | 10 minute tag
WCNV.AuxW_10m_Std | #N/A | WCNV. | AuxW_10m_Std | Auxiliary Active power (std) | Translate | Translate | Translate | Auxiliary Active power | W | W | Standard Deviation | Double | 10 minute tag
WCNV.GriPPV_10m_Avg | #N/A | WCNV. | GriPPV_10m_Avg | Converter P-P Voltage Grid side (avg) | Konverter P-P Spannung Netzseite (avg) | Tensión P-P del convertidor en el lado de la red eléctrica (avg) | Konwerter P-P Nap. strona sieci (avg) | Grid side 3 phase phase-to-phase voltage | V | V | Average | Double | 10 minute tag
WCNV.GriPPV_10m_Max | #N/A | WCNV. | GriPPV_10m_Max | Converter P-P Voltage Grid side (max) | Konverter P-P Spannung Netzseite (max) | Tensión P-P del convertidor en el lado de la red eléctrica (max) | Konwerter P-P Nap. strona sieci (max) | Grid side 3 phase phase-to-phase voltage | V | V | Maximum | Double | 10 minute tag
WCNV.GriPPV_10m_Min | #N/A | WCNV. | GriPPV_10m_Min | Converter P-P Voltage Grid side (min) | Konverter P-P Spannung Netzseite (min) | Tensión P-P del convertidor en el lado de la red eléctrica (min) | Konwerter P-P Nap. strona sieci (min) | Grid side 3 phase phase-to-phase voltage | V | V | Minimum | Double | 10 minute tag
WCNV.GriPPV_10m_Std | #N/A | WCNV. | GriPPV_10m_Std | Converter P-P Voltage Grid side (std) | Konverter P-P Spannung Netzseite (std) | Tensión P-P del convertidor en el lado de la red eléctrica (std) | Konwerter P-P Nap. strona sieci (std) | Grid side 3 phase phase-to-phase voltage | V | V | Standard Deviation | Double | 10 minute tag
WCNV.SttPPV_10m_Avg | #N/A | WCNV. | SttPPV_10m_Avg | Converter P-P Voltage Stator side (avg) | Konverter P-P Spannung Statorseite (avg) | Tensión P-N en el lado del estátor del generador | Wentylator P-P Strona stojana napięcia | Converter stator 3 phase phase-to-phase voltage | V | V | Average | Double | 10 minute tag
WCNV.SttPPV_10m_Max | #N/A | WCNV. | SttPPV_10m_Max | Converter P-P Voltage Stator side (max) | Konverter P-P Spannung Statorseite (max) | Tensión P-N en el lado del estátor del generador | Wentylator P-P Strona stojana napięcia | Converter stator 3 phase phase-to-phase voltage | V | V | Maximum | Double | 10 minute tag
WCNV.SttPPV_10m_Min | #N/A | WCNV. | SttPPV_10m_Min | Converter P-P Voltage Stator side (min) | Konverter P-P Spannung Statorseite (min) | Tensión P-N en el lado del estátor del generador | Wentylator P-P Strona stojana napięcia | Converter stator 3 phase phase-to-phase voltage | V | V | Minimum | Double | 10 minute tag
WCNV.SttPPV_10m_Std | #N/A | WCNV. | SttPPV_10m_Std | Converter P-P Voltage Stator side (std) | Konverter P-P Spannung Statorseite (std) | Tensión P-N en el lado del estátor del generador | Wentylator P-P Strona stojana napięcia | Converter stator 3 phase phase-to-phase voltage | V | V | Standard Deviation | Double | 10 minute tag
WGEN.SttPPV_10m_Avg | #N/A | WGEN. | SttPPV_10m_Avg | Generator P-P Voltage Stator side (avg) | Translate | Translate | Translate | Generator stator 3 phase phase-to-phase voltage | V | V | Average | Double | 10 minute tag
WGEN.SttPPV_10m_Max | #N/A | WGEN. | SttPPV_10m_Max | Generator P-P Voltage Stator side (max) | Translate | Translate | Translate | Generator stator 3 phase phase-to-phase voltage | V | V | Maximum | Double | 10 minute tag
WGEN.SttPPV_10m_Min | #N/A | WGEN. | SttPPV_10m_Min | Generator P-P Voltage Stator side (min) | Translate | Translate | Translate | Generator stator 3 phase phase-to-phase voltage | V | V | Minimum | Double | 10 minute tag
WGEN.SttPPV_10m_Std | #N/A | WGEN. | SttPPV_10m_Std | Generator P-P Voltage Stator side (std) | Translate | Translate | Translate | Generator stator 3 phase phase-to-phase voltage | V | V | Standard Deviation | Double | 10 minute tag
WROT.HubCtlTmp_10m_Max | #N/A | WROT. | HubCtlTmp_10m_Max | Rotor Hub Controller Temp (max) | Reglertemperatur der Rotornabe (max) | Temperatura del controlador del buje del rotor (max) | Temp kontrolera Hub rotora (max) | Temperature in the rotor hub controller | deg_c | °C | Maximum | Double | 10 minute tag
WROT.HubCtlTmp_10m_Min | #N/A | WROT. | HubCtlTmp_10m_Min | Rotor Hub Controller Temp (min) | Reglertemperatur der Rotornabe (min) | Temperatura del controlador del buje del rotor (min) | Temp kontrolera Hub rotora (min) | Temperature in the rotor hub controller | deg_c | °C | Minimum | Double | 10 minute tag
WROT.HubCtlTmp_10m_Std | #N/A | WROT. | HubCtlTmp_10m_Std | Rotor Hub Controller Temp (std) | Reglertemperatur der Rotornabe (std) | Temperatura del controlador del buje del rotor (std) | Temp kontrolera Hub rotora (std) | Temperature in the rotor hub controller | deg_c | °C | Standard Deviation | Double | 10 minute tag

## Logic nodes IEC 61400-25-2
IEC

## Standard Tags IEC 61400-25-2
TAG Name | Node | Data Object Name | Common Data Class | Explanation | IEC Standard
WALM.AlmSt | WALM. | AlmSt | AST | Alarm set status | IEC
WAPC.CutHiTurNum | WAPC. | CutHiTurNum | INS | Number of turbines not running due to high wind speed | IEC
WAPC.CutLoTurNum | WAPC. | CutLoTurNum | INS | Number of turbines not running due to low wind speed | IEC
WAPC.DelAct | WAPC. | DelAct | CMD | Activate delta control function | IEC
WAPC.DelEna | WAPC. | DelEna | STV | Delta function enabled | IEC
WAPC.DelSpt | WAPC. | DelSpt | SPV | Set reference value for the delta function, wind power plant active power reserve | IEC
WAPC.Gra | WAPC. | Gra | MV | Wind power plant gradient | IEC
WAPC.GraAct | WAPC. | GraAct | CMD | Activate gradient control function | IEC
WAPC.GraEna | WAPC. | GraEna | STV | Gradient function enabled | IEC
WAPC.OpTurNum | WAPC. | OpTurNum | INS | Actual number of wind turbines in operation | IEC
WAPC.VA | WAPC. | VA | MV | Wind power plant apparent power | IEC
WAPC.VAAct | WAPC. | VAAct | CMD | Activate apparent power control function | IEC
WAPC.VAEna | WAPC. | VAEna | STV | Active power control mode enabled controlling apparent power | IEC
WAPC.VASpt | WAPC. | VASpt | SPV | Set reference value for the wind power plant apparent power output | IEC
WAPC.W | WAPC. | W | MV | Wind power plant active generation | IEC
WAPC.WAct | WAPC. | WAct | CMD | Activate active power control function | IEC
WAPC.WCap | WAPC. | WCap | MV | Wind power plant active power output capability | IEC
WAPC.WDel | WAPC. | WDel | MV | Wind power plant active power reserve utilizing the delta function – the difference between active power generation capability and active | IEC
WAPC.WDnGraSpt | WAPC. | WDnGraSpt | SPV | Set reference value for gradient ramping down the wind power plant active power output | IEC
WAPC.WLimEna | WAPC. | WLimEna | STV | Active power limitation mode enabled | IEC
WAPC.WMinCap | WAPC. | WMinCap | MV | Wind power plant minimum capability active power | IEC
WAPC.WSpt | WAPC. | WSpt | SPV | Set reference value for the wind power plant active power output | IEC
WAPC.WUpGraSpt | WAPC. | WUpGraSpt | SPV | Set reference value for gradient ramping up the wind power plant active power output | IEC
WAVL.AvlTmsRs | WAVL. | AvlTmsRs | TMS | Turbine availability time in seconds (implementation specific) | IEC
WAVL.Ia | WAVL. | Ia | INC | Information available | IEC
WAVL.Iafm | WAVL. | Iafm | INC | Information available force majeure | IEC
WAVL.Iano | WAVL. | Iano | INC | Information available nonoperative | IEC
WAVL.Ianofo | WAVL. | Ianofo | INC | Information available nonoperative forced outage | IEC
WAVL.Ianopca | WAVL. | Ianopca | INC | Information available nonoperative planned corrective actions | IEC
WAVL.Ianos | WAVL. | Ianos | INC | Information available nonoperative suspended | IEC
WAVL.Ianosm | WAVL. | Ianosm | INC | Information available nonoperative scheduled maintenance | IEC
WAVL.Iao | WAVL. | Iao | INC | Information available operative | IEC
WAVL.Iaog | WAVL. | Iaog | INC | Information available operative generating | IEC
WAVL.Iaogfp | WAVL. | Iaogfp | INC | Information available operative generating with full performance | IEC
WAVL.Iaogpp | WAVL. | Iaogpp | INC | Information available operative generating with partial performance | IEC
WAVL.Iaong | WAVL. | Iaong | INC | Information available operative nongenerating | IEC
WAVL.Iaongel | WAVL. | Iaongel | INC | Information available operative nongenerating out of electrical specification | IEC
WAVL.Iaongen | WAVL. | Iaongen | INC | Information available operative nongenerating out of environmental specification | IEC
WAVL.Iaongrs | WAVL. | Iaongrs | INC | Information available operative nongenerating requested shutdown | IEC
WAVL.Iaongts | WAVL. | Iaongts | INC | Information available operative nongenerating technical standby | IEC
WAVL.Iu | WAVL. | Iu | INC | Information unavailable | IEC
WAVL.OpTmsRs | WAVL. | OpTmsRs | TMS | Operation time in seconds (implementation specific) | IEC
WAVL.SysAvl | WAVL. | SysAvl | MV | System availability (implementation specific) | IEC
WAVL.TurAvl | WAVL. | TurAvl | MV | Turbine availability (implementation specific) | IEC
WCNV.ClSt | WCNV. | ClSt | STV | Status of converter cooling system | IEC
WCNV.CnvOpSt | WCNV. | CnvOpSt | STV | Status of converter | IEC
WCNV.DclA | WCNV. | DclA | MV | DC-link current inside converter | IEC
WCNV.DclTmp | WCNV. | DclTmp | MV | Temperature inside the converter | IEC
WCNV.DclV | WCNV. | DclV | MV | DC-link voltage inside converter | IEC
WCNV.GnA | WCNV. | GnA | WYE | Generator side 3 phase current | IEC
WCNV.GnHz | WCNV. | GnHz | MV | Generator side frequency | IEC
WCNV.GnPF | WCNV. | GnPF | WYE | Generator side 3 phase power factor | IEC
WCNV.GnPNV | WCNV. | GnPNV | WYE | Generator side 3 phase-to-neutral voltage | IEC
WCNV.GnPPV | WCNV. | GnPPV | DEL | Generator side 3 phase phase-to-phase voltage | IEC
WCNV.GnTmp | WCNV. | GnTmp | MV | Generator side temperature | IEC
WCNV.GriA | WCNV. | GriA | WYE | Grid side 3 phase current | IEC
WCNV.GriHz | WCNV. | GriHz | MV | Grid side frequency | IEC
WCNV.GriPF | WCNV. | GriPF | WYE | Grid side 3 phase power factor | IEC
WCNV.GriPNV | WCNV. | GriPNV | WYE | Grid side 3 phase-to-neutral voltage | IEC
WCNV.GriPPV | WCNV. | GriPPV | DEL | Grid side 3 phase phase-to-phase voltage | IEC
WCNV.GriTmp | WCNV. | GriTmp | MV | Grid side temperature | IEC
WCNV.OpTmsRs | WCNV. | OpTmsRs | TMS | Converter operation time in seconds (vendor specific) | IEC
WCNV.Torq | WCNV. | Torq | MV | Torque value | IEC
WGEN.ClSt | WGEN. | ClSt | STV | Status of generator cooling system | IEC
WGEN.GnOpSt | WGEN. | GnOpSt | STV | Status of generator | IEC
WGEN.InletTmp | WGEN. | InletTmp |  | Temperature measurement for inlet air/water temperature at generator | IEC
WGEN.OpTmsRs | WGEN. | OpTmsRs | TMS | Generator operation time in seconds (vendor specific) | IEC
WGEN.RotA | WGEN. | RotA | WYE | Generator rotor 3 phase current | IEC
WGEN.RotExtAC | WGEN. | RotExtAC | MV | Generator rotor alternating current excitation | IEC
WGEN.RotExtDC | WGEN. | RotExtDC | MV | Generator rotor direct current excitation | IEC
WGEN.RotPNV | WGEN. | RotPNV | WYE | Generator rotor 3 phase-to-neutral voltage | IEC
WGEN.RotPPV | WGEN. | RotPPV | DEL | Generator rotor 3 phase phase-to-phase voltage | IEC
WGEN.RotSpd | WGEN. | RotSpd | MV | Rotational speed | IEC
WGEN.RotTmp | WGEN. | RotTmp | MV | Temperature measurements for generator rotor | IEC
WGEN.SttA | WGEN. | SttA | WYE | Generator stator 3 phase current | IEC
WGEN.SttPNV | WGEN. | SttPNV | WYE | Generator stator 3 phase phase-to-neutral voltage | IEC
WGEN.SttPPV | WGEN. | SttPPV | DEL | Generator stator 3 phase phase-to-phase voltage | IEC
WGEN.SttTmp | WGEN. | SttTmp | MV | Temperature measurements for generator stator | IEC
WGEN.VAr | WGEN. | VAr | WYE | Generator reactive power | IEC
WGEN.W | WGEN. | W | WYE | Generator active power | IEC
WMET.AirDen | WMET. | AirDen | MV | Density of air | IEC
WMET.Alt | WMET. | Alt | MV | Sensor altitude | IEC
WMET.CloudCvr | WMET. | CloudCvr | MV | Cloud cover level | IEC
WMET.DctInsol | WMET. | DctInsol | MV | Direct normal insolation | IEC
WMET.DewPt | WMET. | DewPt | MV | Dew point | IEC
WMET.DffInsol | WMET. | DffInsol | MV | Diffuse insolation | IEC
WMET.DlDur | WMET. | DlDur | MV | Daylight duration (time elapsed between sunrise and sunset) | IEC
WMET.EnvHum | WMET. | EnvHum | MV | Humidity | IEC
WMET.EnvPres | WMET. | EnvPres | MV | Barometric pressure | IEC
WMET.EnvTmp | WMET. | EnvTmp | MV | Ambient temperature | IEC
WMET.HorInsol | WMET. | HorInsol | MV | Total horizontal insolation | IEC
WMET.HorWdDir | WMET. | HorWdDir | MV | Horizontal wind direction | IEC
WMET.HorWdSpd | WMET. | HorWdSpd | MV | Horizontal wind speed | IEC
WMET.Ice | WMET. | Ice | MV | Thickness of ice | IEC
WMET.IceSt | WMET. | IceSt | STV | Status of ice detection | IEC
WMET.RnFll | WMET. | RnFll | MV | Rainfall | IEC
WMET.SnwCvr | WMET. | SnwCvr | MV | Snow cover | IEC
WMET.SnwDen | WMET. | SnwDen | MV | Density of snowfall | IEC
WMET.SnwEq | WMET. | SnwEq | MV | Water equivalent of snowfall | IEC
WMET.SnwFll | WMET. | SnwFll | MV | Snowfall | IEC
WMET.SnwTmp | WMET. | SnwTmp | MV | Temperature of snowfall | IEC
WMET.VerWdDir | WMET. | VerWdDir | MV | Vertical wind direction | IEC
WMET.VerWdSpd | WMET. | VerWdSpd | MV | Vertical wind speed | IEC
WMET.WdGustSpd | WMET. | WdGustSpd | MV | Wind gust speed | IEC
WMET.WetBlbTmp | WMET. | WetBlbTmp | MV | Wet bulb temperature | IEC
WMET.WtrTmp | WMET. | WtrTmp | MV | Temperature of water | IEC
WNAC.AneSt | WNAC. | AneSt | STV | Status of primary anemometer /secondary anemometer | IEC
WNAC.BecBlbSt | WNAC. | BecBlbSt | STV | Status of beacon | IEC
WNAC.BecLevSpt | WNAC. | BecLevSpt | SPV | Setpoint bulb light level of beacon | IEC
WNAC.BecLumLev | WNAC. | BecLumLev | MV | Value of luminosity level of beacon | IEC
WNAC.BecMod | WNAC. | BecMod | CMD | Set modus of beacon | IEC
WNAC.Dir | WNAC. | Dir | MV | Nacelle orientation | IEC
WNAC.FlshSpt | WNAC. | FlshSpt | SPV | Setpoint value of flash duty cycle of beacon | IEC
WNAC.IntnHum | WNAC. | IntnHum | MV | Humidity inside component | IEC
WNAC.IntnTmp | WNAC. | IntnTmp | MV | Temperature inside component | IEC
WNAC.OpTmsRs | WNAC. | OpTmsRs | TMS | Operation time of beacon in seconds (vendor specific) | IEC
WNAC.Vis | WNAC. | Vis | MV | Visibility outside nacelle | IEC
WNAC.WdHtSt | WNAC. | WdHtSt | STV | Status of heater for wind sensor | IEC
WNAC.XdirDsp | WNAC. | XdirDsp | MV | Tower displacement (longitudinal direction) | IEC
WNAC.YdirDsp | WNAC. | YdirDsp | MV | Tower displacement (lateral direction) | IEC
WROT.BlPthAngTgt | WROT. | BlPthAngTgt | MV | Pitch angle target value | IEC
WROT.BlPthAngVal | WROT. | BlPthAngVal | MV | Pitch angle for blade as feedback from the pitch system | IEC
WROT.BlPthHyPres | WROT. | BlPthHyPres | MV | Pressure of hydraulic pitch system | IEC
WROT.BlSt | WROT. | BlSt | STV | Status of blade as feedback from the pitch system | IEC
WROT.HubTmp | WROT. | HubTmp | MV | Temperature in the rotor hub | IEC
WROT.PthCtlSt | WROT. | PthCtlSt | STV | Status of pitch control | IEC
WROT.PthEmgChk | WROT. | PthEmgChk | CMD | Check emergency pitch system | IEC
WROT.RotBlk | WROT. | RotBlk | CMD | Block rotor position command | IEC
WROT.RotPos | WROT. | RotPos | MV | Angular rotor position | IEC
WROT.RotSpd | WROT. | RotSpd | MV | Rotational speed | IEC
WROT.RotSt | WROT. | RotSt | STV | Status of rotor | IEC
WRPC.DrpSpt | WRPC. | DrpSpt | SPV | Set reference value for slope of voltage control droop | IEC
WRPC.OpTurNum | WRPC. | OpTurNum | INS | Actual number of wind turbines in operation | IEC
WRPC.PF | WRPC. | PF | MV | Wind power plant actual power factor | IEC
WRPC.PFSign | WRPC. | PFSign | INS | Power factor sign convention: IEEE = 2 | IEC
WRPC.PFSpt | WRPC. | PFSpt | SPV | Set reference value for wind power plant power factor – negative: lagging (producing reactive power); positive: leading (consuming reactive power) as defined by IEEE | IEC
WRPC.V | WRPC. | V | MV | Wind power plant output voltage at the external grid connection point | IEC
WRPC.VAr | WRPC. | VAr | MV | Wind power plant reactive power generation | IEC
WRPC.VArAct | WRPC. | VArAct | CMD | Activate reactive power control function | IEC
WRPC.VArCapExpt | WRPC. | VArCapExpt | MV | Wind power plant reactive power export (supply) capability | IEC
WRPC.VArCapImpt | WRPC. | VArCapImpt | MV | Wind power plant reactive power import (demand) capability | IEC
WRPC.VArDnGraSpt | WRPC. | VArDnGraSpt | SPV | Set reference value for gradient for ramping down the wind power plant reactive power output | IEC
WRPC.VArMinCap | WRPC. | VArMinCap | MV | Wind power plant minimum reactive power capability of plant | IEC
WRPC.VArMod | WRPC. | VArMod | STV | Reactive power control mode | IEC
WRPC.VArSpt | WRPC. | VArSpt | SPV | Set reference value of wind power plant reactive power output | IEC
WRPC.VArUpGraSpt | WRPC. | VArUpGraSpt | SPV | Set reference value for gradient for ramping up the wind power plant reactive power output | IEC
WRPC.VDnGraSpt | WRPC. | VDnGraSpt | SPV | Set reference value for wind power plant voltage ramping down | IEC
WRPC.VSpt | WRPC. | VSpt | SPV | Set reference value for wind power plant voltage output | IEC
WRPC.VUpGraSpt | WRPC. | VUpGraSpt | SPV | Set reference value for wind power plant voltage ramping up | IEC
WTOW.DehumSt | WTOW. | DehumSt | STV | Status of de-humidifier | IEC
WTOW.HtexSt | WTOW. | HtexSt | STV | Status of heat-exchanger | IEC
WTOW.IntnHum | WTOW. | IntnHum | MV | Humidity inside tower | IEC
WTOW.LftPos | WTOW. | LftPos | MV | Lift position | IEC
WTOW.LftSt | WTOW. | LftSt | STV | Status of lift system | IEC
WTRF.ClSt | WTRF. | ClSt | STV | Status of transformer cooling system | IEC
WTRF.GriA | WTRF. | GriA | WYE | Grid side 3 phase current | IEC
WTRF.GriPNV | WTRF. | GriPNV | WYE | Grid side 3 phase-to-neutral voltage | IEC
WTRF.GriPPV | WTRF. | GriPPV | DEL | Grid side 3 phase phase-to-phase voltage | IEC
WTRF.GriSwOp | WTRF. | GriSwOp | CMD | Main grid switch command | IEC
WTRF.GriTmp | WTRF. | GriTmp | MV | Temperature on grid side | IEC
WTRF.OilLevSt | WTRF. | OilLevSt | STV | Oil level status information for oil filled transformers | IEC
WTRF.OpTmsRs | WTRF. | OpTmsRs | TMS | Transformer operation time in seconds (vendor specific) | IEC
WTRF.TnkPresSt | WTRF. | TnkPresSt | STV | Gas pressure status of main tank for oil filled transformers | IEC
WTRF.TurA | WTRF. | TurA | WYE | Turbine side 3 phase current | IEC
WTRF.TurPNV | WTRF. | TurPNV | WYE | Turbine side 3 phase-to-neutral voltage | IEC
WTRF.TurPPV | WTRF. | TurPPV | DEL | Turbine side 3 phase phase-to-phase voltage | IEC
WTRF.TurTmp | WTRF. | TurTmp | MV | Temperature on turbine side | IEC
WTRM.BrkHyPres | WTRM. | BrkHyPres | MV | Hydraulic pressure for shaft brake | IEC
WTRM.BrkOpSt | WTRM. | BrkOpSt | STV | Status of shaft brake | IEC
WTRM.ClSt | WTRM. | ClSt | STV | Status of transmission cooling system | IEC
WTRM.FilSt | WTRM. | FilSt | STV | Status of filtration system | IEC
WTRM.GbxOilLev | WTRM. | GbxOilLev | MV | Oil level in gearbox sump | IEC
WTRM.GbxOilPres | WTRM. | GbxOilPres | MV | Gear oil pressure | IEC
WTRM.GbxOilTmp | WTRM. | GbxOilTmp | MV | Measured temperature of gearbox oil | IEC
WTRM.GbxVbr | WTRM. | GbxVbr | MV | Measured gearbox vibration of gearbox | IEC
WTRM.GsLev | WTRM. | GsLev | MV | Grease level for lubrication of main shaft bearing | IEC
WTRM.HtSt | WTRM. | HtSt | STV | Status of heating system | IEC
WTRM.InlFil | WTRM. | InlFil | MV | Inline filter contamination | IEC
WTRM.InlFilSt | WTRM. | InlFilSt | STV | Status of inline filter contamination | IEC
WTRM.LuSt | WTRM. | LuSt | STV | Status of gearbox lubrication system | IEC
WTRM.OfFil | WTRM. | OfFil | MV | Offline filter contamination | IEC
WTRM.OfFilSt | WTRM. | OfFilSt | STV | Status of offline filter contamination | IEC
WTRM.OilLevSt | WTRM. | OilLevSt | STV | Status of oil level in gearbox sump | IEC
WTRM.ShftBrgTmp | WTRM. | ShftBrgTmp | MV | Measured temperature of shaft bearing | IEC
WTRM.ShftBrkTmp | WTRM. | ShftBrkTmp | MV | Measured temperature of shaft brake (surface) | IEC
WTUR.DmdPFSpt | WTUR. | DmdPFSpt | SPV | Turbine power factor setpoint | IEC
WTUR.DmdVArh | WTUR. | DmdVArh | BCR | Reactive energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine) | IEC
WTUR.DmdVArSpt | WTUR. | DmdVArSpt | SPV | Turbine reactive power generation setpoint | IEC
WTUR.DmdVSpt | WTUR. | DmdVSpt | SPV | Turbine voltage output setpoint | IEC
WTUR.DmdWh | WTUR. | DmdWh | BCR | Active (real) energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine) | IEC
WTUR.DmdWSpt | WTUR. | DmdWSpt | SPV | Turbine active power generation setpoint | IEC
WTUR.StopCnt | WTUR. | StopCnt | CTE | Number of turbine stops (vendor-specific) | IEC
WTUR.StrCnt | WTUR. | StrCnt | CTE | Number of turbine starts (vendor-specific) | IEC
WTUR.SupVArh | WTUR. | SupVArh | BCR | Reactive energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar) | IEC
WTUR.SupWh | WTUR. | SupWh | BCR | Active (real) energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar) | IEC
WTUR.TotVArh | WTUR. | TotVArh | CTE | Total (net) reactive energy production | IEC
WTUR.TotWh | WTUR. | TotWh | CTE | Total (net) active energy production | IEC
WTUR.TurOp | WTUR. | TurOp | CMD | Wind turbine operation command | IEC
WTUR.TurSt | WTUR. | TurSt | STV | Turbine status | IEC
WTUR.VAr | WTUR. | VAr | MV | Reactive power generation | IEC
WTUR.VArOvW | WTUR. | VArOvW | SPC | Activate wind turbine reactive power priority over active power | IEC
WTUR.W | WTUR. | W | MV | Active power generation | IEC
WYAW.BrkPres | WYAW. | BrkPres | MV | Yaw brake pressure | IEC
WYAW.BrkSt | WYAW. | BrkSt | STV | Status of the yaw brake | IEC
WYAW.CabWup | WYAW. | CabWup | MV | Cable windup. Number of windings from calibration point | IEC
WYAW.CcwOpTms | WYAW. | CcwOpTms | TMS | Counter clockwise yawing operation time in seconds | IEC
WYAW.CwOpTms | WYAW. | CwOpTms | TMS | Clockwise yawing operation time in seconds | IEC
WYAW.RotSpd | WYAW. | RotSpd | MV | Rotational speed | IEC
WYAW.SysGsLev | WYAW. | SysGsLev | MV | Grease level for lubrication of yaw system | IEC
WYAW.Tmp | WYAW. | Tmp | MV | Yawing motor/gear temperature | IEC
WYAW.YwAng | WYAW. | YwAng | MV | Yaw bearing rotational angle relative to nominal true North | IEC
WYAW.YwOp | WYAW. | YwOp | CMD | Yaw system command | IEC
WYAW.YwSt | WYAW. | YwSt | STV | Status of yaw system | IEC

## Abreviated terms IEC 61400-25-2
3 Abbreviated terms (IEC 61400-25-2) |  | Table 2 – Attributes defined on classes of LogicalNodes_25_2 package (Ed.3 AutoGenerated) |  |  |  |  | Wind power plant general logical nodes
Term | Description | Name | Type | (Used in) Description | Term | Description | LN classes | Description | M/O
A | Current | AirDen | MV | (WMET) Density of air | CDC | Common Data Class | WTUR | Wind turbine general information | O
AC | AC, alternating current | AlmSt | ASS | (WALM) Alarm set status | DC | Data Class | WPPD | Wind power plant general information | O
Acs | Access | Alt | MV | (WMET) Sensor altitude | IED | Intelligent Electronic Device | WALM | Alarm information | O
Act | Action, activity, active, activate | AneSt | STV | (WNAC) Status of primary anemometer /secondary anemometer | LCB | Log Control Block | WMET | Meteorological information | O
Alm | Alarm | AvlTmsRs | TMS | (WAVL) Turbine availability time in seconds (implementation specific) | LD | Logical Device | WAPC | Active power control information | O
Alt | Altitude | BecBlbSt | STV | (WNAC) Status of beacon | LN | Logical Node | WRPC | Reactive power control information | O
An | Analogue | BecLevSpt | SPV | (WNAC) Setpoint bulb light level of beacon | LPHD | Logical node Physical Device Information | WSLG | State log information | O
Ane | Anemometer | BecLumLev | MV | (WNAC) Value of luminosity level of beacon | RCB | Report Control Block | WALG | Analogue log information | O
Ang | Angle | BecMod | CMD | (WNAC) Set modus of beacon | SBO | Select Before Operate | WREP | Report information | O
Avl | Availability | BlPthAngTgt | MV | (WROT) Pitch angle target value for blade | WPP | Wind Power Plant | WAVL | Availability information | O
Bec | Beacon | BlPthAngVal | MV | (WROT) Pitch angle for blade as feedback from the pitch system | WT | Wind Turbine | LTIM | Time management (inherited from IEC 61850-7-4) | O
Beh | Behaviour | BlPthHyPres | MV | (WROT) Pressure of hydraulic pitch system for blade | XML | Extensible Markup Language
Bl | Blade | BlSt | STV | (WROT) Status of blade as feedback from the pitch system
Blb | Bulb | BrkHyPres | MV | (WTRM) Hydraulic pressure for shaft brake |  |  | Logical nodes for modelling a wind turbine
Blk | Block, blocked | BrkOpSt | STV | (WTRM) Status of shaft brake | IEC LN | IEC Logical Node | LN classes | Description | M/O
Brg | Bearing | BrkPres | MV | (WYAW) Yaw brake pressure | IEC DO | IEC Data Object | WTUR | General information | M
Brk | Brake | BrkSt | STV | (WYAW) Status of the yaw brake | IEC DA | IEC Data Attribute | WROT | Rotor information | M
Cab | Cable | CabWup | MV | (WYAW) Cable windup. Number of windings from calibration point. The number of windings is defined positive in clockwise direction, seen from the top of the nacelle towards the ground |  |  | WTRM | Transmission information | O
Cap | Capability, capacity | CcwOpTms | TMS | (WYAW) Counter clockwise operation time in seconds. The rotational angle is negative in counter clockwise direction, seen from the top of the nacelle towards the ground |  |  | WGEN | Generator information | M
Ccw | Counter clockwise | ClSt | STV | (WCNV) Status of converter cooling system |  |  | WCNV | Converter information | O
Chk | Check |  |  | (WGEN) Status of generator cooling system |  |  | WTRF | Transformer information | O
Chr | Characteristic |  |  | (WTRF) Status of transformer cooling system |  |  | WNAC | Nacelle information | M
Cl | Cooling, cooling system |  |  | (WTRM) Status of transmission cooling system; ON meaning cooling system is operating |  |  | WYAW | Yawing information | M
Clc | Calculate, calculated, calculation | CloudCvr | MV | (WMET) Cloud cover level |  |  | WTOW | Tower information | O
Cloud | Cloud | CnvOpSt | STV | (WCNV) Status of converter |  |  | WALM | Alarm information | M
Cmd | Command | CutHiTurNum | INS | (WAPC) Number of wind turbines not running due to high wind speed |  |  | WMET | Meteorological information | O
Cnt | Counter, counting | CutLoTurNum | INS | (WAPC) The number of wind turbines not running due to low wind speed |  |  | WSLG | State log information | O
Cnv | Converter | CwOpTms | TMS | (WYAW) Clockwise yawing operation time in seconds. The rotational angle is positive in clockwise direction, seen from the top of the nacelle towards the ground |  |  | WALG | Analogue log information | O
Ctl | Control | DclA | MV | (WCNV) DC-link current inside converter |  |  | WREP | Report information | O
Cut | Cut, cut-out, cut-in | DclTmp | MV | (WCNV) Temperature inside the converter |  |  | WAVL | Availability information | O
Cvr | Cover, cover level | DclV | MV | (WCNV) DC-link voltage inside converter |  |  | LTIM | Time management (inherited from IEC 61850-7-4) | O
Cw | Clockwise | DctInsol | MV | (WMET) Direct normal insolation
DC | DC, direct current | DehumSt | STV | (WTOW) Status of de-humidifier; ON meaning the de-humidifier is operating
Dcl | DC-link | DelAct | CMD | (WAPC) Activate delta control function
Dct | Direct | DelEna | STV | (WAPC) Delta function enabled
Dehum | De-humidifier | DelSpt | SPV | (WAPC) Set reference value for the delta function, wind power plant active power reserve
Del | Delta | DevOp | CDCFake | (WPPD) Device operation command
Den | Density | DevSt | STV | (WPPD) Device status
Dev | Device | DewPt | MV | (WMET) Dew point
Dew | Dew | DffInsol | MV | (WMET) Diffuse insolation
Dff | Diffuse | Dir | MV | (WNAC) Nacelle orientation
Dir | Direction | DlDur | MV | (WMET) Daylight duration (time elapsed between sunrise and sunset)
Dl | Daylight | DmdPFSpt | SPV | (WTUR) Turbine power factor setpoint
Dmd | Demand | DmdVArSpt | SPV | (WTUR) Turbine reactive power generation setpoint
Dn | Down, downstream | DmdVArh | BCR | (WTUR) Reactive energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine)
Drp | Droop | DmdVSpt | SPV | (WTUR) Turbine voltage output setpoint
Dsp | Displacement | DmdWSpt | SPV | (WTUR) Turbine active power generation setpoint
Dur | Duration | DmdWh | BCR | (WTUR) Active (real) energy demand (default demand direction: energy flow from a substation busbar away and towards the wind turbine)
EE | External equipment | DrpSpt | SPV | (WRPC) Set reference value for slope of voltage control droop
Emg | Emergency | EnvHum | MV | (WMET) Ambient humidity
Ena | Enabled, enable, allow operation | EnvPres | MV | (WMET) Barometric pressure of environment
Env | Environment | EnvTmp | MV | (WMET) Temperature of environment
Eq | Equalization, equal | FilSt | STV | (WTRM) Status of filtration system; ON meaning filtration system is operating
Exp | Expired | FlshSpt | SPV | (WNAC) Setpoint value of flash duty cycle of beacon
Expt | Export | GbxOilLev | MV | (WTRM) Oil level in gearbox sump
Ext | Excitation | GbxOilPres | MV | (WTRM) Gear oil pressure
Fil | Filter, filtration, filtration system | GbxOilTmp | MV | (WTRM) Measured temperature of gearbox oil
Fll | Fall | GbxVbr | MV | (WTRM) Measured gearbox vibration of gearbox
Flsh | Flash, flashing | GnA | WYE | (WCNV) Generator side 3 phase current
Gbx | Gearbox | GnHz | MV | (WCNV) Generator side frequency
Gn | Generator | GnOpSt | STV | (WGEN) Status of generator
Gr | Group | GnPF | WYE | (WCNV) Generator side 3 phase power factor
Gra | Gradient | GnPNV | WYE | (WCNV) Generator side 3 phase-to-neutral voltage
Gri | Grid | GnPPV | DEL | (WCNV) Generator side 3 phase phase-to-phase voltage
Gs | Grease | GnTmp | MV | (WCNV) Generator side temperature
Gust | Gust | Gra | MV | (WAPC) Wind power plant gradient
Health | Health | GraAct | CMD | (WAPC) Activate gradient control function
Hi | High, highest | GraEna | STV | (WAPC) Gradient function enabled
Hor | Horizontal | GriA | WYE | (WCNV) Grid side 3 phase current
Ht | Heating, heating system |  |  | (WTRF) Grid side 3 phase current
Htex | Heat-exchanger | GriHz | MV | (WCNV) Grid side frequency
Hub | Hub | GriPF | WYE | (WCNV) Grid side 3 phase power factor
Hum | Humidity | GriPNV | WYE | (WCNV) Grid side 3 phase-to-neutral voltage
Hy | Hydraulic, hydraulic system |  |  | (WTRF) Grid side 3 phase-to-neutral voltage
Hz | Frequency | GriPPV | DEL | (WCNV) Grid side 3 phase phase-to-phase voltage
Ia | Information available |  |  | (WTRF) Grid side 3 phase phase-to-phase voltage
Iafm | Information available force majeure | GriSwOp | CMD | (WTRF) Main grid switch command; ON meaning close connection to main grid switch
Iano | Information available nonoperative | GriTmp | MV | (WCNV) Grid side temperature
Ianofo | Information available nonoperative forced outage |  |  | (WTRF) Temperature on grid side
Ianopca | Information available nonoperative planned corrective actions | GsLev | MV | (WTRM) Grease level for lubrication of main shaft bearing
Ianos | Information available nonoperative suspended | HorInsol | MV | (WMET) Total horizontal insolation
Ianosm | Information available nonoperative scheduled maintenance | HorWdDir | MV | (WMET) Horizontal wind direction
Iao | Information available operative | HorWdSpd | MV | (WMET) Horizontal wind speed
Iaog | Information available operative generating | HtSt | STV | (WTRM) Status of heating system; ON meaning heating system is operating
Iaogfp | Information available operative generating with full performance | HtexSt | STV | (WTOW) Status of heat-exchanger; ON meaning the heat-exchanger is operating
Iaogpp | Information available operative generating with partial performance | HubTmp | MV | (WROT) Temperature in the rotor hub
Iaong | Information available operative nongenerating | Ia | INC | (WAVL) Information available (defined in IEC 61400-26-1)
Iaongel | Information available operative nongenerating out of electrical specification | Iafm | INC | (WAVL) Information available force majeure (defined in IEC 61400-26-1)
Iaongen | Information available operative | Iano | INC | (WAVL) Information available nonoperative (defined in IEC 61400-26-1)
| nongenerating out of environmental specification | Ianofo | INC | (WAVL) Information available nonoperative forced outage (defined in IEC 61400-26-1)
Iaongrs | Information available operative | Ianopca | INC | (WAVL) Information available nonoperative planned corrective actions (defined in IEC 61400-26-1)
| nongenerating requested shutdown | Ianos | INC | (WAVL) Information available nonoperative suspended (defined in IEC 61400-26-1)
Iaongts | Information available operative nongenerating technical standby | Ianosm | INC | (WAVL) Information available nonoperative scheduled maintenance (defined in IEC 61400-26-1)
Ice | Ice | Iao | INC | (WAVL) Information available operative (defined in IEC 61400-26-1)
Impt | Import | Iaog | INC | (WAVL) Information available operative generating (defined in IEC 61400-26-1)
In | Input | Iaogfp | INC | (WAVL) Information available operative generating with full performance (defined in IEC 61400-26-1)
Inl | Inline | Iaogpp | INC | (WAVL) Information available operative generating with partial performance (defined in IEC 61400-26-1)
Inlet | Inlet | Iaong | INC | (WAVL) Information available operative nongenerating (defined in IEC 61400-26-1)
Insol | Insolation | Iaongel | INC | (WAVL) Information available operative nongenerating out of electrical specification (defined in IEC 61400-26-1)
Intn | Internal | Iaongen | INC | (WAVL) Information available operative nongenerating out of environmental specification (defined in IEC 61400-26-1)
Intv | Interval | Iaongrs | INC | (WAVL) Information available operative nongenerating requested shutdown (defined in IEC 61400-26-1)
Iu | Information unavailable | Iaongts | INC | (WAVL) Information available operative nongenerating technical standby (defined in IEC 61400-26-1)
Key | Key, physical control device | Ice | MV | (WMET) Thickness of ice
Lev | Level | IceSt | STV | (WMET) Status of ice detection; ON meaning that there is ice
Lft | Lifting, lift | InlFil | MV | (WTRM) Inline filter contamination
Lim | Limit | InlFilSt | STV | (WTRM) Status of inline filter contamination
Lo | Low | InletTmp | MV | (WGEN) Temperature measurement for inlet air/water temperature at generator
Loc | Local | IntnHum | MV | (WNAC) Humidity inside nacelle
Log | Log |  |  | (WTOW) Humidity inside tower
Lu | Lubrication | IntnTmp | MV | (WNAC) Temperature inside nacelle
Lum | Luminosity | Iu | INC | (WAVL) Information unavailable (defined in IEC 61400-26-1)
Min | Minimum | LftPos | MV | (WTOW) Lift position
Mod | Mode | LftSt | STV | (WTOW) Status of lift system
Mth | Method | LuSt | STV | (WTRM) Status of gearbox lubrication system; ON meaning gearbox lubrication system is operating
Nam | Name | OfFil | MV | (WTRM) Offline filter contamination
Num | Number | OfFilSt | STV | (WTRM) Status of offline filter contamination
Of | Off line | OilLevSt | STV | (WTRF) Status of oil level for oil filled transformers
Oil | Oil |  |  | (WTRM) Status of oil level in gearbox sump
Op | Operate, Operating | OpTmsRs | TMS | (WAVL) Operation time in seconds (implementation specific)
Out | Output |  |  | (WCNV) Converter operation time in seconds (vendor-specific)
Ov | Over, override, overflow |  |  | (WGEN) Generator operation time in seconds (vendor-specific)
Per | Periodic, period |  |  | (WNAC) Nacelle operation time of beacon in seconds (vendor-specific)
PF | Power factor |  |  | (WTRF) Transformer operation time in seconds (vendor-specific)
Phs | Phase | OpTurNum | INS | (WAPC) Actual number of wind turbines in operation
Phy | Physical |  |  | (WRPC) Actual number of wind turbines in operation
Pl | Plant | PF | MV | (WRPC) Wind power plant actual power factor
Plt | Plate, long-term flicker severity | PFSign | INS | (WRPC) Power factor sign convention: IEEE = 2
PNV | Phase to neutral voltage | PFSpt | SPV | (WRPC) Set reference value for wind power plant power factor - negative: lagging (producing reactive power); positive: leading (consuming reactive power) as defined by IEEE
Pos | Position | PthCtlSt | STV | (WROT) Status of pitch control; ON meaning pitch control is operating
PPV | Phase to phase voltage | PthEmgChk | CMD | (WROT) Command to check the pitch emergency system; START meaning start to check
Pres | Pressure | RnFll | MV | (WMET) Rainfall
Prod | Production | RotA | WYE | (WGEN) Generator rotor 3 phase current
Proxy | Proxy | RotBlk | CMD | (WROT) Block rotor position command; ON meaning block rotor position
Pt | Point | RotExtAC | MV | (WGEN) Generator rotor alternating current excitation
Pth | Pitch | RotExtDC | MV | (WGEN) Generator rotor direct current excitation
Pwr | Power | RotPNV | WYE | (WGEN) Generator rotor 3 phase-to-neutral voltage
Ref | Reference | RotPPV | DEL | (WGEN) Generator rotor 3 phase phase-to-phase voltage
Rf | Refreshment | RotPos | MV | (WROT) Angular rotor position
Rn | Rain | RotSpd | MV | (WGEN) Rotational speed
Rot | Rotational, rotor |  |  | (WROT) Rotational speed
Rp | Report |  |  | (WYAW) Rotational speed
Rs | Reset, resettable | RotSt | STV | (WROT) Status of rotor
Shft | Shaft | RotTmp | MV | (WGEN) Temperature measurements for generator rotor
Sign | Sign | ShftBrgTmp | MV | (WTRM) Measured temperature of shaft bearing
Snw | Snow | ShftBrkTmp | MV | (WTRM) Measured temperature of shaft brake (surface)
Spd | Speed | SnwCvr | MV | (WMET) Snow cover
Spt | Setpoint | SnwDen | MV | (WMET) Density of snowfall
Src | Source | SnwEq | MV | (WMET) Water equivalent of snowfall
St | Status, state | SnwFll | MV | (WMET) Snowfall
Sta | Station, function at plant level | SnwTmp | MV | (WMET) Temperature of snowfall
Stat | Statistics | StopCnt | CTE | (WPPD) Number of device stops (vendor-specific)
Stop | Stop |  |  | (WTUR) Number of turbine stops (vendor-specific)
Str | Start | StrCnt | CTE | (WPPD) Number of device starts (vendor-specific)
Stt | Stator |  |  | (WTUR) Number of turbine starts (vendor-specific)
Sub | Sub | SttA | WYE | (WGEN) Generator stator 3 phase current
Sup | Supply | SttPNV | WYE | (WGEN) Generator stator 3 phase phase-to-neutral voltage
Sw | Switch, switched | SttPPV | DEL | (WGEN) Generator stator 3 phase phase-to-phase voltage
Syn | Synchronisation, synchronous, synchronism | SttTmp | MV | (WGEN) Temperature measurements for generator stator
Sys | System | SupVArh | BCR | (WTUR) Reactive energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar)
Tgt | Target | SupWh | BCR | (WTUR) Active (real) energy supply (default supply direction: energy flow from the wind turbine and towards a substation busbar)
Tm | Time | SysAvl | MV | (WAVL) System availability (implementation specific)
Tmh | Time in hours | SysGsLev | MV | (WYAW) Grease level for lubrication of yaw system
Tmms | Time in milli seconds | Tmp | MV | (WYAW) Yawing motor/gear temperature
Tmp | Temperature | TnkPresSt | STV | (WTRF) Status of gas pressure of main tank for oil filled transformers
Tms | Time in seconds | Torq | MV | (WCNV) Torque value
Tnk | Tank | TotVArh | CTE | (WTUR) Total (net) reactive energy production
Torq | Torque | TotWh | CTE | (WTUR) Total (net) active energy production
Tot | Total | TurA | WYE | (WTRF) Turbine side 3 phase current
Trf | Transformer | TurAvl | MV | (WAVL) Turbine availability (implementation specific)
Trg | Trigger | TurOp | CMD | (WTUR) Wind turbine operation command
Tur | Turbine | TurPNV | WYE | (WTRF) Turbine side 3 phase-to-neutral voltage
Typ | Type | TurPPV | DEL | (WTRF) Turbine side 3 phase phase-to-phase voltage
Up | Up, upstream | TurSt | STV | (WTUR) Turbine status
Urg | Urgent | TurTmp | MV | (WTRF) Temperature on turbine side
V | Voltage | V | MV | (WRPC) Wind power plant output voltage at the external grid connection point
VA | Apparent power (volt amperes) | VA | MV | (WAPC) Wind power plant apparent power
Val | Value | VAAct | CMD | (WAPC) Activate apparent power control function
VAr | Reactive power (volt amperes reactive) | VAEna | STV | (WAPC) Active power control mode enabled controlling apparent power
VArh | Reactive energy | VASpt | SPV | (WAPC) Set reference value for the wind power plant apparent power output
Vbr | Vibration | VAr | MV, MV, WYE | (WRPC) Wind power plant reactive power output
Ver | Vertical |  |  | (WTUR) Wind turbine reactive power generation
Vis | Visibility |  |  | (WGEN) Generator reactive power output
W | Active power | VArAct | CMD | (WRPC) Activate reactive power control function
Wac | Watchdog | VArCapExpt | MV | (WRPC) Wind power plant reactive power export (supply) capability
Wd | Wind | VArCapImpt | MV | (WRPC) Wind power plant reactive power import (demand) capability
Wet | Wet | VArDnGraSpt | SPV | (WRPC) Set reference value for gradient for ramping down the wind power plant reactive power output
Wh | Watt hours | VArMinCap | MV | (WRPC) Wind power plant minimum reactive power capability
Wrm | Warm | VArMod | STV | (WRPC) Reactive power control mode
Wtr | Water | VArOvW | SPC | (WTUR) Activate wind turbine reactive power priority over active power
Wup | Windup | VArSpt | SPV | (WRPC) Set reference value of wind power plant reactive power output
Xdir | X-direction (Shaft Direction) (Longitudinal) | VArUpGraSpt | SPV | (WRPC) Set reference value for gradient for ramping up the wind power plant reactive power output
Ydir | Y-direction (Transversal) (Lateral) | VDnGraSpt | SPV | (WRPC) Set reference value for wind power plant voltage ramping down
Yw | Yaw | VSpt | SPV | (WRPC) Set reference value for wind power plant voltage output
|  | VUpGraSpt | SPV | (WRPC) Set reference value for wind power plant voltage ramping up
|  | VerWdDir | MV | (WMET) Vertical wind direction
|  | VerWdSpd | MV | (WMET) Vertical wind speed
|  | Vis | MV | (WNAC) Visibility outside nacelle
|  | W | MV, MV, WYE | (WAPC) Wind power plant active power output
(WTUR) Wind turbine active power generation
(WGEN) Generator active power output
|  | WAct | CMD | (WAPC) Activate active power control function
|  | WCap | MV | (WAPC) Wind power plant active power output capability
|  | WDel | MV | (WAPC) Wind power plant active power reserve utilizing the delta function – the difference between active power generation capability and active power generated
|  | WDnGraSpt | SPV | (WAPC) Set reference value for gradient ramping down the wind power plant active power output
|  | WLimEna | STV | (WAPC) Active power limitation mode enabled
|  | WMinCap | MV | (WAPC) Wind power plant minimum capability active power. Portion of the net power output to which the system operator may command.
This is the minimum achievable real power output for the entire plant under present wind and turbine conditions which may be commanded by the operator
|  | WSpt | SPV | (WAPC) Set reference value for the wind power plant active power output
|  | WUpGraSpt | SPV | (WAPC) Set reference value for gradient ramping up the wind power plant active power output
|  | WdGustSpd | MV | (WMET) Wind gust speed
|  | WdHtSt | STV | (WNAC) Status of heater for wind sensor
|  | WetBlbTmp | MV | (WMET) Wet bulb temperature
|  | WtrTmp | MV | (WMET) Temperature of water
|  | XdirDsp | MV | (WNAC) Tower displacement (longitudinal direction)
|  | YdirDsp | MV | (WNAC) Tower displacement (lateral direction)
|  | YwAng | MV | (WYAW) Yaw bearing rotational angle relative to nominal true North. The rotational angle is positive in clockwise direction, seen from the top of the nacelle towards the ground
|  | YwOp | CMD | (WYAW) Yaw system command
|  | YwSt | STV | (WYAW) Status of yaw system
For building the new Data Object class name, the abbreviated terms of IEC 61850-7-4:2010 shall be used if applicable.
Only in other cases new, abbreviations out of the English are allowed.
The Data Object class name consists of the different abbreviations to get more information’s about the data.
Each abbreviation term in the Data Object class name shall start with a upper case alpha character. The last abbreviation shall reflect the functionality or manner of the data e.g. “Tmp / temperature”, “Spt / setpoint”, “St / status”.
Be aware, that only 12 characters are allowed for the complete Data Object class name. This includes one numeric last character which indicates multiple instantiation capability

## Abrev. terms IEC 61850-7-4 2015
4.2 Abbreviated terms used in data object names (IEC 61850-7-4 :2015 CDV)
Term | Description
A | Current; phase A (L1)
Abr | Abrasion
Abs | Absolute
Absb | Absorbing
AC | AC, alternating current
Acc | Accuracy; acceleration (deprecated: use Accl instead)
Accl | Acceleration
Accm | Accumulated
Ack | Acknowledgement, acknowledge
Acs | Access
Act | Action, activity, active, activate
Actr | Actuator
Acu | Acoustic
Adj | Adjustment
Adp | Adapter, adaptation
Aff | Affected
AGC | Automatic generation control
Age | Ageing
Ahr | Ampere hours
Air | Air
Alg | Algorithm
Alm | Alarm
Alt | Altitude
Amnt | Amount
Amp | Ampere, current DC or non-phase-related AC
An | Analogue
Anc | Ancillary
Ane | Anemometer
Ang | Angle
Ap | Access point
Apc | Analogue point control
App | Apparent
Ar | Amperes reactive (reactive current)
Arc | Arc
Area | Area
Arr | Array
ASG | Analogue setting CDC
At | At
Auth | Authorisation
Auto | Automatic
Aux | Auxiliary
Av | Average
Avl | Availability
AWatt | Wattmetric component of current
Ax | Axial
Azi | Azimuth
B | Bushing; phase B (L2)
Bac | Binary-controlled analogue value
Base | Base
Bat | Battery
Bck | Backup
Bec | Beacon
Beh | Behaviour
Ber | Bit error rate
BG | Before Gain
Bias | Bias
Bl | Blade
Blb | Bulb
Blk | Block, blocked
Blow | Blowby
Bnd | Band, bandwidth
Boil | Boiler
Bot | Bottom
Brcb | Buffered report control block
Brg | Bearing
Brk | Brake
Bsc | Binary status control
Bst | Boost
Bt | Heartbeat
Bus | Bus
C | Carbon; phase C (L3)
C2H2 | Acetylene
C2H4 | Ethylene
C2H6 | Ethane
Cab | Cable
Cal | Calorie, caloric
Cam | Cam, e.g. rotating non-circular disk
Cap | Capability, capacity
Capac | Capacitance
Car | Carrier
CB | Circuit breaker
Cbr | Calibration
Ccw | Counter clockwise
Ccy | Currency
CE | Cooling equipment (see also Cl)
Ceil | Ceiling
Cel | Cell
Cf | Crest factor
Cff | Coefficient
Cfg | Configuration
CG | Core ground
Ch | Channel
CH4 | Methane
Cha | Charger
Chg | Change
Chk | Check
CHP | Combined heat and power
Chr | Characteristic
Circ | Circulating, circuit
Cl | Cooling, coolant, cooling system (see also CE)
Clc | Calculate, calculated
Clip | Clip
Clk | Clock
Cloud | Cloud
Clr | Clear
Cls | Close, closed
Cm | Centimetres
Cmbu | Combustible, combustion
Cmd | Command
Cmpl | Completed, completion, complete
Cmut | Commute, commutator
Cndct | Conductivity
Cnt | Counter
Cntt | Contractual
Cnv | Converter
CO | Carbon monoxide
CO2 | Carbon dioxide
Col | Coil
Comm | Communication
Comp | Compensation
ConfRev | Configuration revision (confRev from IEC 61850-7-2)
Conn | Connected, connections
Cons | Constant (general)
Cor | Correction
Core | Core
Cost | Cost
Crank | Crank
Crd | Coordination
Crit | Critical
Crl | Correlation
Crp | Creeping, slow movement
Crv | Curve
Csmp | Consumption, consumed
Ctl | Control
Ctr | Center
Cur | Current
Cut | Cut, cut-out, cut-in
Cvr | Cover, cover level
Cw | Clockwise
Cwb | Crowbar
Cyc | Cycle
D | Derivate
Dam | Dam
Damp | Damping
Date | Date, date and time of action
Day | Day
Db | Deadband
DC | DC, direct current
Dcl | DC-link
Dct | Direct
De | De (prefix)
Dea | Dead
Dec | Decrease
Deg | Degrees
Dehum | De-humidifier
Del | Delta
Den | Density
Dep | Dependent
DER | Distributed energy resource
Det | Detected
Detun | Detuning
Dev | Device
Dew | Dew
DExt | De-excitation
Dff | Diffuse
Dfl | Deflector (used in Pelton turbines)
Dia | Diaphragm
Diag | Diagnostics
Dif | Differential, difference
Dig | Digital
Dip | Dip
Dir | Direction
Dis | Distance
Dith | Dither
Dl | Delay
Dlt | Delete
Dlv | Delivery
Dmd | Demand
Dn | Down, downstream
Dpc | Double point control
DPCSO | Double point controllable status output
Dpt | Departure
DQ0 | Direct, quadrature, and zero axis quantities
Drag | Drag hand
Dropout | Dropout
Drp | Droop
Drt | Derate
Drtb | Draft tube
Drv | Drive
DS | Device state
Dsa | Disable, disabled
Dsc | Discrepancy
Dsch | Discharge
Dscon | Disconnected
Dsp | Displacement
DT | Daylight saving time
Dtc | Detection
Dur | Duration
Dust | Dust
Dv | Deviation
Dw | Delta Omega
Echo | Echo
ECP | Electrical connection point
Edt | Edit, edited
EE | External equipment
EF | Earth fault
Efc | Efficiency
EFN | Earth-fault neutriliser (Petersen coil)
El | Elevation
Em | Emission
Emg | Emergency
En | Energy
Ena | Enabled, enable, allow operation
Enc | Enumerated control
Encl | Enclosure
End | End
ENG | Enumerated status setting CDC
Eng | Engine
ENS | Enumerated status CDC
Ent | Entity, entities
Entr | Entry, entries
Env | Environment
Eq | Equalization, equal, equivalent
Err | Error
Est | Estimated
EV | Electrical Vehicle
Ev | Evaluation
Evn | Even
EVSE | EV Supply Equipment
Evt | Event
Ex | External
Exc | Exceeded
Excl | Exclusion
ExIm | Export/import
Exp | Expired
Expt | Export
Ext | Excitation
F | Float
FA | Fault arc
Fa | Fire all sequence (to thyristors)
Fact | Factor
Fail | Failure
Fan | Fan
Fbc | Field breaker configuration
Fer | Frame error rate
Fil | Filter, filtration system
Fish | Fish
Fix | Fixed
Fld | Field
Fll | Fall
Flm | Flame
Flood | Flood
Flsh | Flash, flashing
Flt | Fault
Flush | Flush
Flw | Flow, flowing
Fol | Follower, following
Forc | Forced
FPM | Fuel processing module
Fu | Fuse
Fuel | Fuel
Full | Full
Fwd | Forward
Gain | Gain
Gas | Gas
Gbx | Gearbox
Gdv | Guide vane
Gen | General
Gn | Generator
Gnd | Ground
Gocb | GOOSE control block
GoCBRef | GOOSE control block reference
Gr | Group
Gra | Gradient
Grd | Guard
Gri | Grid
Gross | Gross
Gs | Grease
Gte | Gate
Gust | Gust
H | Harmonics (phase-related)
H2 | Hydrogen
H2O | Water (chemical aspect: liquid, steam, etc.)
Ha | Harmonics (non-phase-related AC)
Hd | Head
Hdr | Hydrological, hydro, water
Health | Health
Heat | Heater, heating, heat (see also Ht)
Hi | High, highest
Hold | Hold
Hor | Horizontal
Horn | Horn
HP | Hot point
HPh | Harmonics phase
Ht | Heating, heating system (see also Heat)
Htex | Heat-exchanger
Hub | Hub
Hum | Humidity
Hy | Hydraulic, hydraulic system
Hyd | Hydrological, hydro, water
Hys | Hysteresis
Hz | Frequency
Hz1 | Frequency at side 1
Hz2 | Frequency at side 2
I | Integral, integration
Ia | Information available
Iafm | Information available force majeure
Iano | Information available non-operative
Ianofo | Information available non-operative forced outage
Ianopca | Information available non-operative planned corrective action
Ianos | Information available non-operative suspended
Ianosm | Information available non-operative scheduled maintenance
Iao | Information available operative
Iaog | Information available operative generating
Iaogfp | Information available operative generating with full performance
Iaogpp | Information available operative generating with partial performance
Iaong | Information available operative non-generating
Iaongel | Information available operative non-generating out of electrical specification
Iaongen | Information available operative non-generating out of environment specification
Iaongrs | Information available operative non-generating requested shutdown
Iaongts | Information available operative non-generating technical standby
Ice | Ice
Id | Identity, identifier
Ieee | IEEE definition
IeeeKH | Proportional gain HF (High Frequency). Defined in IEEE 421.5
IeeeKH1 | Proportional gain HF positive. Defined in IEEE 421.5
IeeeKH11 | Lead gain HF positive. Defined in IEEE 421.5
IeeeKH17 | Lead gain HF negative. Defined in IEEE 421.5
IeeeKH2 | Proportional gain HF negative. Defined in IEEE 421.5
IeeeKI | Proportional gain IF (Intermediate Frequency). Defined in IEEE 421.5
IeeeKI1 | Proportional gain IF positive. Defined in IEEE 421.5
IeeeKI11 | Lead gain IF positive. Defined in IEEE 421.5
IeeeKI17 | Lead gain IF negative. Defined in IEEE 421.5
IeeeKI2 | Proportional gain IF negative. Defined in IEEE 421.5
IeeeKL | Proportional gain LF (Low Frequency). Defined in IEEE 421.5
IeeeKL1 | Proportional gain LF positive. Defined in IEEE 421.5
IeeeKL11 | Lead gain LF positive. Defined in IEEE 421.5
IeeeKL17 | Lead gain LF negative. Defined in IEEE 421.5
IeeeKL2 | Proportional gain LF negative. Defined in IEEE 421.5
IeeeKs1 | Gain Ks1. Defined in IEEE 421.5
IeeeKs2 | Gain Ks2. Defined in IEEE 421.5
IeeeKs3 | Gain Ks3. Defined in IEEE 421.5
IeeeM | Ramptrack lowpass degree M. Defined in IEEE 421.R
IeeeN | Ramptrack overall degree N. Defined in IEEE 421.5
IeeeT1 | Time constant T1. Defined in IEEE 421.5
IeeeT10 | Time constant T10. Defined in IEEE 421.5
IeeeT11 | Time constant T11. Defined in IEEE 421.5
IeeeT2 | Time constant T2. Defined in IEEE 421.5
IeeeT3 | Time constant T3. Defined in IEEE 421.5
IeeeT4 | Time constant T4. Defined in IEEE 421.5
IeeeT7 | Time constant T7. Defined in IEEE 421.5
IeeeT8 | Time constant T8. Defined in IEEE 421.5
IeeeT9 | Time constant T9. Defined in IEEE 421.5
IeeeTH1 | Time constant TH1 (High frequency positive). Defined in IEEE 421.5
IeeeTH10 | Time constant TH10 (High frequency negative). Defined in IEEE 421.5
IeeeTH11 | Time constant TH11 (High frequency negative). Defined in IEEE 421.5
IeeeTH12 | Time constant TH12 (High frequency negative). Defined in IEEE 421.5
IeeeTH2 | Time constant TH2 (High frequency positive). Defined in IEEE 421.5
IeeeTH3 | Time constant TH3 (High frequency positive). Defined in IEEE 421.5
IeeeTH4 | Time constant TH4 (High frequency positive). Defined in IEEE 421.5
IeeeTH5 | Time constant TH5 (High frequency positive). Defined in IEEE 421.5
IeeeTH6 | Time constant TH6 (High frequency positive). Defined in IEEE 421.5
IeeeTH7 | Time constant TH7 (High frequency negative). Defined in IEEE 421.5
IeeeTH8 | Time constant TH8 (High frequency negative). Defined in IEEE 421.5
IeeeTH9 | Time constant TH9 (High frequency negative). Defined in IEEE 421.5
IeeeTI1 | Time constant TI1 (Intermediate frequency positive). Defined in IEEE 421.5
IeeeTI10 | Time constant TI10 (Intermediate frequency negative). Defined in IEEE 421.5
IeeeTI11 | Time constant TI11 (Intermediate frequency negative). Defined in IEEE 421.5
IeeeTI12 | Time constant TI12 (Intermediate frequency negative). Defined in IEEE 421.5
IeeeTI2 | Time constant TI2 (Intermediate frequency positive). Defined in IEEE 421.5
IeeeTI3 | Time constant TI3 (Intermediate frequency positive). Defined in IEEE 421.5
IeeeTI4 | Time constant TI4 (Intermediate frequency positive). Defined in IEEE 421.5
IeeeTI5 | Time constant TI5 (Intermediate frequency positive). Defined in IEEE 421.5
IeeeTI6 | Time constant TI6 (Intermediate frequency positive). Defined in IEEE 421.5
IeeeTI7 | Time constant TI7 (Intermediate frequency negative). Defined in IEEE 421.5
IeeeTI8 | Time constant TI8 (Intermediate frequency negative). Defined in IEEE 421.5
IeeeTI9 | Time constant TI9 (Intermediate frequency negative). Defined in IEEE 421.5
IeeeTL1 | Time constant TL1 (Low frequency positive). Defined in IEEE 421.5
IeeeTL10 | Time constant TL10 (Low frequency negative). Defined in IEEE 421.5
IeeeTL11 | Time constant TL11 (Low frequency negative). Defined in IEEE 421.5
IeeeTL12 | Time constant TL12 (Low frequency negative). Defined in IEEE 421.5
IeeeTL2 | Time constant TL2 (Low frequency positive). Defined in IEEE 421.5
IeeeTL3 | Time constant TL3 (Low frequency positive). Defined in IEEE 421.5
IeeeTL4 | Time constant TL4 (Low frequency positive). Defined in IEEE 421.5
IeeeTL5 | Time constant TL5 (Low frequency positive). Defined in IEEE 421.5
IeeeTL6 | Time constant TL6 (Low frequency positive). Defined in IEEE 421.5
IeeeTL7 | Time constant TL7 (Low frequency negative). Defined in IEEE 421.5
IeeeTL8 | Time constant TL8 (Low frequency negative). Defined in IEEE 421.5
IeeeTL9 | Time constant TL9 (Low frequency negative). Defined in IEEE 421.5
IeeeTw1 | Time constant wash out Tw1. Defined in IEEE 421.5
IeeeTw2 | Time constant wash out Tw2. Defined in IEEE 421.5
IeeeTw3 | Time constant wash out Tw3. Defined in IEEE 421.5
IeeeTw4 | Time constant wash out Tw4. Defined in IEEE 421.5
IeeeVHMax | Maximum limit set-point HF. Defined in IEEE 421.5
IeeeVHMin | Minimum limit set-point HF. Defined in IEEE 421.5
IeeeVIMax | Maximum limit set-point IF. Defined in IEEE 421.5
IeeeVIMin | Minimum limit set-point IF. Defined in IEEE 421.5
IeeeVLMax | Maximum limit set-point LF. Defined in IEEE 421.5
IeeeVLMin | Minimum limit set-point LF. Defined in IEEE 421.5
IeeeVsi1Max | Input High Limit 1. Defined in IEEE 421.5
IeeeVsi1Min | Input Low Limit 1. Defined in IEEE 421.5
IeeeVsi2Max | Input High Limit 2. Defined in IEEE 421.5
IeeeVsi2Min | Input Low Limit 2. Defined in IEEE 421.5
IeeeVstMax | Output High Limit. Defined in IEEE 421.5
IeeeVstMin | Output Low Limit. Defined in IEEE 421.5
Imb | Imbalance
Imp | Impedance non-phase-related AC
Impact | Impact
Impt | Import
In | Input
Ina | Inactivity
Inc | Integer control
Incr | Increment, increase
Ind | Indication
Indp | Independent
Iner | Inertia
ING | Integer status setting CDC
Inh | Inhibit
Inl | Inline
Inlet | Inlet
INS | Integer status CDC
Ins | Insulation
Insol | Insolation
Inst | Instantaneous
Int | Integer
Intn | Internal
Intr | Interrupt, interruption
Intv | Interval
Inv | Inverter, inverted, inverse
Isc | Integer status control
ISCSO | Integer status controllable status output
Isld | Islanded
Iso | Isolation
Iu | Information unavailable
Ix | Index
Jmp | Jump
Jnt | Joint
K | Constant (regulation)
K0Fact | Zero-sequence (residual) compensation factor
Kck | Kicker
Key | Key, physical control device
KFact | K factor (harmonics)
km | Kilometre
L | Lower (action)
Last | Last
Ld | Lead
LDC | Line drop compensation
LDCR | Line drop compensation resistance
LDCX | Line drop compensation reactance
LDCZ | Line drop compensation impedance
Leap | Leap (second)
LED | Light-emitting diode
Len | Length
Lev | Level
Lft | Lifting, lift
Lg | Lag
Life | Lifetime
Lim | Limit
Lin | Line
Liv | Live
Lkd | Locked
Lkg | Leakage
Ll | Last long (interval)
Lo | Low (state or value)
Loc | Local
Locb | Log control block
Lod | Load, loading
Log | Log
Lok | (use Lkd instead) Locked
Loop | Loop
Los | Loss
Ls | Last short (interval)
Lst | List
LTC | Load tap changer
Lu | Lubrication
Lub | Lubrication
Lum | Luminosity
M | Minutes
Made | Made
Mag | Magnetic, magnitude
Maint | Maintenance
Man | Manual
Mat | Material
Max | Maximum
Mbr | Membrane
Mdul | Module
Mech | Mechanical
Media | Media
Mem | Memory
Min | Minimum
Mlt | Multiple
Mod | Mode
Mot | Motor
Mrk | Market
Mst | Moisture
Msvcb | Multicast sampled values control block
Mth | Method
Mult | Multiplier
MV | Measured value CDC
Mvm | Movement, moving
Mx | Maximum
N2 | Nitrogen
Nam | Name
Name | Name (reserved for use in data objects EEName and LNName only)
Ndl | Needle (used in Pelton turbines)
NdsCom | Needs commissioning
Neut | Neutral
Ng | Negative
Nhd | Net head
Night | Night
No | No, not
Nom | Nominal, normalising
NOx | Nitrogen oxide
NQS | Average partial discharge current
Num | Number
Nxt | Next
O2 | Oxygen
O3 | Ozon, trioxygen
Obl | Obligation
Oc | Open circuit
Odd | Odd
Of | Offline
Off | Off, device disengaged, not running
Ofs | Offset
Oil | Oil
On | On, device applied, running
Oo | Out of
Op | Operate, operating, operation
Operate | Operate order to any device
Opn | Open, opened
Out | Output
Ov | Over, override, overflow
Ovl | Overload
Ox | Oxidant
P | Proportional
Pa | Partial
Pair | Pair, paired
Pap | Paper
Par | Parallel
Pas | Passive
Pcb | Power quality qualifier bin
Pct | Percent, percentage
Pdm | Power quality demodulation
Pe | Electric Power
Per | Periodic, period
PF | Power factor
PH | Acidity, value of pH
Ph | Phase to reference
Phs | Phase
Phy | Physical
Pi | Instantaneous real power
Pin | Pin
Pipe | Pipe
Pk | Peak
Pl | Plant
Plg | Plug
Pls | Pulse
Plt | Plate; long-term flicker severity
Pmp | Pump
PNV | Phase-to-neutral voltage
Po | Polar
Pol | Polarizing
Polytr | Polytropic
Pos | Position
Pot | Potentiometer
POW | Point on wave switching
PP | Phase to phase
ppm | Parts per million
PPV | Phase to phase voltage
Prc | Price, pricing
Pre | Pre-
Prec | Precondition, initial status
Pres | Pressure
Prg | Progress, in progress
Prm | Permissive
Pro | Protection
Proc | Process
Proxy | Proxy
Prt | Parts, part
Ps | Positive
Psk | Penstock
Pss | PSS, power system stabiliser function
Pst | Post, short-term flicker severity
Pt | Point
PT1 | Low-pass exponential time rate filter
Pth | Pitch
Pwr | Power
Qty | Quantity
Qu | Queue
Qud | Quad
R | Raise, increase
Rad | Radiation
Ral | Rail
Ramp | Ramp
Rat | Ratio
Rb | Runner blade
Rcd | Record, recording
Rch | Reach
Rcl | Reclaim
Rct | Reaction
Rdy | Ready
Re | Retry
React | Reactance, reactive
Rec | Reclose
Rec1 | Reclose after single phase fault
Rec13 | Reclose after evolving fault
Rec3 | Reclose after three phase fault
Recha | Recharge, recharging
Rect | Rectifier
Red | Redundant; (deprecated meaning) reduction
Ref | Reference
Reg | Regulation
Rel | Release
Req | Requested
Res | Residual
Reso | Resonance
Reuse | Reuse
Rf | Refreshment
Ris | Resistance
Rl | Relation, relative
Rm | Mutual resistance
Rmp | Ramping, ramp
Rms | Root mean square
Rn | Rain
Rnbk | Runback
Rng | Range
Rod | Rod
Root | Root
Rot | Rotation, rotor
Rpt | Repeat, repetition
Rs | Reset, resettable
Rsl | Result
Rst | Restraint, restriction
Rsv | Reserve
Rt | Ride-through
Rte | Rate
Rtg | Rating
Rv | Reverse
Rvrt | Revert
Rwy | Runaway, e.g. in runaway speed
Rx | Receive, received
S10 | Coefficient S1.0
S12 | Coefficient S1.2
Saf | Safety
Sag | Sag
Sar | Surge arrestor
Sat | Saturation
Sc | Short circuit
Scale | Scale
Schd | Schedule
Sco | Supply change over
Sec | Security
Sel | Select
Self | Self
Seq | Sequence
Ser | Series, serial
Set | Setting
Sgcb | Setting group control block
Sh | Shunt
Shar | Shared
Shft | Shaft
Sig | Signal
Sign | Sign
Sim | Simulation, simulated
Sld | Solidity
Slnt | Salinity, saline content
Slp | Sleep; slip
SM | Servo, servo-motor
Smok | Smoke
Smp | Sampling
Snd | Sound pressure
SNL | Speed-no-load, connected but not generating
Snpt | Snapshot
Snr | Signal to noise ratio
Snw | Snow
Soc | State of charge
Sof | Switch on to fault
SOx | Sulphur oxide
Spc | Single point control
Spcf | Specific
SPCSO | Single point controllable status output
Spd | Speed
Spec | Spectra
SPG | Single point setting CDC
Spir | Spiral
SPl | Single pole/phase
SPS | Single point status CDC
Spt | Setpoint
Src | Source
Srfc | Surface
ST | Standard time
St | Status, state
Sta | Station, function at plant level
Stab | Stabilizer
Stat | Statistics
Stc | Stack
Stdby | Standby
Step | Step
Stk | Stroke
Stl | Still, not moving
Stnd | Stand, standing
Sto | Storage, e.g. activity of storing data
Stop | Stop
Storm | Storm
Stow | Stow
Str | Start
Strg | String
Stt | Stator
Stuck | Stuck, cannot move
Sub | Sub
Sum | Sum
Sup | Supply
Sv | Sampled value
Svc | Service
SvCBRef | SV control block reference
Sw | Switch, switched
Swg | Swing
Swl | Power quality event swell
Syn | Synchronisation, synchronous, synchronism, synchrocheck
Sys | System
Ta | Armature time constant
Tag | Tag (maintenance work in progress)
Tap | Tap
Task | Task
Td | Transformer derating
Td0p | Td0'
Td0s | Td0''
Tdd | Total demand distortion
Tdf | Transformer derating factor
Tdp | Td'
Tds | Td''
Tech | Technology
Term | Termination
Test | Test
Tgt | Target
Thd | Total harmonic distortion
Thm | Thermal
Ti | Telephone influence
Tilt | Tilt
Tm | Time
Tm1 | Time constant 1
Tm2 | Time constant 2
Tm3 | Time constant 3
Tmh | Time in h
Tmm | Time in min
Tmms | Time in ms
Tmp | Temperature (°C)
Tms | Time in s
Tnk | Tank
Tns | Tension (stress)
Top | Top (position)
Torq | Torque
Tot | Total
TP | Three pole/phase
Tp | Test Point
Tpc | Teleprotection
Tq0p | Tq0'
Tq0s | Tq0''
Tqp | Tq'
Tqs | Tq''
Tr | Trip (electrical protection function)
Trb | Turbine
Trf | Transformer
Trg | Trigger
Trip | Trip (non-electrical function)
Trk | Track, tracking
Trs | Transient
Ts | Total signed
Tu | Total unsigned
Tun | Tuning
Tur | Turbine
Tx | Transmit, transmitted
Typ | Type
Uhf | Ultra-high-frequency
Un | Un-; under
Unav | Unavailable
Unb | Unbalanced
Unld | Unload
Unt | Unit, production unit
Up | Up, upstream
UPS | Uninterruptible power supply
Urcb | Unbuffered report control block
Use | Use
Used | Used
Usvcb | Unicast sampled values control block
Util | Utility
V | Voltage
V1 | Voltage at side 1
V2 | Voltage at side 2
VA | Apparent power (volt amperes)
Va | Variation
Vac | Vacuum
VAh | Apparent energy
Val | Value
VAr | Reactive power (volt amperes reactive)
VArh | Reactive energy
Vbr | Vibration
Ver | Vertical
Viol | Violation
Vis | Visibility
Visc | Viscosity
Vld | Valid, validate, validated
Vlm | Volume
Vlv | Valve
Vol | Voltage DC or non-phase-related AC
VolAmpr | Non-phase-related AC reactive power
W | Active power
W200 | Watts peak at 200 W/m2
Wac | Watchdog
Wash | Washout
Watt | Active power non-phase-related AC
Wav | Wave, waveform
Wd | Wind
Week | Week
Wei | Weak end infeed
Wet | Wet
Wh | Watt hours
Wid | Width
Win | Window
Wkup | Wake up
Wld | Welding
Wrm | Warm
Wrn | Warning
Wtr | Water (physical aspect: river, cooling, etc.)
Wup | Windup
X | Reactance (imaginary part of impedance)
X0 | Zero sequence reactance
X1 | Positive sequence reactance
X2 | Negative sequence reactance X2
Xd | Synchronous reactance Xd
Xdir | X-direction
Xdp | Transient synchronous reactance Xd'
Xds | Subtransient reactance Xd''
Xm | Mutual reactance
Xq | Synchronous reactance Xq
Xqp | Transient synchronous reactance Xq'
Xqs | Subtransient reactance Xq''
Xsec | Cross-section
Ydir | Y-direction
Yw | Yaw
Z | Impedance
Zer | Zero
Zero | (use 'Zer' instead) Zero
Zm | Mutual impedance
Zn | Zone
Zro | Zero sequence

## 61400-25-2 Annex B SI Units
Table B.1 – SI units: base units
Value | Quantity | Unit name | Symbol
1 | None | dimensionless | none
2 | Length | meter | m
3 | Mass | kilogram | kg
4 | Time | second | s
5 | Current | ampere | A
6 | Temperature | kelvin | K
7 | Amount of substance | mole | mol
8 | Luminous intensity | candela | cd
Table B.2 – SI units: derived units
Value | Quantity | Unit name | Symbol
9 | Plane angle | degrees | deg
10 | Plane angle | radian | rad
11 | Solid angle | steradian | sr
21 | Absorbed dose | Gray (J/kg) | Gy
22 | Activity | becquerel (l/s) | q
23 | Relative temperature | degrees Celsius | °C
24 | Dose equivalent | sievert (J/kg) | Sv
25 | Electric capacitance | farad (C/V) | F
26 | Electric charge | coulomb (A s) | C
27 | Electric conductance | siemens (A/V) | S
28 | Electric inductance | henry (Wb/A) | H
29 | Electric potential | volt (W/A) | V
30 | Electric resistance | ohm (VA) | W
31 | Energy | joule (N m) | J
32 | Force | newton (kg m/s2) | N
33 | Frequency | hertz (1/s) | Hz
34 | Illuminence | lux (lm/m2) | lx
35 | Luminous flux | lumen (cd sr) | Lm
36 | Magnetic flux | weber (V s) | Wb
37 | Magnetic flux density | tesla (Wb/m2) | T
38 | Power | watt (J/s) | W
39 | Pressure | pascal (N/m2) | Pa
Table B.3 – SI units: extended units
Value | Quantity | Unit name | Symbol
41 | Area | square meter (m2) | m2
42 | Volume | cubic meter (m3) | m3
43 | Velocity | meters per second (m/s) | ms–1
44 | Acceleration | meters per second2 (m/s2) | ms–2
45 | Volumetric flow rate | cubic meters per second (m3/s) | m3s–1
46 | Fuel efficiency | meters/cubic meter (m/m3) | m/m3
47 | Moment of mass | kilogram meter (kg m) | M
48 | Density | kilogram/cubic meter (kg/m3) | kg/m3
49 | Viscosity | meter square/second (m2/s) | m2/s
50 | Thermal conductivity | watt/meter Kelvin (W/m K) | W/m K
51 | Heat capacity | joule/Kelvin (J/K) | J/K
52 | Concentration | parts per million | ppm
53 | Rotational speed | rotations per second (1/s) | s–1
54 | Angular velocity | radian per second (rad/s) | rads–1
Table B.4 – SI units: industry specific units
Value | Quantity | Unit name | Symbol
61 | Apparent power | volt ampere (VA) | VA
62 | Real power | watts (I2R) | W
63 | Reactive power | volt ampere reactive (VISinq) | VAr
64 | Phase angle | degrees | q
65 | Power factor | (dimensionless) | cosq
66 | Volt seconds | volt seconds (Ws/A) | Vs
67 | Volts squared | volt square (W2/A2) | V2
68 | Amp seconds | amp second (As) | As
69 | Amps squared | amp square (A2) | A2
70 | Amps squared time | amp square second (A2s) | A2s
71 | Apparent energy | volt ampere hours | VAh
72 | Real energy | watt hours | Wh
73 | Reactive energy | volt ampere reactive hours | VArh
74 | Magnetic flux | volts per hertz | V/Hz
75 | Rate of change of frequency | hertz per second | Hz/s
76 | Number of characters | characters | char
77 | Baud | characters per second | char/s
78 | Turbine inertia | kg square meter | kgm2
79 | Sound pressure level | decibel | dB
80 | Heat rate | joule per watt-hour | J/Wh
81 | Ramp rate | watt per second | W/s
82 | Flow rate | litres per second | L/s
83 | Power level | power measurement relative to 1 mW | dBm
84 | Torgue | newton metre | Nm